## List2
Type | Interfaces/Protocols | Direction | Capacity/Limit | Notes
R005 | Sauter EY2400 ↔ RS232 | Gateway/bridge | ~20 controllers | Galvanic separation
R012 | RS232 ↔ RS485 | Converter | 1200…115200 bit/s | Galvanic separation
R025 | Ethernet ↔ RS232; Modbus RTU/TCP router | IP↔Serial Router | Modbus routing RTU↔TCP | Use VLAN/VPN; avoid public exposure
R035 | Ethernet ↔ RS485; Modbus RTU/TCP router | IP↔RS485 Router | Modbus routing RTU↔TCP | Respect RS485 termination & device counts
R060 | Belimo MP-Bus ↔ Modbus RTU/TCP | Gateway | up to 8 actuators | Follow MP-Bus addressing & spur rules
R065 | DMX512 ↔ Modbus RTU/TCP | Gateway | up to 2×512 channels | Respect DMX topology and termination
R080 | USB ↔ RS485 | Adapter | — | Commissioning/diagnostics adapter
R085 | P-bus ↔ RS485 | Gateway | up to 32 BE points | Legacy P-bus migration
R086 | P-bus ↔ RS485 | Gateway | up to 64 BE points | Higher capacity vs R085
R091 | DALI ↔ Modbus TCP (multimaster) | Gateway | up to 64 DALI devices | DALI supply/topology limits apply
R095 | M-Bus ↔ RS232 | Gateway | up to 25 devices | Observe unit loads & cable length
R096 | M-Bus ↔ RS232 | Gateway | up to 60 devices | Plan segmentation/repeaters for long runs