## List1
Type | AI | AO | DI | DO | Notes
RCIO | 8 | 6 | 8 | 8 (relay) | Combined I/O, galvanic separation
MLIO | 4 | 1 | - | 2 (relay) | Small distributed I/O; optimized case for easy in-room/near-device install
RMIO | 4 | 2 | 4 | 7 | Multi I/O compact module
RXIO | 16 | 8 | 32 | 32 (relay) | Maxi combined I/O, galvanic separation
R220 | - | - | - | 12 (relay) | Relay DO 8 A @ 250 V AC / 24 V DC
R312 | - | - | - | 8 (triac, 24 V AC, 0.4 A) | Triac outputs; suitable for 24 V thermal actuators; PWM/binary
R313 | - | - | - | 8 (triac, 230 V AC, 0.12 A) | Triac SSR for 230 V AC; PWM/binary
R320 | - | - | - | 16 (open collector) | DC loads; requires external supply; check sink/source wiring
R330 | - | - | - | 32 (open collector) | High-density OC outputs; DC loads
R420 | - | - | 16 (30 V AC / 50 V DC, common ground) | - | Low-voltage DI; consider noise filtering on long runs
R430 | - | - | 32 (30 V AC / 50 V DC, common ground) | - | High-density DI; common ground
R500 | 8 (0…10 V) | - | - | - | Voltage/current ranges; galvanic isolation
R560 | 8 (multi-range: V/Ω/°C/mA) | - | - | - | Universal AI; per-channel range selection
R610 | - | 8 (0…10 V) | - | - | Analog outputs for dampers/VFDs
R710 | - | - | 4 (counters/pulse) | - | Pulse counting (meters/events)
R800 | 8 (multi-range) | 8 (0…10 V) | - | - | Combined AI + AO in one module
MW240-B | - | - | 2 | 2 (relay) | Lights & blinds control; local + bus logic options
MW241 | - | - | 2 | 2 (SSR 230 V AC) | SSR for switching of LED light power supplies
MW501 | 1 (0…10 V) | - | - | - | Single AI add-on for quick retrofits