H2Vector

Energy

Technologies

October 2025

PRODUCTS

Thrusting Ideas

Energy moves and connects us, it alllows our society development and growth.

For our environment, health and well-being, energy must be sustainable and non-polluting.

Hydrogen is the key factor to maximize and promote the use of renewable energy sources, generating a clean and safe energy cycle.

H2Vector offers comprehensive, modular and scalable solutions based on hydrogen that contribute to achieving better energy for everyone.

H2Vector Energy Technologies S.L. was born with the aim of offering new solutions addressed to the adoption of a self-sufficient, circular and climate-neutral energy model.

SECTORS

Our products and developments facilitate the transition to cleaner energy in different sectors and applications.

- Industrial machinery (forklifts, elevators, cranes, robots, cleaning machinery, among others).

- Mobility in the agricultural sector.

- Fuel cell light vehicles, trucks, boats or motorcycles.

- Electricity and heat generation system in hotels, homes and recreation centers.

HYDROGEN SOLUTIONS FOR A SUSTAINABLE FUTURE

WHERE WE ACT

Energy models based on green Hydrogen.

H2

O2

H20

Energy Security

Ssytems

Sustainable

Clean Tech

RESEARCH AND DEVELOPMENT

INNOVATIVE IDEAS FOR SUSTAINABLE SOLUTIONS

TECHNOLOGICAL DEVELOPMENTS TOWARDS A NEW ENERGY MODEL

PRODUCTS

Product development is H2Vector´s heart and soul.

Our products seize the following key concepts:

- Adaptability to your Use case

- Easy to Install and Operate

- Smart process integration and interaction. Control your energy flow.

VECTOR SERIES

A Hydrogen Energy Management System to take full advantage of your renewable energy.

PET SERIES

Fuel cell systems designed to provide green energy in stationary and mobile applications.

Vector2DYNA - HYDROGEN SUPPLIER

Easy, quick and safe access to your new environmentally friendly fuel.

VECTOR SERIES

SISTEMA DE GESTIÓN DE ENERGÍA DE HIDRÓGENO

The VECTOR Series products allows maximum use of renewable energy sources, using hydrogen to store their surpluses.

HYDROGEN ENERGY MANAGEMENT SYSTEM (HEMS)

MOBILITY APPLICATIONS

H2

FUEL CELL

HEAT SUPPLY

COMPRESSION UNIT

AUTOMATED & CONNECTED

ANY RENEWABLE SOURCES

SCALABLE

AC OUTLET

ELECTROYSER

WATER TREATMENT PLANT

CO2

neutral

0% CO2 EMISSIONS

OUTDOOR / INDOOR

PLUG & PLAY

MOBILITY APPLICATIONS

A sustainable solution that provides electricity and heat, without interruptions or CO2 emissions.

Designed and manufactured with strict controls, risk analysis (Hazop / Sil) and CE certification, for efficient and safe energy management.

UTILITY MODEL – Publication number: ES1271780, Owner project: H2Vector Energy Technologies S.L.

| HYDROGEN ENERGY MANAGEMENT SYSTEM (HEMS) | Technical Specifications |
| --- | --- |

| COMPARATIVE TABLE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VECTOR SERIES |  | VECTOR 10 |  |  | VECTOR 20 |  |  | VECTOR 40 |  |  | VECTOR 80 |  | VECTOR 160 |  |
| MODEL |  | Vector 10 STD | Vector 10 + | Vector 10 Premium | Vector 20 | Vector 20 HRS | Vector 20 P2X | Vector 40 | Vector 40 HRS | Vector 40 P2X | Vector 80 HRS | Vector 80 P2X | Vector 160 HRS | Vector 160 P2X |
| HYDROGEN PRODUCTION | Number of Electrolysers | 1 |  |  | 2 |  |  | 4 |  |  | 8 |  | 16 |  |
|  | Hydrogen Production | 0,5 Nm3/h |  |  | 1 Nm3/h |  |  | 2 Nm3/h |  |  | 4 Nm3/h |  | 8 Nm3/h |  |
|  | Hydrogen Outlet Pressure | Up to 350 barg |  |  | Up to 350 barg |  |  | Up to 350 barg |  |  | Up to 350 barg |  | Up to 350 barg |  |
| ELECTRICAL AND HEAT PRODUCTION | Equivalent Fuel Cell | PET-7 |  |  | PET-7 |  |  | PET-13 |  |  | 2 x PET-10 |  | 2 x PET-13 |  |
|  | Technology | PEM |  |  | PEM |  |  | PEM |  |  | PEM |  | PEM |  |
|  | Maximum Electricity Production (Gross) | 6,8 kW |  |  | 6,8 kW |  |  | 13,6 kW |  |  | 21,2 kW |  | 27,2 kW |  |
|  | Maximum Heat Production | 6,8 kW |  |  | 6,8 kW |  |  | 13,6 kW |  |  | 21,2 kW |  | 27,2 kW |  |
|  | Output Option AC 400 V 3P or DC 25 - 800 V |  |  |  |  |  |  |  |  |  |  |  |  |  |
| HYDROGEN REFUELING STATION (HRS) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

DC Output Voltage:

Vector 10: VDC 25-80

Vector 20: VDC 25-80

Vector 40: VDC 100-300

Vector 80: VDC 220-740

Vector 160: VDC 200-780

| HYDROGEN ENERGY MANAGEMENT SYSTEM (HEMS) |  |  | TECHNICAL SPECIFICATIONS |  |
| --- | --- | --- | --- | --- |
|  |  | VECTOR 10 |  | VECTOR 20 + |
| HYDROGEN PRODUCTION |  |  |  |  |
| Number of Electrolysers |  | 1 |  | 2 |
| Hydrogen Production Capacity |  | 0,5 Nm3/h |  | 1 Nm3/h |
| Hydrogen Production Quality |  | 99,9% 3 |  | 99,9% 3 |
| Hydrogen Output Pressure |  | up to 350 barg |  | up to 350 barg |
| Power Consumption with BOP |  | 6 kWh rated peak |  | 10 kWh rated peak 1 |
| Feed Water Quality |  | < 2 μS/cm |  | < 2 μS/cm |
| Feed Water Inlet Pressure |  | 1 - 4 barg |  | 1 - 4 barg |
| Electrolyser Operational Hours |  | >70.000 h |  | >70.000 h |
| Consumption in Hydrogen Production |  | 2,5 – 3,5 kWh |  | 5 – 10 kWh |
| ELECTRICAL AND HEAT PRODUCTION |  |  |  |  |
| Fuel Cell Model (FC) |  | PET-7 |  | PET-7 |
| Peak Power Output DC |  | 6,8 kW Electrical + 6,8 kW Heat |  | 6,8 kW Electrical + 6,8 kW Heat |
| Voltage DC 4 |  | 25 - 80 V |  | 25 - 80 V |
| Current DC |  | 0 - 250 A |  | 0 - 250 A |
| Auxiliary Electricity Consumption + Heat Generation |  | 1,5 kWh |  | 1,5 kWh |
| Maximum Hydrogen Consumption |  | 80 Nl/min |  | 80 Nl/min |
| External Fuel Minimum Quality |  | Grade D ISO 14687-2:2008 |  | Grade D ISO 14687-2:2008 |
| Fuel Cell Operational Hours |  | 24.000 h |  | 24.000 h |
| GENERAL |  |  |  |  |
| Cooling System |  | Air or Water cooled |  | Air or Water cooled |
| Closed Cooling Water Quality |  | < 10 μS/cm |  | < 10 μS/cm |
| Open Cooling Water Pressure |  | 1 - 10 barg |  | 1 - 10 barg |
| Open Cooling Water Temperature |  | < 50 ºC |  | < 50 ºC |
| Room Temperature |  | 5 - 45 ºC |  | 5 - 45 ºC |
| Dimensions (mm) (WxDxH) |  | 1000 x 650 x 2000 |  | 1000 x 650 x 2000 |
| HYDROGEN VEHICLE REFUELING STATION |  |  |  |  |
| FCV Supply |  | Optional 3 |  | Optional 3 |

1 Air compression power consumption accounted. Air compression unit NOT included.

2 Output option to choose between AC 400V 3P or DC 500V.

3 Vector 10 HRS, Vector 10 P2X, Vector 20 HRS and Vector 20 P2X models have a refueling dispenser for hydrogen vehicles at 350 barg (pipeline up to 500 barg), with delivered hydrogen quality of 99.999%.

| HYDROGEN ENERGY MANAGEMENT SYSTEM (HEMS) |  |  | TECHNICAL SPECIFICATIONS |  |
| --- | --- | --- | --- | --- |
|  |  | VECTOR 40 |  | VECTOR 80 |
| HYDROGEN PRODUCTION |  |  |  |  |
| Number of Electrolysers |  | 4 |  | 8 |
| Hydrogen Production Capacity |  | 2 Nm3/h |  | 4 Nm3/h |
| Hydrogen Production Quality |  | 99,9% 3 |  | 99,999% |
| Hydrogen Output Pressure |  | up to 350 barg |  | up to 350 barg |
| Power Consumption with BOP |  | 22 kWh rated peak 1 |  | 32 kWh rated peak 1 |
| Feed Water Quality |  | < 2 μS/cm |  | < 2 μS/cm |
| Feed Water Inlet Pressure |  | 1 - 4 barg |  | 1 - 4 barg |
| Electrolyser Operational Hours |  | >70.000 h |  | >70.000 h |
| Consumption in Hydrogen Production |  | 10 – 22 kWh |  | 20 – 32 kWh |
| ELECTRICAL AND HEAT PRODUCTION |  |  |  |  |
| Fuel Cell Model (FC) |  | PET-13 |  | PET-10 |
| Peak Power Output DC |  | 13,6 kW Electrical + 13,6 kW Heat |  | 21,2 kW Electrical + 21,2 kW Heat |
| Voltage DC 4 |  | 93.2 - 58.9 V |  | 145,6 – 92,2 V |
| Current DC |  | 0 - 230 A |  | 0 - 230 A |
| Auxiliary Electricity Consumption + Heat Generation |  | 2,25 kWh |  | 4 kWh |
| Maximum Hydrogen Consumption |  | 160 Nl/min |  | 240 Nl/min |
| External Fuel Minimum Quality |  | Grade D ISO 14687-2:2008 |  | Grade D ISO 14687-2:2008 |
| Fuel Cell Operational Hours |  | 24.000 h |  | 24.000 h |
| GENERAL |  |  |  |  |
| Cooling System |  | Air or Water cooled |  | Air or Water cooled |
| Closed Cooling Water Quality |  | < 10 μS/cm |  | < 10 μS/cm |
| Open Cooling Water Pressure |  | 1 - 10 barg |  | 1 - 10 barg |
| Open Cooling Water Temperature |  | < 50 ºC |  | < 50 ºC |
| Room Temperature |  | 5 - 45 ºC |  | 5 - 45 ºC |
| Dimensions (mm) (WxDxH) |  | 600 x 800 x 2200 + 1200 x 650 x 1500 |  | 2 x (600 x 800 x 2200) + 1200 x 650 x 1500 |
| HYDROGEN VEHICLE REFUELING STATION |  |  |  |  |
| FCV Supply |  | Optional 3 |  | Included 3 |

1 Air compression power consumption accounted. Air compression unit NOT included.

2 Output option to choose between AC 400V 3P or DC 500V.

3 Vector 40 HRS, Vector 40 P2X, Vector 80 HRS and Vector 80 P2X models have a refueling dispenser for hydrogen vehicles at 350 barg (pipeline up to 500 barg), with delivered hydrogen quality of 99.999%.

4 Fixed voltage in DC, customizable 25 – 800 V.

| HYDROGEN ENERGY MANAGEMENT SYSTEM (HEMS) |  |  | TECHNICAL SPECIFICATIONS |  |
| --- | --- | --- | --- | --- |
|  |  |  |  | VECTOR 160 |
| HYDROGEN PRODUCTION |  |  |  |  |
| Number of Electrolysers |  |  |  | 16 |
| Hydrogen Production Capacity |  |  |  | 8 Nm3/h |
| Hydrogen Production Quality |  |  |  | 99,999% |
| Hydrogen Output Pressure |  |  |  | up to 350 barg |
| Power Consumption with BOP |  |  |  | 51 kWh rated peak 1 |
| Feed Water Quality |  |  |  | < 2 μS/cm |
| Feed Water Inlet Pressure |  |  |  | 1 - 4 barg |
| Electrolyser Operational Hours |  |  |  | >70.000 h |
| Consumption in Hydrogen Production |  |  |  | 40 – 51 kWh |
| ELECTRICAL AND HEAT PRODUCTION |  |  |  |  |
| Fuel Cell Model (FC) |  |  |  | PET-13 |
| Peak Power Output DC |  |  |  | 27,2 kW Electrical + 27,2 kW Heat |
| Voltage DC 4 |  |  |  | 186,4 – 117,8 V |
| Current DC |  |  |  | 0 - 230 A |
| Auxiliary Electricity Consumption + Heat Generation |  |  |  | 5 kWh |
| Maximum Hydrogen Consumption |  |  |  | 320 Nl/min |
| External Fuel Minimum Quality |  |  |  | Grade D ISO 14687-2:2008 |
| Fuel Cell Operational Hours |  |  |  | 24.000 h |
| GENERAL |  |  |  |  |
| Cooling System |  |  |  | Air or Water cooled |
| Closed Cooling Water Quality |  |  |  | < 10 μS/cm |
| Open Cooling Water Pressure |  |  |  | 1 - 10 barg |
| Open Cooling Water Temperature |  |  |  | < 50 ºC |
| Room Temperature |  |  |  | 5 - 45 ºC |
| Dimensions (mm) (WxDxH) |  |  |  | 4 x (600 x 800 x 2200) + 1200 x 650 x 1500 |
| HYDROGEN VEHICLE REFUELING STATION |  |  |  |  |
| FCV Supply |  |  |  | Included 3 |

1 Air compression power consumption accounted. Air compression unit NOT included.

2 Output option to choose between AC 400V 3P or DC 500V.

3 Vector 160 HRS and Vector 160 P2X models have a refueling dispenser for hydrogen vehicles at 350 barg (pipeline up to 500 barg), with delivered hydrogen quality of 99.999%.

4 Fixed voltage in DC, customizable 25 – 800 V.

PET SERIES

AC OR DC OUTPUT

CO2

neutral

0% CO2 EMISSIONS

SCALABLE

AUTOMATED & CONNECTED

PLUG & PLAY

OUTDOOR / INDOOR

MOBILITY APPLICATIONS

H2

WATER TREATMENT PLANT

HEAT SUPPLY

FUEL CELL

COMPRESSION UNIT

PET Series consists of energy enabling equipment, which combines energy delivery and heat generation, all in an efficient and environmentally friendly way.

| POWER ENABLING TECHNOLOGY (PET) | TECHNICAL SPECIFICATIONS |
| --- | --- |

| COMPARATIVE TABLE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PET SERIES | PET7 |  |  | PET10 |  |  | PET13 |  |  | PET20 |  | PET26 |  |  | PET50 |  | PET100 |  | PET250 |  |
| MODEL | PET-7 STD | PET-7 + | PET-7 PREMIUM | PET-10-STD | PET-10 + | PET-10 PREMIUM | PET-13-STD | PET-13 + | PET-13 PREMIUM | PET-20 + | PET-20 PREMIUM | PET-26 + | PET-26 PREMIUM |  | PET-50 + | PET-50 PREMIUM | PET-100 + | PET-100 PREMIUM | PET-250 + | PET-250 PREMIUM |
| Number of PEM Fuel Cell (FC) Stacks | 1 |  |  | 1 |  |  | 1 |  |  | 2 |  | 2 |  |  | 4 |  | 8 |  | 20 |  |
| Maximum Electricity Production (Gross) | 6,8 kW |  |  | 10,6 kW |  |  | 13,6 kW |  |  | 21,2 kW |  | 27,2 kW |  |  | 54,4 kW |  | 108,8 kW |  | 272 kW |  |
| Maximum Heat Production | 6,8 kW |  |  | 10,6 kW |  |  | 13,6 kW |  |  | 21,2 kW |  | 27,2 kW |  |  | 54,4 kW |  | 108,8 kW |  | 272 kW |  |
| Cooling System |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AC 400 V 3P Output |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| DC V 25 - 800 Output |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

DC Output Voltage:

PET-7-DC/DC: VDC -25-80

PET-10-DC/DC: VDC -42-80

PET-13-DC/DC: VDC 100-300

PET-20-DC/DC: VDC 220-740

PET-26-DC/DC: VDC 200-780

PET-50-DC/DC: VDC 340-800

| POWER ENABLING TECHNOLOGY (PET) |  |  | TECHNICAL SPECIFICATIONS |  |
| --- | --- | --- | --- | --- |
|  |  | PET-7 |  | PET-10 |
| ELECTRICAL AND HEAT PRODUCTION |  |  |  |  |
| Number of Fuel Cell Stacks |  | 1 |  | 1 |
| Peak Power Output DC |  | 6,8 kW Electrical + 6,8 kW Heat |  | 10,6 kW Electrical + 10,6 kW Heat |
| DC Net Electric Power Delivered (Max. BOL) |  | 5,0 kW |  | 9,8 kW |
| AC Net Electric Power Delivered (Max. BOL) |  | 4,0 kW |  | 9,0 kW |
| DC Voltage |  | 25 - 80 V |  | 42 - 80 V |
| DC Current |  | 0 - 250 A |  | 0 - 250 A |
| Auxiliary Electricity Consumption + Heat Generation |  | 1,5 kWh |  | 1,75 kWh |
| Maximum Hydrogen Consumption |  | 80 Nl/min |  | 120 Nl/min |
| External Fuel Minimum Quality |  | Grade D ISO 14687-2:2008 |  | Grade D ISO 14687-2:2008 |
| Supply Pressure |  | 0,35 barg |  | 0,35 barg |
| Supply Pressure (Optional) |  | up to 350 barg |  | up to 350 barg |
| Fuel Cell Operational Hours |  | 24.000 h |  | 24.000 h |
| GENERAL |  |  |  |  |
| Water Treatment Plant |  | Included |  | Included |
| Cooling System |  | Water cooled |  | Water cooled |
| Closed Cooling Water Quality |  | < 10 μS/cm |  | < 10 μS/cm |
| Open Cooling Water Pressure |  | 1 - 10 barg |  | 1 - 10 barg |
| Open Cooling Water Temperature |  | < 50 ºC |  | < 50 ºC |
| Room Temperature |  | 0 - 45 ºC |  | 0 - 45 ºC |
| Dimensions (mm) (WxDxH) |  | 1200 x 650 x 1500 |  | 1200 x 650 x 1500 |

| POWER ENABLING TECHNOLOGY (PET) |  |  | TECHNICAL SPECIFICATIONS |  |
| --- | --- | --- | --- | --- |
|  |  | PET-13 |  | PET-20 |
| ELECTRICAL AND HEAT PRODUCTION |  |  |  |  |
| Number of Fuel Cell Stacks |  | 1 |  | 2 |
| Peak Power Output DC |  | 13,6 kW Electrical + 13,6 kW Heat |  | 21,2 kW Electrical + 21,2 kW Heat |
| DC Net Electric Power Delivered (Max. BOL) |  | 11,0 kW |  | 16,9 kW |
| AC Net Electric Power Delivered (Max. BOL) |  | 10,0 kW |  | - |
| DC Voltage |  | 93,2 – 58,9 V |  | 145,6 – 92,2 V |
| DC Current |  | 0 - 230 A |  | 0 - 230 A |
| Auxiliary Electricity Consumption + Heat Generation |  | 2,25 kWh |  | 4 kWh |
| Maximum Hydrogen Consumption |  | 160 Nl/min |  | 240 Nl/min |
| External Fuel Minimum Quality |  | Grade D ISO 14687-2:2008 |  | Grade D ISO 14687-2:2008 |
| Supply Pressure |  | 0,35 barg |  | 0,35 barg |
| Supply Pressure (Optional) |  | up to 350 barg |  | up to 350 barg |
| Fuel Cell Operational Hours |  | 24.000 h |  | 24.000 h |
| GENERAL |  |  |  |  |
| Water Treatment Plant |  | Included |  | Included |
| Cooling System |  | Water cooled |  | Water cooled |
| Closed Cooling Water Quality |  | < 10 μS/cm |  | < 10 μS/cm |
| Open Cooling Water Pressure |  | 1 - 10 barg |  | 1 - 10 barg |
| Open Cooling Water Temperature |  | < 50 ºC |  | < 50 ºC |
| Room Temperature |  | 0 - 45 ºC |  | 0 - 45 ºC |
| Dimensions (mm) (WxDxH) |  | 1200 x 650 x 1500 |  |  |

| POWER ENABLING TECHNOLOGY (PET) |  |  | TECHNICAL SPECIFICATIONS |  |
| --- | --- | --- | --- | --- |
|  |  | PET-26 |  | PET-50 |
| ELECTRICAL AND HEAT PRODUCTION |  |  |  |  |
| Number of Fuel Cell Stacks |  | 1 |  | 4 |
| Peak Power Output DC |  | 27,2 kW Electrical + 27,2 kW Heat |  | 54,4 kW Electrical + 54,4 kW Heat |
| DC Net Electric Power Delivered (Max. BOL) |  | 21,9 kW |  | 47,8 kW |
| DC Voltage (BOL) |  | 186,4 – 117,8 V |  | 372,8 – 235,6 V |
| DC Current |  | 0 - 230 A |  | 0 - 230 A |
| Auxiliary Electricity Consumption + Heat Generation |  | 5 kWh |  | 6,25 kWh |
| Maximum Hydrogen Consumption |  | 320 Nl/min |  | 640 Nl/min |
| External Fuel Minimum Quality |  | Grade D ISO 14687-2:2008 |  | Grade D ISO 14687-2:2008 |
| Supply Pressure |  | 0,35 barg |  | 0,35 barg |
| Supply Pressure (Optional) |  | up to 350 barg |  | up to 350 barg |
| Fuel Cell Operational Hours |  | 24.000 h |  | 24.000 h |
| GENERAL |  |  |  |  |
| Water Treatment Plant |  | Included |  | Not included |
| Cooling System |  | Water cooled |  | Water cooled |
| Closed Cooling Water Quality |  | < 10 μS/cm |  | < 10 μS/cm |
| Open Cooling Water Pressure |  | 1 - 10 barg |  | 1 - 10 barg |
| Open Cooling Water Temperature |  | < 50 ºC |  | < 50 ºC |
| Room Temperature |  | 0 - 60 ºC |  | 0 - 60 ºC |
| Dimensions (mm) (WxDxH) |  |  |  |  |

| POWER ENABLING TECHNOLOGY (PET) |  |  | TECHNICAL SPECIFICATIONS |  |
| --- | --- | --- | --- | --- |
|  |  | PET-100 |  | PET-250 |
| ELECTRICAL AND HEAT PRODUCTION |  |  |  |  |
| Number of Fuel Cell Stacks |  | 8 |  | 20 |
| Peak Power Output DC |  | 108,8 kW Electrical + 108,8 kW Heat |  | 272 kW Electrical + 272 kW Heat |
| DC Net Electric Power Delivered (Max. BOL) |  | 98,9 kW |  | 247,3 kW |
| DC Voltage (BOL) |  | 745,6 – 471,2 V |  | 1.864 – 1.178 V |
| DC Current |  | 0 – 230 A |  | 0 - 230 A |
| Auxiliary Electricity Consumption + Heat Generation |  | 9,6 kWh |  | 24 kWh |
| Maximum Hydrogen Consumption |  | 1.280 Nl/min |  | 3.200 Nl/min |
| External Fuel Minimum Quality |  | Grade D ISO 14687-2:2008 |  | Grade D ISO 14687-2:2008 |
| Supply Pressure |  | 0,35 barg |  | 0,35 barg |
| Supply Pressure (Optional) |  | up to 350 barg |  | up to 350 barg |
| Fuel Cell Operational Hours |  | 24.000 h |  | 24.000 h |
| GENERAL |  |  |  |  |
| Water Treatment Plant |  | Not included |  | Not included |
| Cooling System |  | Water cooled |  | Water cooled |
| Closed Cooling Water Quality |  | < 10 μS/cm |  | < 10 μS/cm |
| Open Cooling Water Pressure |  | 1 - 10 barg |  | 1 - 10 barg |
| Open Cooling Water Temperature |  | < 50 ºC |  | < 50 ºC |
| Room Temperature |  | 0 - 45 ºC |  | 0 - 45 ºC |
| Dimensions (mm) (WxDxH) |  |  |  |  |

ISPENSADOR DE HIDRÓADOR DE HIDRÓGENO

Vector2DYNA – HYDROGEN SUPPLIER

Our goal is to provide our customers with access to mobility through hydrogen in any sector and field of application, always in a sustainable and affordable way.

For this, our Hydrogen Supplier makes it possible to dispose of this new fuel in different outlet pressure requirements, quickly and safely.

Designed to handle refueling protocols at various scenarios, Vector2DYNA enables and ensures the smartest and fastest response:

- SAE J2601 Protocol

- SAE J2601-2 Protocol

- H2Vector Protocol – Maintains SAE safety requirements and adapts to customer installation

UTILITY MODEL – Publication number ES1290274, Owner project: H2Vector Energy Technologies S.L.

FCV Applications

Hydrogen Delivery using the H2Vector Supplier: Vector2DYNA

Hydrogen Compression to Pressure Specified by Application

Hydrogen Supplyand Storage

© 2025, H2Vector Energy Technologies, S.L., Spain. All rights reserved. Designs and specifications are subject to change without notice or obligation. Read all safety instructions in the manual before usage.

info@h2vector.com

www.h2vector.com

H2Vector Energy Technologies, S.L.

Thrusting Ideas

Certifications:                                                           Partners:                                                                      Membership: