## Template
Description of Green Infrastructure Opportunity
A green/complete street concept design was developed for two blocks of 2nd Street, Baywood. Currently, stormwater runoff is routed along 2nd Street and conveyed, untreated, into two inlets located at the curb/gutter location within the street right-of-way. The runoff is discharged via outfall at the beach area of the estuary, near the Baywood Pier. This area is used frequently by the public for passive and active recreation. Additionally, the estuary is an important ecological resource to be protected. Rather than evaluate a full street reconstruction that would be very costly, targeted improvements that leverage the existing landscaped areas and make use of the wide street right-of-way, were evaluated. The concept design integrates stormwater management, improves pedestrian safety and is consistent with the community's planning effort, led by San Luis Obispo County. The design also includes pedestrian safety improvements that slow traffic and provide safe crossing areas. Effort was taken to create a concept design that was appropriate for this particular neighborhood, which includes significant foot traffic in the street, a weekly farmer's market, street fairs and a informal neighborhood atmosphere.
|  | Design Summary |  | Construction Cost
|  | SCM Type | Total SCM Area (ft2) | see cost estimating worksheet in this Excel file
|  | Biofiltration (lower block) | 4000 | $45/ft2 | 180000
|  | Bioretention (upper block) | 7000 | $45ft2 | 315000
Sizing and design notes: The design assumes use of bioretention design on the upper (NW) portion of the block. A biofiltration design is used on the lower (SE & SW) block as high groundwater is not conducive to infiltration. The biofiltration design includes 24" of bioretention soil and 12" aggregate depths. Use of an underdrain versus passive surface overflow will require further analysis to ensure proper drawdown. Biofiltration and bioretention engineering standards can be found at centralcoastlidi.org. The estimated DMA Effective Impervious Areas were used for volume performance. See detailed estimated performance calculations provided as part of this Excel file.
Stormwater Performance
| The capacity of the concept design exceeds the water quality objective to treat and/or infiltrate the 85th percentile, 24-hr storm event. The lower block (SW & SE) includes a biofiltration design to target treatment rather than infiltration due to the high groundwater table. The upper block (NW & NE) includes a water quality treatment and infiltration focus and the design also exceeds the 85th percentile, 24-hr storm event objective. The opportunity for stormwater "banking" with this design can support future growth stormwater quality control requirements. Performance details are provided in the "Volume Performance" tab of this Excel file. | Site Description
|  | Location |  | 2nd Street, Baywood between Santa Ysabel and El Morro Avenue.
|  | Street/parcel type |  | Collector
|  | Stormwater System |  | Curb/gutter/inlet/pipe/outfall
|  | Receiving Water |  | Morro Bay Estuary
Disclaimer: All elements of this design are concept only.
2nd Street Baywood, Green Street Project
N
N

## Volume Performance
SLO County - 2nd Street
85th % Rain Depth (in) | 1
DMA #1 (SE)
Tirbutary Area (ac) | 0.30698 |  | SF | 13372 | 1/2 street only (crowned street)
% Impervious | 0.98 |  |  |  |  | DMAs were defined as the contributing street right of way area for each block and each half block (due to crowned nature of the roadway) therefore, four total DMAs for the two blocks. Private parcel contributions appear to be negligable but would need to be reevaluated if future development routes runoff to the street.
C Value | 0.85695
85th % Runoff Volume Required (cf) | 954.9288
85% Treatment Flowrate Required (cfs) | 0.052613 |  | 0.2 | in/hr for treatment intensity
Treatment DMA #1 (SE)
Ponded Area for Biofiltration Required (sf) | 454.5777 |  | 5 | in/hr for bioretention soil infiltration rate
Ponded Area for Biofiltration Provided (sf) | 2239
Treatment Flowrate Provided (cfs) | 0.25914 | treatment area can surpass 85th percentile event treatment |  |  |  | Biofiltration (square feet) (SW & SE block)
3954
Area Pavers (sf) | 2630
Depth of paver base (in) | 16 |  |  |  |  | Bioretention (square feet) (NW block)
Paver base void % | 40 |  |  |  |  | 5060
85th % Runoff Volume in Paver Area Only (cf) | 187.815
Volume Provided in Paver Area Only (cf) | 1402.6667 |  |  | Pavers self treat 85% storm with no runoff and remainder of street adding additional capacity if desired.
DMA #2 (NE)
Tirbutary Area (ac) | 0.3079 |  | SF | 13412 | 1/2 street only (crownded street)
% Impervious | 0.98
C Value | 0.85695
85th % Runoff Volume Required (cf) | 957.7853
Treatment DMA #2 (NE)
Area Pavers (sf) | 215
Depth of paver base (in) | 16
Paver base void % | 40
Volume Provided (cf) | 114.6667
Total Volume Provided DMA #2 (SE) | 114.6667 | treatment areas is only pevious paver cross-walk. Conventional landscape design was assumed for the NE street side given constraints from adjacent buildings. Filterra type tree units could be considered if additionals WQ treatment is desired
DMA #3 (NW)
Tirbutary Area (ac) | 0.29008 |  | SF | 12636 | 1/2 street only
% Impervious | 0.98
C Value | 0.85695
85th % Runoff Volume Required (cf) | 902.3691
Treatment DMA #3 (NW)
Area Bioretention Soil (sf) | 5060
Avg Ponding Depth (in) | 6
Planting Soil Depth (in) | 24
Planting Soil void % | 30
Drain Rock Depth (in) | 12
Drain Rock void % | 40
Volume Provided (cf) | 7590 | volume benefit from bioretention
Area Pavers (sf) | 5000
Depth of paver base (in) | 16
Paver base void % | 40
Volume Provided (cf) | 2666.6667
Total Volume Provided DMA #1 (SE) | 10256.6667 | Pavers plus bioretention
DMA #4 (SW)
Tirbutary Area (ac) | 0.30491 |  | SF | 13282 | 1/2 street only
% Impervious | 0.98
C Value | 0.85695
85th % Runoff Volume Required (cf) | 948.5016
85% Treatment Flowrate Required (cfs) | 0.052259 |  | 0.2 | in/hr for treatment intensity
Treatment DMA #4 (SW)
Ponded Area for Biofiltration Required (sf) | 451.5181 |  | 5 | in/hr for bioretention soil infiltration rate
Ponded Area for Biofiltration Provided (sf) | 1715
Treatment Flowrate Provided (cfs) | 0.1985 | greatly exceeds 85th percentile
Area Pavers (sf) | 610
Depth of paver base (in) | 16
Paver base void % | 40
85th % Runoff Volume in Paver Area Only (cf) | 43.5617
Volume Provided in Paver Area Only (cf) | 325.3333 |  |  | Pavers self treat 85% storm with no runoff

## Cost Estimate
Bioretention / biofiltration average square foot cost construct |  |  | Notes |  | Pervious Paver average square foot cost design/construct ($)
Complexity | lower range | upper range | Simple rain garden design/construct tend to be at the lower cost range. As complexity increases due to site preparation, additional infrastructure considerations, etc., the cost increases. The higher end costs reflect designs that may include connection to existing infrastructure, site stability elements (e.g., geotechnical design elements). There may also be a higher cost associated with constructing a small SCM where construction does not provide an economy of scale for the contractor and cost per square foot tends to be higher than if the single facility were replicated several times and put out to construction bid as one project. The $45 / square foot if often used as an average cost for street right-of-way bioretention in the Central Coast region as it is backed by data from several projects in the region and consistent with statewide and national averages. |  | material and installation |  | 15
Low | 5 | 20 |  |  | site preparation |  | 10
Moderate | 30 | 50
High | 50 | 150 | [5 empty] | 2nd Street, Baywood construction costs used for concept design was $45/ft2, which is average for this type of green street design in the Central Coast Region. Higher than the rain garden typical costs provided in the table left to account for underdrain, curb construction, etc. More refined cost estimates should be conducted if the project is pursued.
Typical Asphalt Demo to Rain Garden*
Item No. | Description | Quantity | Unit | Unit Cost | Cost
Demolition Services
1 | Mobilization (5%) | 1 | LS | 1825 | 1825
2 | Sawcut asphalt | 120 | LF | 5 | 600
3 | Excavation of asphalt/sub-base (average 6" depth) | 20 | CY | 40 | 800
4 | Excavation of earthwork (average 18" depth) | 60 | CY | 30 | 1800
5 | Hauling of earthwork | 1 | LS | 400 | 400
Site Improvements
6 | 6"x 24" concrete street curb & gravel sub-base | 270 | LF | 25 | 6750
7 | 12" wide asphalt patch | 120 | SF | 3 | 360
8 | Rototill native soil conditions | 1000 | SF | 0.35 | 350
9 | Deliver Topsoil & Mulch | 1 | LS | 400 | 400
10 | Topsoil Mix (18" Import) | 55 | CY | 80 | 4400
11 | Fine Grading Topsoil & Mulch | 1000 | CY | 0.5 | 500
12 | Irrigation** | 1000 | SF | 4 | 4000
13 | Landscape (1 gal containers @ 24" O.C) | 250 | EA | 12 | 3000
14 | Street Trees (2" Caliper) | 4 | EA | 500 | 2000
14 | Entry Curb Cut and Concrete Forebay Construction | 1 | EA | 1500 | 1500
15 | Exit Curb Cut | 1 | EA | 1000 | 1000
16 | 2" mulch layer | 6 | CY | 40 | 240
|  |  |  | Total Stormwater Rain Garden Area = | 29925 | 27125 | without trees or need to cut/remove asphalt
|  |  |  | Cost/SF | 29.925 | 27.125
* Assumes no underdrain, gravel storage, or major alterations/connections to storm pipe system.
** Assumes that a reasonable point-of-connection can be made at an adjacent water source