## Childrens Ward
Childrens Ward
Circuits | Areas | Total Sqft | Height | Total Volume (Cubic FT) | Total Area Load | Total No of People | Total Human & Equipment Load | Total Load (BTU/HR) | Total No of IDU | BTU per IDU | Type of Indoor | Indoor Model no | Remote controller (Japan Model) | kw Per indoor | Total capacity | Outdoor Model | Outdoor Qty | Outdoor Capacity
C1 | Ward 1 | 546 | 9 | 4914 | 36855 | 12 | 12000 | 48855 | 2 | 24427.5 | 4 Way casette | RCI-2.5FSKDN1Q | 1 | 7.1 | 14.2 | RAS-28CNBCMQ | 2 | 78.5
| Ward 2 | 480 | 9 | 4320 | 32400 | 12 | 12000 | 44400 | 2 | 22200 | 4 Way casette | RCI-2.5FSKDN1Q | 1 | 7.1 | 14.2
| Ward 3 | 550 | 9 | 4950 | 37125 | 12 | 12000 | 49125 | 2 | 24562.5 | 4 Way casette | RCI-2.5FSKDN1Q | 1 | 7.1 | 14.2
| Nurse Station | 713 | 9 | 6417 | 48127.5 | 20 | 18000 | 66127.5 | 2 | 24000 | 4 Way casette | RCI-2.5FSKDN1Q | 1 | 7.1 | 14.2
| Corridor 1 | 408 | 9 | 3672 | 25704 | 0 | 0 | 25704 | 2 | 12852 | 1 way casette | RCIS-1.3FSKDNQ | 1 | 3.6 | 7.2
| Dirty Utility Room | 90 | 9 | 810 | 5670 | 0 |  | 5670 | 1 | 9000 | 1 way casette | RCIS-1.0FSKDNQ | 1 | 2.8 | 2.8
| Tea room | 130 | 9 | 1170 | 8190 | 6 | 5000 | 13190 | 1 | 12000 | 1 way casette | RCIS-1.3FSKDNQ | 1 | 3.6 | 3.6
| Nurse room | 72 | 9 | 648 | 4536 | 2 | 2000 | 6536 | 1 | 9000 | 1 way casette | RCIS-1.0FSKDNQ | 1 | 2.8 | 2.8
C2 | Ward 4 | 528 | 9 | 4752 | 35640 | 12 | 12000 | 47640 | 2 | 23820 | 4 Way casette | RCI-2.5FSKDN1Q | 1 | 7.1 | 14.2 | RAS-28CNBCMQ | 2 | 78.5
| Ward 5 | 418 | 9 | 3762 | 28215 | 12 | 12000 | 40215 | 2 | 20107.5 | 4 Way casette | RCI-2.5FSKDN1Q | 1 | 7.1 | 14.2
| Ward 6 | 528 | 9 | 4752 | 35640 | 12 | 12000 | 47640 | 2 | 23820 | 4 Way casette | RCI-2.5FSKDN1Q | 1 | 7.1 | 14.2
| Nurse Station | 713 | 9 | 6417 | 48127.5 | 20 | 18000 | 66127.5 | 1 | 24000 | 4 Way casette | RCI-2.5FSKDN1Q | 1 | 7.1 | 7.1
| Corridor 2 | 408 | 9 | 3672 | 25704 | 0 | 0 | 25704 | 2 | 12852 | 1 way casette | RCIS-1.3FSKDNQ | 1 | 3.6 | 7.2
| Clean Utility room | 90 | 9 | 810 | 5670 | 0 |  | 5670 | 1 | 9000 | 1 way casette | RCIS-1.0FSKDNQ | 1 | 2.8 | 2.8
| Drug Store | 50 | 9 | 450 | 3150 | 2 | 2000 | 5150 | 1 | 9000 | 1 way casette | RCIS-1.0FSKDNQ | 1 | 2.8 | 2.8
| treatment room | 130 | 9 | 1170 | 8190 | 2 | 2000 | 10190 | 1 | 12000 | 1 way casette | RCIS-1.3FSKDNQ | 1 | 3.6 | 3.6
| Kids Play Area | 400 | 9 | 3600 | 25200 | 3 | 2750 | 27950 | 1 | 27950 | 4 Way casette | RCI 3.0FSKDN1Q | 1 | 8 | 8
| Ventilation Required | ACH per hour | Airflow (CMH) | Qty | Ducting
| KPI-200H-A-GQ1 | 4 to 6 | 2000 | 2 | PI Ducting