## BOQ
RELOCATION OF THREE (3) LPG STORAGE BULLET TANKS – THILAFUSHI SITE
BILL OF QUANTITIES (BOQ)
tem No. | Description | Unit | Quantity | Unit Rate | Amount
INSTRUCTIONS TO BIDDERS 1- The Bidder shall complete all shaded columns with their offered unit rates and extended amounts. 2- All rates shall be in [Insert Currency: USD / MVR] . 3- Rates shall include all labor, materials, equipment, consumables, supervision, overheads, and profit for the complete execution of the item as described. 4- Quantities are estimated based on the Scope of Work and Drawings. The Bidder shall verify all quantities and shall not claim additional payment for discrepancies unless formally varied by the Engineer. 5- Where a "Lump Sum" item is indicated, the Bidder shall provide a single inclusive price for the complete scope of that item. 6- The BOQ forms the basis for the Lump Sum Price Proposal and for valuation of progress payments and variations.
1 | MOBILIZATION, SITE SETUP & SAFETY
1.1 | Mobilization & Demobilization
1.1.1 | Mobilization of all plant, equipment, tools, and personnel to Thilafushi site, including all transportation, fuel, and logistical arrangements | Lump Sum | 1
1.1.2 | Demobilization of all plant, equipment, tools, and personnel from Thilafushi site upon project completion | Lump Sum | 1
1.2 | Site Establishment
1.2.1 | Establishment of contractor’s compound including office container, tool storage, first aid station, and welfare facilities (toilets, rest area, potable water) | Lump Sum | 1
1.2.2 | Temporary fencing and barricading of work areas (existing tank location and new foundation location) to isolate from operational areas | Meter | 200
1.2.3 | Installation of site signage (safety signs, project signage, directional signs) | Lump Sum | 1
1.3 | Safety System Implementation
1.3.1 | Provision of portable fire extinguishers (CO2 and dry powder) at all work locations | Each | 10
1.3.2 | Provision of multi-gas detectors (portable, calibrated) for continuous gas monitoring | Each | 4
1.3.3 | Implementation of Permit to Work (PTW) system including documentation and coordination | Lump Sum | 1
1.3.4 | Site safety induction for all contractor personnel | Lump Sum | 1
1.3.5 | Provision of emergency response equipment (stretcher, first aid kit, fire blanket, spill kit) | Lump Sum | 1
1.4 | Pre-Work Surveys
1.4.1 | Joint site survey with Engineer to verify existing tank locations, piping configurations, and ground conditions | Lump Sum | 1
1.4.2 | Identification and marking of existing underground utilities in new foundation areas | Lump Sum | 1
1.4.3 | Pre-work condition report documenting state of tanks, piping, and coatings prior to commencement | Lump Sum | 1
SECTION 1 TOTAL
2 | NEW FOUNDATION CONSTRUCTION (3 UNITS)
2.1 | Survey & Excavation
2.1.1 | Land survey and setting out of three (3) foundation locations as per FINAL drawing (Page 4) and RELOCATION drawings (Pages 6 & 9) | Lump Sum | 1
2.1.2 | Mechanical excavation of foundation pits to dimensions and levels shown on CONCRETE FOUNDATION details (Pages 3 & 5) | m³ | 45
2.2 | Subgrade & Blinding
2.2.1 | Compaction of subgrade to 95% Modified Proctor density | m² | 45
2.2.2 | Blinding concrete (C15) – 75mm thick | m³ | 3.4
2.3 | Reinforcement Steel
2.3.1 | Supply of high-yield deformed steel reinforcement bars (BS 4449 Grade B500B) | Ton | 3.5
2.3.2 | Cutting, bending, and fixing of reinforcement steel including spacers and chairs | Ton | 3.5
2.4 | Anchor Bolts & Embedded Plates
2.4.1 | Supply of galvanized anchor bolts (Grade 8.8) complete with nuts, washers, and levelling plates – as per foundation drawings | Each | 24
2.4.2 | Fabrication and installation of steel templates for anchor bolt positioning (tolerance ±3mm) | Each | 3
2.4.3 | Supply and installation of embedded steel plates (sole plates, base plates) as per drawings | Kg | 150
2.5 | Formwork
2.5.1 | Supply, erection, and stripping of formwork for foundations (steel or plyform) | m² | 45
2.6 | Concrete Works
2.6.1 | Supply of ready-mix concrete (C30/37) with marine exposure resistance | m³ | 22.5
2.6.2 | Pouring, compaction (mechanical vibrators), and finishing of concrete | m³ | 22.5
2.6.3 | Curing of concrete (wet hessian, polythene sheeting, or curing compound) for minimum 7 days | m² | 45
2.7 | Quality Control
2.7.1 | Concrete mix design submission and approval | Lump Sum | 1
2.7.2 | Slump testing on each concrete pour | Each | 3
2.7.3 | Concrete cube sampling, curing, and compressive strength testing (7-day and 28-day) | Set | 3
SECTION 2 TOTAL
3 | PREPARATION, DISCONNECTION & API SUPERVISION
3.1 | System Isolation & Purging
3.1.1 | System isolation and Lockout/Tagout (LOTO) procedure implementation for three (3) tanks | Lump Sum | 1
3.1.2 | Supply of nitrogen for purging of tanks and piping systems | m³ | 200
3.1.3 | Gas-free certification including continuous atmospheric monitoring during disconnection | Lump Sum | 1
3.2 | Pipeline Disconnection
3.2.1 | Disconnection of Main LPG Line (2" diameter) – mechanical cutting and capping | Each | 3
3.2.2 | Disconnection of Main LPG Line (3" diameter) – mechanical cutting and capping | Each | 3
3.2.3 | Disconnection of Main LPG Line (4" diameter) – mechanical cutting and capping | Each | 3
3.2.4 | Disconnection of Main LPG Line (6" diameter) – mechanical cutting and capping | Each | 3
3.2.5 | Disconnection of LPG Return Line (2" diameter) – mechanical cutting and capping | Each | 3
3.2.6 | Disconnection of Vapour Line (2" diameter) – mechanical cutting and capping | Each | 3
3.2.7 | Disconnection of Hydraulic Valve lines (small bore tubing) – capping | Each | 6
3.2.8 | Supply and installation of blind flanges or welded caps on all disconnected piping ends | Each | 24
3.3 | Electrical & Instrumentation
3.3.1 | De-energizing and disconnection of electrical supply to hydraulic valve actuators | Each | 6
3.3.2 | Disconnection of instrumentation lines (pressure transmitters, level gauges, temperature sensors) | Each | 12
3.3.3 | Tagging of all disconnected cables, tubing, and conduits for reconnection | Each | 30
3.4 | Tank Preparation
3.4.1 | Removal of loose external attachments and insulation | Lump Sum | 1
3.4.2 | Inspection of lifting lugs and installation of certified lifting beams if required | Lump Sum | 1
3.5 | API Engineer Supervision
3.5.1 | API Engineer (API 653/570 certified) on-site supervision during disconnection phase | Lump Sum | 1
SECTION 3 TOTAL
4 | TANK LIFTING & RELOCATION (3 TANKS)
4.1 | Lifting Engineering
4.1.1 | Preparation and submission of detailed engineered lifting plan including load calculations, crane positioning, rigging configuration, and ground bearing pressure analysis | Lump Sum | 1
4.1.2 | Third-party verification of lifting plan (if required) | Lump Sum | 1
4.2 | Crane & Lifting Equipment
4.2.1 | Mobilization of 80-ton minimum capacity hydraulic mobile crane to site | Lump Sum | 1
4.2.2 | 80-ton mobile crane with operator – daily rate (lifting days only) | Day | 3
4.2.3 | Supply of certified rigging gear (slings, shackles, spreader beams) for lifting 60-ton tanks | Lump Sum | 1
4.2.4 | Provision of crane outrigger pads / cribbing to distribute ground bearing pressure | Lump Sum | 1
4.3 | Lifting Operations
4.3.1 | Pre-lift safety meeting and toolbox talk | Lump Sum | 1
4.3.2 | Test lift (100mm hold for 10 minutes) with inspection of rigging and crane stability | Per Tank | 3
4.3.3 | Lifting of each tank from existing foundation | Per Tank | 3
4.3.4 | Transportation of each tank to new location (if required – distance to be verified) | Per Tank | 3
4.3.5 | Setting and alignment of each tank on new foundations with anchor bolt engagement | Per Tank | 3
4.3.6 | Levelling and grouting of tank support base plates (non-shrink grout) | Per Tank | 3
4.4 | Lifting Support Services
4.4.1 | Certified riggers for lifting operations | Day | 3
4.4.2 | Signalmen / spotters for crane operations | Day | 3
4.4.3 | Establishment of exclusion zones with barriers during lifting | Lump Sum | 1
SECTION 4 TOTAL
5 | REINSTATEMENT, PIPING & COMMISSIONING
5.1 | Piping Reinstallation
5.1.1 | Reconnection of Main LPG Line (2" diameter) including new flanges, fittings, and gaskets as required – under API supervision | Each | 3
5.1.2 | Reconnection of Main LPG Line (3" diameter) including new flanges, fittings, and gaskets as required – under API supervision | Each | 3
5.1.3 | Reconnection of Main LPG Line (4" diameter) including new flanges, fittings, and gaskets as required – under API supervision | Each | 3
5.1.4 | Reconnection of Main LPG Line (6" diameter) including new flanges, fittings, and gaskets as required – under API supervision | Each | 3
5.1.5 | Reconnection of LPG Return Line (2" diameter) including new flanges, fittings, and gaskets as required – under API supervision | Each | 3
5.1.6 | Reconnection of Vapour Line (2" diameter) including new flanges, fittings, and gaskets as required – under API supervision | Each | 3
5.1.7 | Reconnection of Hydraulic Valve lines (small bore tubing) | Each | 6
5.2 | Valve Works
5.2.1 | Reinstallation of existing valves (gate, ball, check, hydraulic) | Each | 15
5.3 | NDT
5.3.1 | Radiographic Testing (RT) – per weld (new welds) | Each | 20
5.3.2 | Ultrasonic Testing (UT) – per weld (existing reconnected welds) | Each | 10
5.3.3 | NDT reporting and documentation | Lump Sum | 1
5.4 | Testing & Commissioning
5.4.1 | Hydrostatic pressure test (including test pumps, gauges, hoses, and water supply) – 1.5 x design pressure, 1-hour hold | Lump Sum | 1
5.4.2 | Pneumatic pressure test with nitrogen (if hydrostatic not feasible) – 1.5 x design pressure | Lump Sum | 1
5.5.3 | Nitrogen for purging and testing | m³ | 150
5.4.3 | Leak testing with leak detection spray or electronic gas detectors | Lump Sum | 1
5.4.4 | Controlled introduction of LPG and commissioning of tanks | Lump Sum | 1
5.5.4 | Verification and testing of safety devices (PSVs, level gauges, ESD systems) | Lump Sum | 1
5.5 | API Engineer Supervision
5.5.1 | API Engineer (API 653/570 certified) on-site supervision during reconnection and commissioning phase | Lump Sum | 1
SECTION 5 TOTAL
6 | DEMOLITION, SITE CLEARANCE & HANDOVER
6.1 | Demolition of Existing Foundations
6.1.1 | Mechanical demolition of three (3) existing concrete foundations at original tank locations using hydraulic breaker | m³ | 22.5
6.1.2 | Cutting and removal of existing reinforcement steel from demolished concrete | Lump Sum | 1
6.2 | Debris Removal & Disposal
6.2.1 | Loading and transportation of demolition debris (concrete, steel, scrap) to licensed disposal facility | Ton | 55
6.2.2 | Disposal fees at licensed facility | Ton | 55
6.2.3 | Removal of all temporary works, waste, and surplus materials from site | Lump Sum | 1
6.3 | Site Grading
6.3.1 | Backfilling of demolition areas with clean fill material | m³ | 25
6.3.2 | Compaction of backfilled areas | m² | 50
6.3.3 | Final grading and leveling of original site to match surrounding ground | m² | 100
6.4 | Handover Documentation
6.4.1 | Preparation of as-built drawings documenting any field changes | Lump Sum | 1
6.4.2 | Compilation of project dossier including all test reports, NDT reports, material certificates, commissioning logs, and O&M documentation | Lump Sum | 1
6.4.3 | Final joint inspection and handover with Engineer | Lump Sum | 1
SECTION 6 TOTAL

## Summary
SUMMARY OF BOQ
Section | Description | Total Amount
Section 1 | Mobilization, Site Setup & Safety
Section 2 | New Foundation Construction (3 Units)
Section 3 | Preparation, Disconnection & API Supervision
Section 4 | Tank Lifting & Relocation (3 Tanks)
Section 5 | Reinstatement, Piping & Commissioning
Section 6 | Demolition, Site Clearance & Handover
SUB-TOTAL (Direct Works)
GST 8%
TOTAL LUMP SUM PRICE
DECLARATION & SIGNATURE
I/We, the undersigned, hereby confirm that the rates and amounts quoted in this Bill of Quantities are in accordance with the Scope of Work and Technical Specification. I/We have verified the quantities and understand that the total of this BOQ represents the Lump Sum Price for the complete project.
Company Name:
Authorized Signatory:
Name & Title:
Date:
Official Company Stamp: