## Sheet1
Installation of Main Power Cable and Main Distribution Panel
Thinadhoo LPG Distribution Site
BOQ – Installation of Main Cable and Main Distribution Panel
Item No. | Description | Unit | Qty | Unit Rate | Amount
The bidder shall complete the BOQ with unit rates and total prices. All rates shall include materials, labor, transport, tools, equipment, installation, testing, commissioning, overheads, and profit. Note: The bidder shall ensure that the BOQ prices include: All material costs All labor costs Transport to site Loading and unloading Tools and equipment Excavation and reinstatement Permits and approvals Testing and commissioning Safety arrangements Consumables Documentation Contractor overhead and profit No additional claim shall be accepted for any item required for the completion of the works unless specifically approved by the Employer in writing.
1 | Preliminary and General Requirements | LS | 1
1.1 | Site survey, route verification, coordination, and mobilization | LS | 1
1.2 | Preparation of method statement, risk assessment, and work schedule | LS | 1
1.3 | Obtaining excavation permits and required authority approvals | LS | 1
1.4 | Demobilization and site cleaning after completion | LS | 1
2 | Excavation and Cable Trench Works
2.1 | Excavation of cable trench, 0.900 m depth x 0.200 m width | m | 181
2.2 | Sand bedding below cable | m | 181
2.3 | Sand covering above cable | m | 181
2.4 | Cable protection tiles/slabs/covers | m | 181
2.5 | Underground electrical warning tape | m | 181
2.6 | Backfilling and compaction | m | 181
2.7 | Road/pavement/ground reinstatement | LS | 1
2.8 | Cable route markers | No. | As required
3 | Main Power Cable and Accessories
3.1 | Supply of 240 mm² copper XLPE/PVC armoured power cable | m | 181 + allowance
3.2 | Laying of 240 mm² copper power cable | m | 181 + allowance
3.3 | Cable sleeves/ducts for crossings and wall entries | LS | 1
3.4 | Brass double compression cable glands | Set | 1
3.5 | Tinned copper cable lugs | Set | 1
3.6 | Heat shrink sleeves and phase identification materials | LS | 1
3.7 | Cable termination at Fenaka transformer/supply end | LS | 1
3.8 | Cable termination at Main Distribution Panel end | LS | 1
4 | Main Distribution Panel
4.1 | Design, fabrication, supply, and delivery of Main Distribution Panel | LS | 1
4.2 | Panel enclosure, IP54, floor-mounted, powder-coated | LS | 1
4.3 | 630 A, 4P main utility incomer MCCB/ACB | No. | 1
4.4 | 630 A, 4P generator incomer MCCB/switch disconnector | No. | 1
4.5 | 630 A, 4P manual changeover switch | No. | 1
4.6 | Copper busbar system, minimum 630 A, preferably 800 A | Set | 1
4.7 | Neutral bar and earth bar | Set | 1
4.8 | Outgoing feeder MCCB No. 1 | No. | 1
4.9 | Outgoing feeder MCCB No. 2 | No. | 1
4.1 | Outgoing feeder MCCB No. 3 | No. | 1
4.11 | Outgoing feeder MCCB No. 4 | No. | 1
4.12 | Outgoing feeder MCCB No. 5 | No. | 1
4.13 | Digital multifunction meter | No. | 1
4.14 | Current transformers for metering | Set | 1
4.15 | LED indication lamps and control accessories | LS | 1
4.16 | Type 2 surge protection device | No. | 1
4.17 | Internal wiring, terminal blocks, ferrules, labels, and accessories | LS | 1
4.18 | Removable gland plates and cable termination accessories | LS | 1
5 | Panel Installation and Connection
5.1 | Transport, unloading, positioning, and fixing of panel | LS | 1
5.2 | Glanding and termination of incoming cable | LS | 1
5.3 | Connection of outgoing feeders | LS | 1
5.4 | Panel earthing and bonding | LS | 1
5.5 | Labeling and safety signage | LS | 1
6 | Testing and Commissioning
6.1 | Cable continuity and insulation resistance testing | LS | 1
6.2 | Panel factory testing | LS | 1
6.3 | Site testing and commissioning | LS | 1
6.4 | Manual changeover functional testing | LS | 1
6.5 | Final energization support and commissioning report | LS | 1
7 | Documentation and Handover
7.1 | Shop drawings and approval submissions | LS | 1
7.2 | As-built drawings | LS | 1
7.3 | Test certificates and commissioning reports | LS | 1
7.4 | Operation and maintenance manuals | LS | 1
7.5 | Warranty certificates | LS | 1
SUB-TOTAL (Direct Works)
GST 8%
TOTAL LUMP SUM PRICE