Supply & installation of DH CT machine and MRI UPS Battery pack

- Supply CT Scan Room UPS 40 Batteries

Supply of ROCKET 12V 120Ah SMF VRLA/AGM UPS-grade batteries

or

approved equivalent of the same class, for the CT Scan Room Eaton 93E

160 kVA UPS (480 V DC battery bus, configured as 40 x 12 V battery

blocks).

Batteries should be suitable for continuous medical-grade load

operation.

1.1 Supply Battery Rack and Inter-Cell Accessories (CT Scan Room UPS)

Supply of open steel battery rack and inter-cell connectors for a 40-

block UPS battery bank serving the CT Scan Room UPS. Rack and

connectors should be suitable for ROCKET 12V 120Ah SMF VRLA/AGM

batteries, or approved equivalent of the same class, and for UPS

installation.

1.2 Installation, Testing and Commissioning of Battery Bank (CT Scan Room

UPS)

Removal and disposal handling of the existing battery bank; installation

of a new battery bank onto the supplied rack; inter-cell

connection and terminal torquing to manufacturer-specified values;

polarity and string voltage verification; and functional commissioning

with the CT Scan Room Eaton 93E 160 kVA UPS under medical-grade load conditions.

- Supply 40 UPS Battery MRI Room

Supply of ROCKET 12V 120Ah SMF VRLA/AGM UPS-grade batteries

or

approved equivalent of the same class, for the MRI Room Eaton 93E 160

kVA UPS (480 V DC battery bus, configured as 40 x 12 V battery blocks).

Batteries should be suitable for continuous medical-grade load operation.

2.1 Supply Battery Rack and Inter-Cell Accessories (MRI Room UPS)

Supply of open steel battery rack and inter-cell connectors for a 40-

block UPS battery bank serving the MRI Room UPS. Rack and

connectors should suitable for ROCKET 12V 120Ah SMF VRLA/AGM

batteries, or approved equivalent of the same class, and for UPS

installation.

2.2 Installation, Testing and Commissioning of Battery Bank (MRI Room

UPS)

Removal and disposal handling of the existing battery bank; installation

of a new battery bank, onto the supplied rack; inter-cell

connection and terminal torquing to manufacturer-specified values;

polarity and string voltage verification; and functional commissioning

with the MRI Room Eaton 93E 160 kVA UPS under medical-grade load

conditions.