Supply & installation of DH CT machine and MRI UPS Battery pack
1. Supply CT Scan Room UPS 40 Batteries 

Supply of ROCKET 12V 120Ah SMF VRLA/AGM UPS-grade batteries
or
approved equivalent of the same class, for the CT Scan Room Eaton 93E
160 kVA UPS (480 V DC battery bus, configured as 40 x 12 V battery
blocks). 
Batteries should be suitable for continuous medical-grade load
operation.

1.1 Supply Battery Rack and Inter-Cell Accessories (CT Scan Room UPS)

Supply of open steel battery rack and inter-cell connectors for a 40-
block UPS battery bank serving the CT Scan Room UPS. Rack and
connectors should be suitable for ROCKET 12V 120Ah SMF VRLA/AGM
batteries, or approved equivalent of the same class, and for UPS
installation.

1.2 Installation, Testing and Commissioning of Battery Bank (CT Scan Room
UPS)
Removal and disposal handling of the existing battery bank; installation
of a new battery bank onto the supplied rack; inter-cell
connection and terminal torquing to manufacturer-specified values;
polarity and string voltage verification; and functional commissioning
with the CT Scan Room Eaton 93E 160 kVA UPS under medical-grade load conditions.

2. Supply 40 UPS Battery MRI Room

Supply of ROCKET 12V 120Ah SMF VRLA/AGM UPS-grade batteries 
or
approved equivalent of the same class, for the MRI Room Eaton 93E 160
kVA UPS (480 V DC battery bus, configured as 40 x 12 V battery blocks).
Batteries should be suitable for continuous medical-grade load operation.

2.1 Supply Battery Rack and Inter-Cell Accessories (MRI Room UPS)

Supply of open steel battery rack and inter-cell connectors for a 40-
block UPS battery bank serving the MRI Room UPS. Rack and
connectors should suitable for ROCKET 12V 120Ah SMF VRLA/AGM
batteries, or approved equivalent of the same class, and for UPS
installation.

2.2 Installation, Testing and Commissioning of Battery Bank (MRI Room
UPS)

Removal and disposal handling of the existing battery bank; installation
of a new battery bank, onto the supplied rack; inter-cell
connection and terminal torquing to manufacturer-specified values;
polarity and string voltage verification; and functional commissioning
with the MRI Room Eaton 93E 160 kVA UPS under medical-grade load
conditions.
