## COVER SHEET
BILL OF QUANTITIES
CONSTRUCTION OF OPD EXTENSION AT N. MANADHOO ATOLL HOSPITAL
N. MANADHOO
#REF!

## SUMMARY
SUMMARY OF BILLS OF QUANTITIES
#REF!
Bill No | Description |  | Amount
1 | PRELIMINARIES | Bill no. 01 | 0
2 | GROUND WORKS | Bill no. 02 | 0
3 | CONCRETE | Bill no. 03 | 0
4 | MASONRY AND PLASTERING | Bill no. 04 | 0
5 | ROOFING | Bill no. 05 | 0
6 | DOORS AND WINDOWS | Bill no. 06 | 0
7 | TILING | Bill no. 07 | 0
8 | CEILINGS | Bill no. 08 | 0
9 | PAINTING | Bill no. 09 | 0
10 | ELECTRICAL INSTALLATIONS | Bill no. 10 | 0
11 | HYDRAULICS & DRAINAGE | Bill no. 11 | 0
12 | AIR CONDITIONING SYSTEM | Bill no. 12 | 0
15 | TENDERER'S ADJUSTMENTS | Bill no. 13 | 0
| Sub total |  | 0
| GST 6% |  | 0
| GRAND TOTAL carried to form of bid |  | 0

## BOQ
BILL OF QUANTITIES
CONSTRUCTION OF OPD EXTENSION AT N. MANADHOO ATOLL HOSPITAL
Item | Description | Unit | Quantity | Rate/ Unit | Rate/ Unit | Total Unit Rate | Amount
|  |  |  | Material | Labour | Rates per Units
BILL No: 01
PRELIMINARIES
1.1 | General Notes
(1) | Abbreviations
m - meter
No - numbers
m³ - cubic meter
m² - square meter
Lm - Linear meter
KG - Kilograms
incl - including
mm - millimeter
dia - diameter
SS - Stainless Steel
GI - Galvanized Iron
NOTE:
Rate shall include for all materials, items, fittings, accessories & labour. Contractor must refer to drawings, specification before pricing. All the details are provided in drawing.
All materials must be approved by the consultant/client representative before commencing the work.
1.2 | Clean-up
1 | Allow for clean-up of completed works and site upon completion. | Item | 1 |  |  | 0 | 0
1.3 | Inspection Trips
1 | Arrange inspection trips to a consultant, each inspection trip takes 2 days, the contractor has to arrange 2 air tickets from Male'/N. Maafaru/Male' by air (normal fair) and N. Maafaru / N. Manadhoo/N. Maafaru sea transport (Speed boat), land transport from Maafaru airport to jetty and Jetty to Airport as well as accommodations ( 2 Air condition room) per trip to be include. | Item | 5 |  |  | 0 | 0
| BILL No: 01 PRELIMINARIES | [5 empty] | 0
TOTAL OF BILL No: 01 - Carried over to summary
BILL No: 02
GROUND WORKS
2.1 | General
(a) Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating and disposing surplus soil.
2.2 | Site Clearing
1 | Includes clearing of all trees and bushes complete with stems, roots Flooring and the reimbursement fees if applicable. The contractor is advised to survey the construction site and ensure that all necessary works for site clearing are included and on completion of works. Rates also include to reallocate and divert sewer lines, waster water lines, fresh water lines and electric lines. | m² | 242.35 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0
2.3 | Excavation |  |  |  |  | 0 | 0
| Excavation shall be carried out in all type of materials and by whatever means are necessary accurately to the lines and levels shown in the approved drawing. No blasting of any kind will be permitted. Excavation for foundations and will include timbering of soil faces and dewatering. Excavation quantities are measured to the faces of concrete members. Rates shall include for dewatering, leveling, grading, trimming compacting to faces of excavation, keeping sides plumb, backfilling, consolidating and disposing surplus soil and include for all additional excavation required to place the formwork / shuttering and dewatering the trench for the required days. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1 | Excavation for Footings (F1) | m³ | 4.54 |  |  | 0 | 0
2 | Excavation for Tie beam beams (TB) | m³ | 16.36 |  |  | 0 | 0
[6 empty] | 0 | 0
2.4 | Back Filling up to ground level. |  |  |  |  | 0 | 0
1 | Rates shall include for: leveling, grading, trimming and compacting as specified. | Item | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.3 | Basement filling Above ground level. |  |  |  |  | 0 | 0
1 | Back filling above ground level in 100mm thick compacted layers of approved back fill soil and disposal of any excess soil and including ramp: rates shall include for leveling, grading, trimming and compaction in 100mm layers of filled areas of excavation | m³ | 84.82 |  |  | 0 | 0
[6 empty] | 0 | 0
2.4 | Damp Proof Membrane |  |  |  |  | 0 | 0
| Cutting and laying in position heavy duty polythene sheets of gauge 500 (not less than 1.5mm thick). Rates shall include for: dressing around and sealing to all penetrations. Apply slurry type waterproofing to all surfaces of concrete below ground level in accordance with manufacturer's instructions. |  |  |  |  | 0 | 0
1 | Damp proof membrane above lean concrete ( Footing and Tie beam) | m² | 18.17 |  |  | 0 | 0
2 | Damp proof membrane below floor slab | m² | 242.35 |  |  | 0 | 0
3 | Bituminous application to 3 sides of footings, Tie beams & all the side of columns below ground level. | item | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
| BILL No: 02 - GROUND WORKS | [5 empty] | 0
TOTAL OF BILL No: 02 - Carried over to summary
BILL No: 03
CONCRETE
3.1 | General
Rates shall include for cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wire and other supports, laps and wastage, all reinforcement bars except 6 mm dia bars shall be of deformed high strength bars. 6 mm bar shall be round mild steel bars. Binding wire shall be of 1.6 mm or 1.4 mm soft iron wire. Reinforcement bars shall be cleaned before use i.e. should be free from rust, oil, din, or other coatings that reduces bonds, all reinforced bars and binding wires shall be stored under cover of at least 450 mm above the ground, cutting and bending according to approved manner & the approved working drawing, placing and fixing in position and binding should be as per the approved working drawing, laps in the bars shall be staggered, concrete cover for reinforcement shall not less than 50 mm for substructure, 40 mm for columns & side beams and not more than 30 mm for slab and beam bottoms. Desalinated water shall be used for all purposes, ground water shall not be used.
[6 empty] | 0 | 0
3.2 | Lean Concrete |  |  |  |  | 0 | 0
| Lean concrete shall be 50mm thick & mix ratio shall be 1:2:6 by dry volume. Lean concrete placed at bottom of footing and foundation beam and below plinth for protection according to line and length mentioned in the approved drawing. Quantity measured to the edges of concrete foundation members. Rate shall include of placing any formwork where necessary, batching, mixing, casting in all required items pouring & compacting and curing for 3 days and removal of any formwork include for provision casting of required items & finishing after removal of formwork and additional concrete required to confirm to structural and excavated tolerances and rates shall include supply of all required works |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1 | 50 mm thick lean concrete under the footings / and tie beam | m³ | 1.66 |  |  | 0 | 0
[6 empty] | 0 | 0
3.3 | Reinforced Concrete |  |  |  |  | 0 | 0
| In-situ reinforced concrete to: |  |  |  |  | 0 | 0
| *Add water proofing compound / admixture to concrete mix for walls GL and Roof Slabs |  |  |  |  | 0 | 0
3.3.1 | Footings/Tie beams |  |  |  |  | 0 | 0
1 | Footings, F1 600x600x300mm | m³ | 1.94 |  |  | 0 | 0
2 | Tie Beam, TB 200x200mm | m³ | 5.38 |  |  | 0 | 0
[6 empty] | 0 | 0
3.3.2 | Ground Floor |  |  |  |  | 0 | 0
1 | RCC Ground Slab 100 mm thick, (Rate shall include for shuttering required as per the drawings) | m³ | 24.24 |  |  | 0 | 0
2 | Concrete columns C1 & C2, 200 x 200mm | m³ | 3.62 |  |  | 0 | 0
4 | Concrete Lintel beams, 150 x 150mm | m³ | 0.6 |  |  | 0 | 0
5 | Concrete Sill beams, 150 x 150mm | m³ | 0.2 |  |  | 0 | 0
6 | Laying 100mm thick RC concrete floor at connection area. Rates include the removal of existing flooring, clean debris, laying damp proof membrane, leveling a compacting of ground, masonry and plastering of walls for edges and flooring with 6,mm bar @300 B/W. surface of the slab should be mat finish. | m³ | 1.11 |  |  | 0 | 0
3.3.3 | Roof Level |  |  |  |  | 0 | 0
1 | Roof beam, RB, 200x200 | m³ | 5.38 |  |  | 0 | 0
[6 empty] | 0 | 0
3.3 | Formwork
(a) Rates shall include for all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes and removal of formwork. All materials such as plywood, shutter oils and other items and transportation to work place and secure the formwork in highly precise manner guaranteeing straight and smooth concrete edges. Cutting, fixing, bracing and oiling according to line and length as per approved working drawings removal of it after concrete has set without damaging the concrete faces.
3.3.1 | Foundations
1 | Footings, F1 600x600x300mm | m² | 12.96 |  |  | 0 | 0
2 | Tie beam, TB 200X200mm | m² | 53.76 |  |  | 0 | 0
3.4.2 | Ground Floor |  |  |  |  | 0 | 0
1 | Concrete columns C1 & C2, 200 x 200mm, (50% of form work) same form work to be use balance 50% column | m² | 34.72 |  |  | 0 | 0
[6 empty] | 0 | 0
3.4.2 | Roof level |  |  |  |  | 0 | 0
1 | Roof beam, RB, 200x200 mm | m² | 80.64 |  |  | 0 | 0
[6 empty] | 0 | 0
3.4.3 | Lintel & Sill Beams |  |  |  |  | 0 | 0
1 | Lintel beams and Sill beams, 150x150mm, | Item | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
3.5 | Reinforcement |  |  |  |  | 0 | 0
| GENERAL : Rates shall include for cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wire and other supports, laps and wastage, all reinforcement bars except 6 mm dia bars shall be of deformed high strength bars. 6 mm bar shall be round mild steel bars. Binding wire shall be of 1.6 mm or 1.4 mm soft iron wire. Reinforcement bars shall be cleaned before use i.e. should be free from rust, oil, din, or other coatings that reduces bonds, all reinforced bars and binding wires shall be stored under cover of at least 450 mm above the ground, cutting and bending according to approved manner & the approved working drawing, placing and fixing in position and binding should be as per the approved working drawing, laps in the bars shall be staggered, concrete cover for reinforcement shall not less than 50 mm for substructure, 40 mm for columns & side beams and not more than 30 mm for slab and beam bottoms. |  |  |  |  | 0 | 0
| (b) All reinforcing bars shall be high strength bars. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
3.5.1 | Substructure |  |  |  |  | 0 | 0
| Footings, F1 600X600mm |  |  |  |  | 0 | 0
1 | Steel deformed bars, 12mm dia x 6m | Bars | 22 |  |  | 0 | 0
| Tie Beam |  |  |  |  | 0 | 0
1 | Steel deformed bars, 12mm dia x 6m | Bars | 98 |  |  | 0 | 0
2 | Steel Ring bars, 6mm dia x 6m | Bars | 68
3.5.2 | Ground Floor |  |  |  |  | 0 | 0
| Concrete columns C1 & C2, 200 x 200mm |  |  |  |  | 0 | 0
1 | Steel deformed bars, 12mm dia x 6m | Bars | 70 |  |  | 0 | 0
2 | Steel ring bars, 6mm dia x 6m | Bars | 60 |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
3.5.4 | Roof level |  |  |  |  | 0 | 0
3.5.3.1 | Attached Beams, |  |  |  |  | 0 | 0
| Roof beam, RB, 200x200 mm |  |  |  |  | 0 | 0
1 | Steel deformed bars, 12mm dia | Bars | 98 |  |  | 0 | 0
2 | Steel ring bars, 6mm dia | Bars | 68 |  |  | 0 | 0
[6 empty] | 0 | 0
3.5.5 | Floor Slab |  |  |  |  | 0 | 0
1 | 6 mm dia bars @250 C/C, For ground slab | bars | 353 |  |  | 0 | 0
[6 empty] | 0 | 0
3.6 | OTHER CONCRETE WORKS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1 | Fabrication of Concrete sink cupboard at Laboratory , 4.625 Meter length and 600mm width as per floorplan, Rates includes, concrete works tiling of all surfaces,installation of 2 ceramic laboratory sink 620x480x255mm, (Cotto or equivalent)with an wall mount elbow operated faucet. And Rates shall also include connecting fresh water, waste water related to this item. Also, rates shallinclude fixing the timber door panel and shelves with PVC role fomica on allsurfaces. Granite sheet to be laid on top of the Sink cupboard. 12mm thick plywood to use for door panels of the cupboard with both side Formica, | Item | 1 |  |  | 0 | 0
| BILL No: 03 - CONCRETE WORKS | [5 empty] | 0
TOTAL OF BILL No: 03 - Carried over to summary
BILL No: 04
MASONRY AND PLASTERING
4.1 | General
Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good. Bedding mortar (mixing ratio 1:4 i.e. cement: manufactured sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Masonry work shall be done with approved Machine compact cement blocks (300X150X150) with no defects. Lay in line and length as per approved working drawing Block making (mixing ratio 1:4 i.e. cement: Manufactured sand) shall be of OPC & free form salt.
floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding
Rates shall include for: 25mm groove lines on external surfaces as shown on the drawing. Desalinated water shall be used for all purposes, ground water shall not be used.
4.2 | Cement block work
External and external walls
4.2.1 | 150mm wide Hollow blocks, laid on and incl. 1:5 Cement Mortar, tie rods, compression gap filler, nylon / plastic mesh as specified.
1 | Ground Floor (external walls and laundry internal walls) | m² | 314 |  |  | 0 | 0
4.3 | Plastering
GENERAL: Interior and Exterior: Plaster All masonry wall have smooth finishing of 18 mm thick cement plastering with mix ratio 1:4 (i.e. cement: River Sand), plastering material shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Plastic net should be provided wherever concrete surface and masonry meets, and cracks are unacceptable. Regular curing up to 7 days must be done, edges of doors, windows and ventilators included.
4.3.1 | 25mm thick cement plastering (2 coat) on external walls and 18mm thick cement plastering on internal walls and concrete surfaces with 1:4 Cement mortar mix as specified incl. wire mesh at joints of concrete surfaces and walls (first, second coats).
1 | Ground floor | m² | 638 |  |  | 0 | 0
[6 empty] | 0 | 0
4.4 | Cement Screed Finish |  |  |  |  | 0 | 0
4.4.1 | 50mm thick Cement screening on the |  |  |  |  | 0 | 0
| concrete floor with 1:4 cement mortar |  |  |  |  | 0 | 0
| mix incl. trowel finish; General Areas |  |  |  |  | 0 | 0
1 | Ground Floor | m² | 242.35 |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
2.7 | Dry wall partition |  |  |  |  | 0 | 0
| 100mm thick dry wall partition, Steel frame with 12mm thick Shera board with timber frame. Rates includes to fabricate partition as per manufactures instructions as well as puttying and Anti bacterial and washable paint on both side and etc. |  |  |  |  | 0 | 0
1 | Partition wall , up to the ceiling. | m² | 195 |  |  | 0 | 0
| BILL No: 04 - MASONRY AND PLASTERING | [5 empty] | 0
TOTAL OF BILL No: 04 - Carried over to summary
BILL No: 05
ROOFING
5.1 | General
(a) Rates shall include for: fair edges, dressing over angel fillets, turning into grooves, all other labors, circular edges, nails, screws and other fixings and laps.
(b) Rates shall include to apply Wood preservative to all the surface of timbers (Roof structure).
(b) Rates shall include to remove existing end cap, fascia board and necessary roofing sheets and necessary works to connect new roof to existing roof.
5.2 | Roof Coverings | [5 empty] | 0
1 | Roofing sheets: Blue scope steel international limited MSP, Total coated thickness minimum 0.42mm thick - Aquamarine or equivalent, Rates include to remove roofing sheets with roof structure. Of proposed roofing area of existing corridor. | m² | 353 |  |  | 0 | 0
2
[6 empty] | 0 | 0
5.3 | Capping and Flashings |  |  |  |  | 0 | 0
1 | End cap: Blue scope steel international limited MSP, Total coated thickness minimum 0.42mm thick- Aqua marine or equivalent | m | 32 |  |  | 0 | 0
2 | Ridge cap: Blue scope steel international limited MSP, Total coated thickness minimum 0.42mm thick- Aqua marine or equivalent | m | 22.8 |  |  | 0 | 0
3 | Flashing: Blue scope steel international limited MSP, Total coated thickness minimum 0.42mm thick- Aqua marine or equivalent | m | 26 |  |  | 0 | 0
[6 empty] | 0 | 0
5.4 | Gutter |  |  |  |  | 0 | 0
| (a) MSP Color bond flat sheet gutter 200X200mm, Total coated thickness minimum 0.42mm thick, including framing, and supports, straps, brackets, clips, stop ends, overflow, downpipe outlets, mesh flashings and all fixings and fastenings. |  |  |  |  | 0 | 0
ehen veem | GUTTER: Blue scope steel international MSP- Aqua marine or equivalent | m | 46 |  |  | 0 | 0
[6 empty] | 0 | 0
5.5 | Down Pipes |  |  |  |  | 0 | 0
1 | 75 mm dia uPVC down pipes including bends, junctions, straps, brackets, clips, roof drain strainer and all fixings. | m | 60 |  |  | 0 | 0
[6 empty] | 0 | 0
5.7 | Roof Structure |  |  |  |  | 0 | 0
1 | (a) Rates shall include: all labor in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws. (b) Rates include applying solignam wood preservative oil to all the surfaces of the roof structure. (c) Rates include fixing galvanized bolt with washers and nuts as shown in the drawings. (d) Rates included to fix gussete plate with 12 mm dia GI bolts and roof anchoring bolts as per drawing.. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1 | Timber rafters 50 X 150mm | m | 612 |  |  | 0 | 0
2 | Timber purling 50 X 50mm | m | 690 |  |  | 0 | 0
3 | Facia board, 18mm thick SHERA board 18 X 250mm | m | 103 |  |  | 0 | 0
4 | Applying Solignum wood preservative or equivalent for all roof structure | item | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
5.8 | Roof Insulation |  |  |  |  | 0 | 0
1 | 50mm thick Mineral wool installation with both side reflective foil on Fixed to underside of roofing with 12.5X12.5mm plastic mesh, Connection and edges of the foil to be sealed properly with a approved tape from consultant. | m² | 353 |  |  | 0 | 0
| BILL No: 05 - ROOFING | [5 empty] | 0
TOTAL OF BILL No: 05 - Carried over to summary
BILL N0: 06
DOORS AND WINDOWS
6.1 | General
Aluminum Doors and windows, Fabricate and fix in position the aluminum doors and window frame - aluminum doors and window (white powder coated, 60-80 micron, 1.5mm profile thickness) using recommended material with specified fixtures as shown in approved working drawings and installation should be as per technical specifications. Rates shall include for locks, latches, closures, push plates, pull handles, bolts, kick plates hinges, screws, washer and all door and window hardware and these materials should be of ss steel according to drawing and of superior quality.
(a) All door and window frames and panels shall be as specified in the drawing and timber boarder to be fixed all timber doors.
(b) All glazing shall be 6mm Tinted.
(Profiles to be chosen by client).
6.2 | Door / Windows units
1 | D1, Solid timber Door 2150X900mm with panels as per drawings. Rates to include demolition of existing walls to fix the new doors, clean debris and plastering of the edge of the wall. | no | 6 |  |  | 0 | 0
2 | D2, Solid timber Door 2150X1350mm with panels as per drawings. Rates to include demolition of existing walls to fix the new doors, clean debris and plastering of the edge of the wall. | no | 3 |  |  | 0 | 0
3 | D3, Solid timber Door 2150X800mm with panels as per drawings. Rates to include demolition of existing walls to fix the new doors, clean debris and plastering of the edge of the wall. | no | 1 |  |  | 0 | 0
4 | D4, Solid timber Door 2150X1900mm with panels as per drawings. Rates to include demolition of existing walls to fix the new doors, clean debris and plastering of the edge of the wall. | no | 1 |  |  | 0 | 0
5 | D5, Aluminum 60-80 Micron, white powder coated Door 2150x1900mm with panels as per drawings (also include Aluminum grill). | no | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
6 | W1, Aluminum 60-80 Micron, white powder coated window 2300x1300mm with panels as per drawings (also include Aluminum grill). | no | 8 |  |  | 0 | 0
7 | W2, Aluminum 60-80 Micron, white powder coated window 2300x1300mm with panels as per drawings (also include Aluminum grill). | no | 1 |  |  | 0 | 0
8 | V1, Aluminum 60-80 Micron, white powder coated window 500x6750mm with panels as per drawings (also include Aluminum grill). | no | 1 |  |  | 0 | 0
9 | V2, Aluminum 60-80 Micron, white powder coated window 500x1300mm with panels as per drawings (also include Aluminum grill). | no | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
6.3 | Window Curtains |  |  |  |  | 0 | 0
| Supply and installation of roller blinds for following windows, quality of roller blinds should be sun protected high quality, Rates should be complete installation of curtain with railing and ect.. |  |  |  |  | 0 | 0
1 | W1 windows , size of finished curtain should be 2.8m height, X1.9meter width. ( 2pcs for curtain for each window) | No | 8 |  |  | 0 | 0
2 | W2 windows , size of finished curtain should be 2.8m height, X1.9meter width. ( 2pcs for curtain for each window) | No | 1 |  |  | 0 | 0
6.4 | BED SIDE CURTAINS |  |  |  |  | 0 | 0
| Supply and complete installation of top quality Hospital grade bed side curtain including railing. Length of curtain to be taken from furniture/floor plan and height of curtain would be 2.9 meter. |  |  |  |  | 0 | 0
1 | Consultation rooms | Item | 6 |  |  | 0 | 0
6.5 | Counters |  |  |  |  | 0 | 0
1 | Design and Fabrication of Registration counter as per Floor plan, Fabrication of counter to be timber and appropriate thick plywood with PVC fomica. Granite sheet to be laid on top of the Counters. | No | 1 |  |  | 0 | 0
| BILL N0: 06 - DOORS AND WINDOWS | [5 empty] | 0
TOTAL OF BILL No: 06 - Carried over to summary
BILL N0: 07
TILING
7.1 | General
Prepare surface for approved bedding tiles with reach bedding materials as per the technical specifications & approved working drawings, fix tiles with ct grout in a precise manner to maintain correct alignment, applying tile grout and wiping any excess grout to ensure the required standards of finished works. Rates shall include for: fixing, bedding, grouting, and pointing materials; making good around pipes, sanitary fixtures, and similar; cleaning down and polishing any other similar works to ensure the required finish. All tiles shall be Porcelain tiles or equivalent.
7.2 | Floor finish
7.2.1 | Removal of existing floor tiles and close a;ll plumbing lines, leveliong of floor with flooring and laying of 300x300 skid resistant White Ceramic (white ceramic body) floor tiles, Tile selection and design to be finalized by consultant.
1 | Toilet area | m² | 2.9 |  |  | 0 | 0
1 | Connection area with tile boarder. | m² | 8.76 |  |  | 0 | 0
[6 empty] | 0 | 0
7.3 | Wall finish |  |  |  |  | 0 | 0
7.3.1 | 300x600 mm full body homogeneous wall tile, |  |  |  |  | 0 | 0
1 | Toilet area, 2.4M from FFL. | m² | 14.64 |  |  | 0 | 0
2 | Micor Biology, 1.8 M from FFL. | m² | 18.18 |  |  | 0 | 0
3 | Sample Collection, 1.8 M from FFL. | m² | 22.68
4 | Laboratory, 1.8 M from FFL. | m² | 40.5
[6 empty] | 0 | 0
| Vinyl Floring |  |  |  |  | 0 | 0
4.3.1 | Supply and complete installation of Industrial quality Vunyl planks to be installed with Consultant instruction, Rates include supply and complete installation, preparation of floor as per manufactures standards. Vinyl planks to be installed as per manufactures instructions. Rates also includes to fix timber border as well for all the walls. Size of planks: 920X180mm. Thickness: Minimum 3mm Anti wear layer: Minimum 0.3mm |  |  |  |  | 0 | 0
1 | laying of Vinyl flooring, | m² | 240 |  |  | 0 | 0
[6 empty] | 0 | 0
| BILL No: 7 - TILING | [5 empty] | 0
TOTAL OF BILL No: 7 - Carried over to summary
BILL No: 8
CEILINGS
8.1 | Interior Ceilings
The interior ceiling consist of a 50X50mm timber frame with a 10mm thick Gypsum board suspended ceiling, including framing beading nails and screws as per drawing and picture provided by this document. spans of timber frame are 600mm c/c vertical, 1200mm c/c Horizontal frame. Rates include fabrication of frame, fixing of Gypsum boards, puttying and painting. Rates also include Gypsum cornice of all adges.
1 | Ground floor Rooms ( single layer ceiling) | m² | 143.02 |  |  | 0 | 0
1 | Ground floor Corridor and waiting area ( Double layer ceiling) as per drawing. | m² | 99.31 |  |  | 0 | 0
8.2 | Exterior Ceilings
Exterior ceiling consist of 6mm thick M board suspended ceiling, including framing beading nails and screws. Grid of the frame to be 600 X 600 with timber supports to roof structure at every 1200 mm on the main entrance ceiling & 600X900 mm at eaves of roof ceiling, timber framing and supports shall 50 x 50mm size shall be seasoned red meranti timber as per given drawing.
1 | Ground floor | m² | 70.8 |  |  | 0 | 0
| BILL N0: 8 CEILINGS | [5 empty] | 0
TOTAL OF BILL No:8 - Carried over to summary
BILL No: 9
PAINTING
9.1 | General
Exterior wall shall be of 1 coat of oil based textured paint and 2 coats of Kansani weather bond paint ( oil based ) over 1 coat of oil based sealer ( white) or equivalent (according to technical specifications or approved drawings). Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams.
Interior wall shall be of 2-3 coats over 1 coat of water based sealer. Rates includes Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams.
Exterior & Exterior Ceiling (interior and exterior) shall be of 2 coats of (wood paint over 1 coat of wood primer or equivalent. Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for the provision and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and or masking floors fittings and similar work removing and replacing door window furniture.
All painting work shall be carried in accordance with the Specifications
9.2 | Wall painting
9.2.1 | External painting 1 coat of wall sealer, 1 coat texture compound & 2 coats of paints ( all coats to be oil based and external paint).
Internal Painting 1 coat of wall sealer & 2 coats of paints, Emulsion paint putty finish system on plastered and concrete surfaces of internal walls.
1 | Ground floor, Masonry walls | m² | 638 |  |  | 0 | 0
2 | Partition walls | m² | 390 |  |  | 0 | 0
[6 empty] | 0 | 0
9.3 | Interior and Exterior ceiling painting |  |  |  |  | 0 | 0
1 | Interior Ceiling painting as per specification given. | m² | 242.33 |  |  | 0 | 0
2 | Exterior Ceiling painting as per specification given. | m² | 70 |  |  | 0 | 0
| BILL No: 9 - PAINTING | [5 empty] | 0
TOTAL OF BILL No: 9 - Carried over to summary
BILL No: 10
ELECTRICAL INSTALLATIONS
10.1 | General
(a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories
(b) Rates for work in trench shall include for: excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers, warning tape and disposal of surplus spoil
(c) Rates shall include for electrical conduits, fittings, equipment and similar all fixings to various building surfaces
(d) Each Light/ light fixture and its switch is measured as one point; similarly each fan or each socket outlet is measured as one point;
(e) Rates shall include for supply and complete installation
10.2 | Mains connection
1 | Main connection: Rates shall include for screws, nails, bolts ,nuts, standard cable, fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories. Rates shall including for electrical conduits, fittings, equipment and similar items. Three - PHASE CABLE WIRING TO D-BOARD: All necessary work in trench shall include for excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers warning tape and disposal of surplus soil supply and laying of the cable in according to Maldives electricity bureau. ( 16mm2 4-Core Cable, Approved by respective Authorities, GI pipe, warning tape), contractor has to measure cable length from site. ( Connect B-Board at existing building) | no | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
10.3 | Electrical Boards |  |  |  |  | 0 | 0
1 | Three phase electrical distribution board (wall embedded) with one Meter: Supply and installation of D-Board . Rates Shall include all required Brackets and other electrical appliance as per drawings and Maldivian Regulations ( wall embedded ) Meter to be cover with whether proof box. All the light circuit should be one DB Sockets to be one DB. | no | 1 |  |  | 0 | 0
`
10.4 | Electrical wiring |  |  |  |  | 0 | 0
| Three phase Electrical wiring with copper conductor cable in conduits in walls and in casing on soffits of slab as specified to: |  |  |  |  | 0 | 0
1 | Wiring with 2.5 mm² cable to 1X13amp Power points | points | 23 |  |  | 0 | 0
2 | Wiring with 2.5 mm² cable to 2X13amp Power points | points | 22 |  |  | 0 | 0
3 | Wiring with 6 mm² cable to 1 x 15 Amp Power points | points | 7 |  |  | 0 | 0
4 | Wiring with 6 mm² cable to 1 x 15 Amp Power points (for AC) | points | 12 |  |  | 0 | 0
5 | Wiring with 2.5 mm² cable to lights and fan | points | 66 |  |  | 0 | 0
[6 empty] | 0 | 0
10.5 | Lighting / Fan |  |  |  |  | 0 | 0
1 | Ceiling diffusing embedded down light 150mm dia with 19W LED bulb, (Philips) E27, Cool day light, (not crystal light or not Stellar bright) Total lumen 2300. or equivalent, | no | 49 |  |  | 0 | 0
2 | Whether proof wall mount light with 13W LED bulb, (Philips) E27, Cool day light, Total lumen 1400, for Portico area | no | 8 |  |  | 0 | 0
3 | LED Emergency light ( 2 hours Battery charge) | no | 13 |  |  | 0 | 0
4 | Supply and installation of LED exit board | no | 2 |  |  | 0 | 0
5 | 300X300mm Exaust fan, KDK or equivalent | no | 1 |  |  | 0 | 0
0
10.6 | Socket outlets
(a) All socket outlets shall be "Legrand" or equivalent.
1 | 1x13Amp wall Socket outlet, | no | 23 |  |  | 0 | 0
2 | 2x13Amp wall Socket outlet, | no | 22 |  |  | 0 | 0
3 | 1x15Amp wall socket outlet, | no | 7 |  |  | 0 | 0
4 | 1x15Amp socket outlet, for AC | no | 12 |  |  | 0 | 0
[6 empty] | 0 | 0
10.7 | Light switches |  |  |  |  | 0 | 0
| (a) All light switches shall be "Legrand" or equivalent. Each light should be control by one switch. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1 | One gang switch | no | 7 |  |  | 0 | 0
2 | Two gang switch | no | 9 |  |  | 0 | 0
3 | three gang switch | no | 8 |  |  | 0 | 0
4 | Out door photo cell switch | no | 3 |  |  | 0 | 0
[6 empty] | 0 | 0
10.8 | Air Curtain
| Supply and Complete installation of Air curtain Rates include laying electric points and commission the unit. |  |  |  |  | 0 | 0
1 | Supply and Complete installation on KDK (10ESK ) air curtain, 900mm length. | no | 2 |  |  | 0 | 0
[6 empty] | 0 | 0
10.9 | Telephone Network
Design and supply and complete installation of Telephone network (Including cabling and sockets) and connect to existing PABX. Cat6 cable to be used for laying telephone network.
1 | Completion of Telephone outlet points , rates includes to connect existing telephone network. | No | 9 |  |  | 0 | 0
[6 empty] | 0 | 0
10.1 | Computer Network |  |  |  |  | 0 | 0
| Design, Supply and Complete Installation of computer networking, including CAT6 Cabling, Sockets and double layer switches, Allow for the provision of a completed and detailed set of shop drawings |  |  |  |  | 0 | 0
1 | Completion of Data Network points | No | 9 |  |  | 0 | 0
2 | 24 port, Double layer Manageable network switch as per Specifications | No | 1 |  |  | 0 | 0
3 | Suuplying of Computer System as per Specifications | No | 7 |  |  | 0 | 0
4 | Suuplying of Canon Black and white print as per Specifications | No | 7 |  |  | 0 | 0
[6 empty] | 0 | 0
10.11 | Fire Fighting
1 | CO2 Extinguisher | Item | 6 |  |  | 0 | 0
2 | H2O Extinguisher | Item | 6 |  |  | 0 | 0
10.11 | Lightening Protection System |  |  |  |  | 0 | 0
1 | Design, supply, and Complete installation of Erco, Eritech or equivalent lightening Protection System to cover the whole building as per local regulations (Rate shall include for all fixing of the system and down conductor to earthing) Coverage of lightning protection should be minimum 100 Meter Radius. Pric also include 75mm GI to install Marine grade SS post. | Item | 1 |  |  | 0 | 0
| BILL No: 10 - ELECTRICAL INSTALLATIONS | [5 empty] | 0
TOTAL OF BILL No: 10 - Carried over to summary
BILL No: 11
HYDRAULICS & DRAINAGE
11.1 | Hydraulics
11.1.1 | General
(a) Rates shall include for excavation, laying pipes and backfilling trenches, maintaining faces of drainpipe trenches and pits, backfilling, disposal of surplus soil, bends, junctions, reducers, expansion joints brackets, joints, straps, hangers, screws, nails and fixing complete, and all joints and other incidental material, All Pipes and fittings area high pressure uPVC pipes
fixing complete, including cutting and forming holes; excavating, laying pipes and backfilling trenches.
(b) All pipe work shall be uPVC.
11.1.2 | Ground water and Fresh water supply pipe work
1 | Completion of pipe works and Connect ground water supply pipe work to ground water network installed at hospital. ( WC only) | Item | 1 |  |  | 0 | 0
2 | Completion of pipe works and Connect Fresh water supply pipe work to Fresh water network installed at hospital. | Item | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
11.1.4 | Sanitary fixtures & accessories |  |  |  |  | 0 | 0
| Sanitary fixtures & Accessories: Sanitary fixtures complete including brackets, flush pipes, valves, overflows, plugs and washers, as specified. |  |  |  |  | 0 | 0
1 | Water closet (Cotto) or equivalent, (dual top flush) as shown in material selection. | no | 1 |  |  | 0 | 0
2 | Wash basin with half pedestal (Cotto) or equivalent | no | 8 |  |  | 0 | 0
3 | Water tap lever type for wash basin , ( Cotto) or equivalent | no | 8 |  |  | 0 | 0
4 | Stop Valves, ( Cotto) or equivalent | no | 10 |  |  | 0 | 0
5 | Wall cabinet ( Mirror and towel bar) Cotto and equivalent | no | 1 |  |  | 0 | 0
6 | Muslim Shower with Stop valve, ( Cotto) or equivalent | no | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
11.2 | Drainage |  |  |  |  | 0 | 0
11.2.1 | General |  |  |  |  | 0 | 0
| (a) Rates shall include for: excavation, maintaining faces of drain pipe trenches and pits, backfilling, disposal of surplus spoil; bends, junctions, reducers, expansion joints and all joints and other incidental materials. |  |  |  |  | 0 | 0
| (b) All pipe work shall be UPVC |  |  |  |  | 0 | 0
1 | Constructing Concrete Inspection Chamber of required size with all provisions to connect pipelines as per drawing. | Item | 2 |  |  | 0 | 0
[6 empty] | 0 | 0
11.3 | Pipe work |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1 | Completion of pipe works and Connect Waste disposal pipe 75mm dia to Sewer network installed at existing system at hospital. | Item | 1 |  |  | 0 | 0
2 | Completion of pipe works and Connect Sewer pipe 100mm dia UPVC to existing system. | Item | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
| BILL No: 11 - HYDRAULICS & DRAINAGE | [5 empty] | 0
TOTAL OF BILL No: 11 - Carried over to summary
BILL No: 12
AIR CONDITIONING SYSTEM
12.1 | General
(a) Rates shall include for detail design, supply and complete installation of A/C units pipework, insulation, fixings, electrical wiring, drain pipes etc.
(b) The Contractor shall provide detailed and complete set of shop drawings
12.2 | Air Condition
12.2.1 | Design, supply and complete installation of indoor and out door unit, with 40ø drop in water (type) 25ø extended as Cd drop in 32 flex conduit 18ø Cd drain (typ0 run above FC insulated, all AC unit is HITACHI or equivalent (INVERTER TYPE).
1 | Consultation Rooms, 12,000 BTU spilt type Ceiling cassette air conditioner (with wired remote) Hitachi or equivalent. | Item | 6 |  |  | 0 | 0
2 | Laboratiry, 36,000 BTU spilt type Ceiling cassette air conditioner (with wired remote) Hitachi multi split unit or equivalent. | Item | 2 |  |  | 0 | 0
3 | Sample Collection, 18,000 BTU spilt type Ceiling cassette air conditioner (with wired remote) Hitachi or equivalent. | Item | 1 |  |  | 0 | 0
4 | Sample Collection, 32,000 BTU spilt type Ceiling cassette air conditioner (with wired remote) Hitachi multi split unit or equivalent. | Item | 3 |  |  | 0 | 0
[6 empty] | 0 | 0
| BILL No: 12 -AIR CONDITIONING SYSTEM | [5 empty] | 0
TOTAL OF BILL No: 12 - Carried over to summary
BILL No:13
TENDERER'S ADJUSTMENTS
(a) Provide detail description of work items under each bill and insert extra pages if required.
15.1 | Additions
1 | PRELIMINARIES, Bill no. 01 |  |  |  |  | 0 | 0
2 | GROUND WORKS, Bill no. 02 |  |  |  |  | 0 | 0
3 | CONCRETE, Bill no. 03 |  |  |  |  | 0 | 0
4 | MASONRY AND PLASTERING, Bill no. 04 |  |  |  |  | 0 | 0
5 | METAL WORKS, Bill no. 05 |  |  |  |  | 0 | 0
6 | DOORS AND WINDOWS, Bill no. 06 |  |  |  |  | 0 | 0
7 | TILING, Bill no. 07 |  |  |  |  | 0 | 0
8 | CEILINGS, Bill no. 08 |  |  |  |  | 0 | 0
9 | PAINTING, Bill no. 09 |  |  |  |  | 0 | 0
10 | HYDRAULICS & DRAINAGE, Bill no. 10 |  |  |  |  | 0 | 0
11 | ELECTRICAL INSTALLATIONS, Bill no. 11 |  |  |  |  | 0 | 0
12 | AIR CONDITIONING SYSTEM, Bill no. 12 |  |  |  |  | 0 | 0
13 | TENDERER'S ADJUSTMENTS, Bill no. 13 |  |  |  |  | 0 | 0
| ADDITIONS TOTAL | [5 empty] | 0
15.2 | Omissions
1 | PRELIMINARIES, Bill no. 01 |  |  |  |  | 0 | 0
2 | GROUND WORKS, Bill no. 02 |  |  |  |  | 0 | 0
3 | CONCRETE, Bill no. 03 |  |  |  |  | 0 | 0
4 | MASONRY AND PLASTERING, Bill no. 04 |  |  |  |  | 0 | 0
5 | METAL WORKS, Bill no. 05 |  |  |  |  | 0 | 0
6 | DOORS AND WINDOWS, Bill no. 06 |  |  |  |  | 0 | 0
7 | TILING, Bill no. 07 |  |  |  |  | 0 | 0
8 | CEILINGS, Bill no. 08 |  |  |  |  | 0 | 0
9 | PAINTING, Bill no. 09 |  |  |  |  | 0 | 0
10 | HYDRAULICS & DRAINAGE, Bill no. 10 |  |  |  |  | 0 | 0
11 | ELECTRICAL INSTALLATIONS, Bill no. 11 |  |  |  |  | 0 | 0
12 | AIR CONDITIONING SYSTEM, Bill no. 12 |  |  |  |  | 0 | 0
13 | TENDERER'S ADJUSTMENTS, Bill no. 13 |  |  |  |  | 0 | 0
| OMISSIONS TOTAL | [5 empty] | 0
| BILL No: 13 - TENDERER'S ADJUSTMENTS | [5 empty] | 0
TOTAL OF BILL No: 13 - Carried over to summary