## COVER SHEET
BILL OF QUANTITIES
RENOVATION WORKS AT CT AND MEMOGRAPHY AREA AT R. UGOOFAARU REGIONAL HOSPITAL.
0

## SUMMARY
SUMMARY OF BILLS OF QUANTITIES
RENOVATION WORKS AT CT AND MEMOGRAPHY AREA AT R. UGOOFAARU REGIONAL HOSPITAL.
Bill No | Description |  | Amount
1 | ELECTRICAL INSTALLATIONS | Bill no. 01 | 0
0
| Sub Total |  | 0
| GST 6% |  | 0
| GRAND TOTAL carried to form of bid |  | 0

## BoQ
BILL OF QUANTITIES
RENOVATION WORKS AT CT AND MEMOGRAPHY AREA AT R. UGOOFAARU REGIONAL HOSPITAL.
Item | Description | Unit | Quantity | Rate/ Unit | Rate/ Unit | Total Unit Rate | Amount
|  |  |  | Material | Labour | Rates per Units
BILL No: 01
PRELIMINARIES
1.1 | General Notes
(1) | Abbreviations
m - meter
No - numbers
m³ - cubic meter
m² - square meter
Lm - Linear meter
KG - Kilograms
incl - including
mm - millimeter
dia - diameter
SS - Stainless Steel
GI - Galvanized Iron
NOTE:
Rate shall include for all materials, items, fittings, accessories & labour. Contractor must refer to drawings, specification before pricing. All the details are provided in drawing.
All materials must be approved by the consultant/client representative before commencing the work.
1.2 | Clean-up
1 | Allow for clean-up of completed works and site upon completion. | Item | 1 |  |  | 0 | 0
1.3 | Demolition works.
1 | Demolition of the existing wall at toilet area as per drawing, Rates to include demolition of walls, plastering of edges, painting, and cleaning of debris also include other necessary works required. | m² | 50.62 |  |  | 0 | 0
2 | Removal of wall tiles at the existing toilet block, Rates includes the removal of wall tiles, plastering of tiles area, Applying wall sealer of plastering surface. | m² | 25 |  |  | 0 | 0
3 | Laying 100mm thick RC Flooring. Rates include closing all piles (Freshwater line, wastewater line and Sewer line), laying damp proof membrane . mixing ratio of Mass concrete is 1:2:3, T10@200/BW to be lying in the floor. | m² | 12.2 |  |  | 0 | 0
1.4 | INSPECTION TRIPS
1 | Arrange inspection trips to a consultant, each inspection trip takes 2 days, Ifuru / Ugoofaru/Ifur sea transport (Speed boat) as well as accommodations ( 2 Air condition room) per trip to be include. | No | 3 |  |  |  | 0
| BILL No: 01 PRELIMINARIES | [5 empty] | 0
TOTAL OF BILL No: 01 - Carried over to summary
BILL No: 02
MASONRY AND PLASTERING
2.1 | General
Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good. Bedding mortar (mixing ratio 1:4 i.e. cement: manufactured sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Masonry work shall be done with approved Machine compact cement blocks (300X150X150) with no defects. Lay in line and length as per approved working drawing Block making (mixing ratio 1:4 i.e. cement: Local sand, Free from salt) shall be of OPC & Local sand free form salt.
floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding
2.2 | Cement block work
[6 empty] | 0 | 0
| Internal walls |  |  |  |  | 0 | 0
2.3 | GENERAL: Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good. Bedding mortar (mixing ratio 1:4 i.e. cement: manufactured sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Masonry work shall be done with approved Machine compact cement blocks (300X150X150) with no defects. Lay in line and length as per approved working drawing Block making (mixing ratio 1:4 i.e. cement: Manufactured sand) shall be of OPC & free form salt.
| 200mm wide solid blocks, laid on and incl. 1:5 Cement Mortar, tie rods, compression gap filler, nylon / plastic mesh as specified. |  |  |  |  | 0 | 0
1 | Closing of opening of main anterance balance part of door area, Thickness of the wall should be same as existing wall. | m² | 8 |  |  | 0 | 0
[6 empty] | 0 | 0
2.4 | Plastering
GENERAL: Interior and Exterior: Plaster All masonry wall have smooth finishing of 18 mm thick cement plastering with mix ratio 1:4 (i.e. cement: River Sand), plastering material shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Plastic net should be provided wherever concrete surface and masonry meets, and cracks are unacceptable. Regular curing up to 7 days must be done, edges of doors, windows and ventilators included.
1 | 25mm cement plastering on external walls and concrete surfaces with 1:4 Cement mortar mix as specified incl. wire mesh at joints of concrete surfaces and walls (first, second coats). | m² | 16 |  |  | 0 | 0
`
2.6 | Trenches.
1 | Making of Trench as per drawing, Rates includes the cutting of the existing floor, excavation of trench area, masonry works for tren and laying shera board as per drawing. | m² | 22 |  |  | 0 | 0
| BILL No: 02 - MASONRY AND PLASTERING | [5 empty] | 0
TOTAL OF BILL No: 02 - Carried over to summary
BILL N0: 03
DOORS AND WINDOWS
3.1 | General
Timber doors, Fabricate the doorframes and door panel to specified size using recommended timber fix same and other fittings such as locks etc. wood Paint specified and shown in approved working drawings and installation should be as per technical specifications. Rates shall include for locks (i.e. security lock & dead lock), latches, closures, push plates, pull handles, bolts, kick plates hinges, screws, washer and all door and window hardware and these materials should be of ss steel according to drawing and of superior quality.
Aluminum Doors and windows, Fabricate and fix in position the aluminum doors and window frame - aluminum doors and window (white powder coated, 60-80 micron, 1.5mm profile thickness) using recommended material with specified fixtures as shown in approved working drawings and installation should be as per technical specifications. Rates shall include for locks, latches, closures, push plates, pull handles, bolts, kick plates hinges, screws, washer and all door and window hardware and these materials should be of ss steel according to drawing and of superior quality.
(a) All door and window frames and panels shall be as specified in the drawing and timber boarder to be fixed all timber doors.
(b) All glazing shall be 6mm Tinted.
(Profiles to be chosen by client).
3.2 | Door / Windows units
1 | Fabricate and Fixing of timber Door with panels (D1) with the frame as per the drawings, the width of the door frame should be the same as wall thickness. also timber border (teak wood ) on both sides of the door. Door panel to be fabricated with a timber frame with 6mm thick teak wood plywood on both sides also hand rain to be fixed on both sides of all panel. finishes of the door should be varnish finish. | Item | 1 |  |  | 0 | 0
2 | Fabricate and Fixing of timber Door with panels (D1A) with the frame as per the drawings, the width of the door frame should be the same as wall thickness. also timber border (teak wood ) on both sides of the door. Door panel to be fabricated with a timber frame with 6mm thick teak wood plywood on both sides also hand rain to be fixed on both sides of all panel. finishes of the door should be varnish finish. | Item | 3 |  |  | 0 | 0
3 | Fabricate and Fixing of timber Door with panels (D2) with the frame as per the drawings, Lead sheets to be fixed with door frame and panel as per drawing ( lead sheets will be provided by the client), the width of the door frame should be the same as wall thickness. and thickness of the door should be 75mm thick also timber border (teak wood ) on both sides of the door. Door panel to be fabricated with a timber frame with 6mm thick teak wood plywood on both sides also hand rain to be fixed on both sides of all panel. finishes of the door should be varnish finish. | Item | 1 |  |  | 0 | 0
4 | Fabricate and Fixing of timber Door with panels (D3) with the frame as per the drawings, Lead sheets to be fixed with door frame and panel as per drawing ( lead sheets will be provided by the client), the width of the door frame should be the same as wall thickness. and thickness of the door should be 75mm thick also timber border (teak wood ) on both sides of the door. Door panel to be fabricated with a timber frame with 6mm thick teak wood plywood on both sides also hand rain to be fixed on both sides of all panel. finishes of the door should be varnish finish. | no | 2 |  |  | 0 | 0
5 | Fabricate and Fixing of timber Door with panels (D4) with the frame as per the drawings, the width of the door frame should be the same as wall thickness. also timber border (teak wood ) on both sides of the door. Door panel to be fabricated with a timber frame with 6mm thick teak wood plywood on both sides also hand rain to be fixed on both sides of all panel. finishes of the door should be varnish finish. | no | 1 |  |  | 0 | 0
6 | Fabricate and Fixing of timber Door with panels (D5) with the frame as per the drawings, the width of the door frame should be the same as wall thickness. also timber border (teak wood ) on both sides of the door. Door panel to be fabricated with a timber frame with 6mm thick teak wood plywood on both sides also hand rain to be fixed on both sides of all panel. finishes of the door should be varnish finish. | no | 2 |  |  | 0 | 0
7 | Fabrication of Timer frame for W1, Lead sheets to be fixed with the frame ( lead sheets will be provided by the client), | no | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
| BILL N0: 03 - DOORS AND WINDOWS | [5 empty] | 0
TOTAL OF BILL No: 03 - Carried over to summary
BILL N0: 04
TILING
4.1 | General
Prepare surface for approved bedding tiles with reach bedding materials as per the technical specifications & approved working drawings, fix tiles with ct grout in a precise manner to maintain correct alignment, applying tile grout and wiping any excess grout to ensure the required standards of finished works. Rates shall include for: fixing, bedding, grouting, and pointing materials; making good around pipes, sanitary fixtures, and similar; cleaning down and polishing any other similar works to ensure the required finish. All tiles shall be White ceramic / Homogeneous or equivalent.
4.2 | Floor finish
4.2.1 | laying of 300x300 skid resistant White Ceramic (white ceramic body) floor tiles, Tile selection and design to be finalized by consultant.
1 | New floor area | m² | 112 |  |  | 0 | 0
[6 empty] | 0 | 0
4.3 | NOVILON Floring |  |  |  |  | 0 | 0
4.3.1 | Supply and complete installation of Industrial quality Novilon Novilon to be installed with Consultant instruction, Rates include supply and installation, preparation of floor as per manufactures standards. Novilon to be installed as per manufactures instructions. |  |  |  |  | 0 | 0
1 | New floor area. | m² | 113 |  |  | 0 | 0
| BILL No: 4 - TILING | [5 empty] | 0
TOTAL OF BILL No: 4 - Carried over to summary
BILL No: 5
CEILINGS
5.1 | Interior Ceilings
The interior ceiling consist of a 50X50mm timber frame with a Gypsum board suspended ceiling, including framing beading nails and screws as per drawing and picture provided by this document. spans of timber frame are 600mm c/c vertical, 1200mm c/c Horizontal frame. Rates include removing the existing ceiling, clean debris and supply and fabrication of frame, fixing of Gypsum boards, puttying and painting. Rates also include 50mm thick Mineral wool installation with both side reflective foil Fixed in the ceiling frame, 12.5X12.5mm plastic mesh to be fixed on top of foiled and properly fixed on the ceiling frame,
1 | CT Department. | m² | 113 |  |  | 0 | 0
2 | Gyprum cornice for all the edges between wall and ceilling. | Item | 1 |  |  | 0 | 0
| BILL N0: 5 CEILINGS | [5 empty] | 0
TOTAL OF BILL No: 5 - Carried over to summary
BILL No: 6
PAINTING
6.1 | General
Interior walls Must be putty finish with texture painting(Scandinavian finishing), Terraco decorative paint or equivalent paint. Rates includes Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams.
Exterior & Exterior Ceiling (interior and exterior) shall be of 2 coats of (interior paint over 1 coat of primer or equivalent. Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for the provision and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and or masking floors fittings and similar work removing and replacing door window furniture.
All painting work shall be carried in accordance with the Specifications
For internal painting must be putty finish with texture painting(Scandinavian finishing), Terraco decorative paint or equivalent paint
6.2 | Wall painting
1 | Internal painting as per specification given above. (putty finish with texture painting (Scandinavian finishing), Terraco decorative paint or equivalent paint) | m² | 320 |  |  | 0 | 0
[6 empty] | 0 | 0
6.3 | Interior Ceiling painting |  |  |  |  | 0 | 0
6.3.1 | Interio paint putty finish on ceiling and beams, Gypsum board of all internal surfaces. 1 coat of primer & 2 coats of paints. |  |  |  |  | 0 | 0
1 | Interior paint with putty paint finish | m² | 114 |  |  | 0 | 0
[6 empty] | 0 | 0
| BILL No: 6 - PAINTING | [5 empty] | 0
TOTAL OF BILL No: 6 - Carried over to summary
BILL No: 1
ELECTRICAL INSTALLATIONS
General Notes
(a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories
(b) Rates for work in trench shall include for: excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers and disposal of surplus spoil
(c) Rates shall include for self-coloured, plastic warning tape overprinted with a warning identification text. designed to mark the position of buried utility lines. Made from 100% virgin polyethylene with high acid & alkali resistance.
7.2 | Electrical Boards |  |  |  |  | 0 | 0
1 | Three phase electrical distribution board (wall embedded): Supply and installation of D-Board . Rates Shall include all required Brackets and other electrical appliance as per drawings and Maldivian Regulations ( wall embedded ). All the light circuit should be one DB Sockets to be one DB. Rates to be included to connect main cable from nearest DB to hall area DB and complete all the works. | no | 1 |  |  | 0 | 0
2 | Completion of main connection from hospital panel board, size of cable should be 16m2 foru core cable, Rates includes to laying cable as per MEB regulatios. Length of cable and how to lay the cable to be check by contractor before bidding. | Item | 1 |  |  | 0 | 0
7.3 | Electrical wiring |  |  |  |  | 0 | 0
| Three phase Electrical wiring with copper conductor cable in conduits in walls as specified to: |  |  |  |  | 0 | 0
1 | Wiring with 2.5 mm² cable to Power points ( single sockets) | points | 13 |  |  | 0 | 0
2 | Wiring with 2.5 mm² cable to Power points ( Double sockets) | points | 14
3 | Wiring with 2.5 mm² cable to 1 x 15 Amp Power points | points | 3 |  |  | 0 | 0
4 | Wiring with 6 mm² cable to 1 x 15 Amp Power points (for AC) | points | 7 |  |  | 0 | 0
5 | Wiring with 2.5 mm² cable to lights and fan | points | 22 |  |  | 0 | 0
[6 empty] | 0 | 0
7.4 | Lighting / Fan |  |  |  |  | 0 | 0
1 | Ceiling diffusing embedded down light 150mm dia with 19W LED bulb, (Philips) E27, Cool day light, (not crystal light or not Stellar bright) Total lumen 2300. or equivalent, | no | 22 |  |  | 0 | 0
0
7.5 | Socket outlets
(a) All socket outlets shall be "Legrand" or equivalent.
1 | 1x13Amp wall Socket outlet, | no | 13 |  |  | 0 | 0
2 | 2x13Amp wall Socket outlet, | no | 14 |  |  | 0 | 0
3 | 1x15Amp wall socket outlet, | no | 3 |  |  | 0 | 0
4 | 1x15Amp wall socket outlet, for AC | no | 7 |  |  | 0 | 0
[6 empty] | 0 | 0
7.6 | Light switches |  |  |  |  | 0 | 0
| (a) All light switches shall be "Legrand" or equivalent. Each light should be control by one switch. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1 | Two gang switch | no | 3 |  |  | 0 | 0
2 | Three gang switch | no | 5 |  |  | 0 | 0
[6 empty] | 0 | 0
7.8 | Data, Network
Design, Supply and Complete Installation of computer networking, including CAT6 Cabling, Sockets and double layer switches, Allow for the provision of a completed and detailed set of shop drawings
1 | Completion of Data Network points (Data outlet (single gang)) | No | 6 |  |  | 0 | 0
2 | Completion of Telephone points (Telephone outlet (single gang) | No | 5 |  |  | 0 | 0
3 | Suply and completion of 16 port network switch, double layer switch, Dlink or equivalent | No | 1 |  |  | 0 | 0
7.9 | Finger print scanner |  |  |  |  | 0 | 0
| (a) Finger printing scanner should be fixed on both side of the door at Main entrance to get excess IN and OUT |  |  |  |  | 0 | 0
| (b) Finger scan reader brand ZKFR 1200 with both card and finger reading |  |  |  |  | 0 | 0
| (c) A controller should come with a back-up battery in case power loss. |  |  |  |  | 0 | 0
1 | Supply and complete installation of Access control unit, specification mentioned above. Readers on both side. ( Main entrance of Dialysis, CT room) | Item | 2 |  |  | 0 | 0
7.1 | Distribution Boards
1 | Design, Supply and Complete Installation of distribution board for UPS Incommer (Breaker in UPS Room). Rates include to supply and complete installation as per the following requirements. - Incoming :200A MCCB - Metering: Multifunction Power Meter (A/V/Hz/KW) - Indicators: LEDs per phase on incoming and outgoing - Enclosure: Should be included - Cable terminals Should be included | Item | 1 |  |  | 0 | 0
2 | Design, Supply and Complete Installation of distribution board for 200A PDB (inside CT room) Rates include to supply and complete installation as per the following requirements. - Incoming :200A MCCB - Outgoing : 3 pole, 160A MCCB x 01 Nos - Metering: Multifunction Power Meter (A/V/Hz/KW) - Indicators: LEDs per phase on incoming and outgoing - Enclosure: Should be included - Cable terminals Should be included | Item | 1 |  |  | 0 | 0
7.1 | Main Cable
1 | Supplying of 90sqm unarmed cable to the site to connect UPS to CT Genset and Gantry. | m | 20 |  |  | 0 | 0
2 | Supplying of 70sqm earth cable to the site . | m | 25 |  |  | 0 | 0
(d) Cable should be authorized by Energy authority
1.1 | Cable
1 | Supplying 150mm of armed cable which needs to be connected to the Hospital main panel to CT, UPS Room out side DB | meter | 160 | - | - | - | -
Cable Size: 4C X 150mm² CU/XLPE/SWA/PVC-BS 5467:600/1000 V- Amoured Cable legth: 160m
2 | Supplying 95mm of armed cable which needs to be connected to the CT UPS room out side DB to CT, UPS Room | meter | 6 | - | - | - | -
Cable Size: 4C X 95mm² CU/XLPE/SWA/PVC-BS 5467:600/1000 V- Amoured Cable legth: 6m
3 | Supplying 50mm of armed cable | meter | 55 | - | - | - | -
Cable Size: 4C X50mm² CU/XLPE/SWA/PVC-BS 5467:600/1000 V- Amoured Cable legth:55m
4 | Supplying 50mm of flexible single Core cable | meter | 3 | - | - | - | -
Cable Size: 1C X50mm² ( Flexible Cable) Cable legth: 3m
Supplying 95mm of flexible single Core cable
4 | Cable Size: 1C X95mm² ( Flexible Cable) Cable legth: 3m
5 | Supplying of box Casing
| Size: 2"x 3" | Meter | 7 | - | - | - | -
Length: 7 meter
1.2 | Excavations and refill | meter | 154 | - | - | - | -
1 | Excavation need to be done by according to the drawing 1 (at the depth of a feet warnning tape must be applied to the duct.)
The length and the depth of the trench is 154m and 2.5 feet respectively
1.3 | Earthing
1 | Earth pits with resistance less than 2 ohms
Distance betwwen Existing earth pit and new each pit must be 3 meters
3/4 earth rods must be used and must have clamps at the end
Erthing cable must be 50sqmm and length of earthing cable is 15M.
3 of the earth pit should be covered junction with cover.
2 | Completion of 3 earth pit with earthing cable and completion of earthing as per the above requirements. | Item | 1 | - | - | - | -
1.4 | Distribution Boards
1 | Design, Supply and Complete Installation of distribution board . Rates include to supply and complete installation as per the following requirements. * MCB 350A 3Pole, MCB 200A (With trip coil) * Cable terminal block Should be included (800A 4Pole) | Item | 1 | - | - | - | -
* Lug 150/12mm (12 Pcs)
* Lug 95/10mm (16 Pcs)
*Cable Sleeve 150mm ( Blue, Black, Yellow and Green) each 3 Pcs
* Cable Sleeve 95mm ( Blue, Black, Yellow and Green) each 4 Pcs
* Earth relay
*CT Coil 5/400A
2 | Design, Supply and Complete Installation of distribution board for UPS Incommer (Breaker in UPS Room). Rates include to supply and complete installation as per the following requirements. - Incoming :200A MCCB - Metering: Multifunction Power Meter (A/V/Hz/KW) - Indicators: LEDs per phase on incoming and outgoing - Enclosure: Should be included - Cable terminals Should be included | Item | 1 | - | - | - | -
3 | Design, Supply and Complete Installation of distribution board for 200A PDB (inside CT room) Rates include to supply and complete installation as per the following requirements. - Incoming :200A MCCB - Outgoing : 3 pole, 160A MCCB x 01 Nos - Metering: Multifunction Power Meter (A/V/Hz/KW) - Indicators: LEDs per phase on incoming and outgoing - Enclosure: Should be included - Cable terminals Should be included | Item | 1 | - | - | - | -
4 | Design, Supply and Complete Installation of distribution board . Rates include to supply and complete installation as per the following requirements. * MCB 160A 3Pole (With trip coil) | Item | 1 | - | - | - | -
* Lug 50/10mm ( 10 Pcs)
* Cable Sleeve 50mm ( Blue, Black, Yellow and Green) each 5 Pcs
*CT Coil 5/200A
* Cable terminal block Should be included (300A 4Pole)
BILL No: 1 - ELECTRICAL INSTALLATIONS
TOTAL OF BILL No: 1 - Carried over to summary
BILL No: 8
PARTITION WORKS,
8.1 | Partition Works.
8.1.1 | General
(a) Rates shall include for: insect treatment, all labor in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails, screws and the necessary fixing cleats, putting and painting.
[6 empty] | 0 | 0
[6 empty] | 0 | 0
8.2 | Dry wal Partitions |  |  |  |  | 0 | 0
1 | Fabrication and Completion of Drywall partition (Type 1) as per the drawings and, Rates included fabricating the frame to installing a lead sheet ( Lead sheet to be supplied by the client) and install board, puttying as well as completion of the partition work, | m² | 68 |  |  | 0 | 0
2 | Fabrication and Completion of Drywall partition (Type 2) as per the drawings and, Rates included fabricating the frame to installing a lead sheet ( Lead sheet to be supplied by the client) and install board, puttying as well as completion of the partition work, | m² | 58
3 | Fabrication and Completion of Drywall partition (Type 3) as per the drawings and, Rates included fabricating the frame to install board, puttying as well as completion of the partition work, | m² | 78
4 | Fabrication and Completion of Drywall partition (Type 4) as per the drawings and, Rates included fabricating the frame to install board, puttying as well as completion of the partition work, | m² | 22 |  |  | 0 | 0
[6 empty] | 0 | 0
8.3 | Closing of existing windows
1 | Closing of existing windows at the inside of the room, Rates included Design and fixing the frame with shera board with both side painting, and completion of the task. Size of windiws is 1250X1860mm, No of windows is 4. | m² | 9.3 |  |  | 0 | 0
2 | Closing of existing windows at the inside of the room, Rates included Design and fixing the frame with shera board with both side painting, and completion of the task. Size of windiws is 650X600mm, No of windows is 3. | m² | 1.17 |  |  | 0 | 0
8.4 | Registration counter
1 | Design and Fabrication of Registration counter as per Floor plan, Length of counter is 1.5 Meter, Fabrication of counter to be timber and appropriate thick plywood with PVC fomica. Top oc counter and table to be use granite top. | No | 1 |  |  | 0 | 0
0
BILL No: 8 - WOOD WORKS
TOTAL OF BILL No: 8 - Carried over to summary
BILL No: 09
AIR CONDITIONING SYSTEM
9.1 | General
(a) Rates shall include for detail design, supply and complete installation of A/C units pipework, insulation, fixings, electrical wiring, drain pipes etc.
(b) The Contractor shall provide detailed and complete set of shop drawings
9.2 | Air Condition
9.2.1 | Design, supply and complete installation of indoor unit, with 40ø drop in water (type) 25ø extended as Cd drop in 32 flex conduit 18ø Cd drain (typ0 run above FC insulated, CU1/3 48,000 BTU/HR, all AC unit is LG VRV digital wired thermostat or equivalent (INVERTER TYPE). |  |  |  |  | 0 | 0
| (b) All the Air conditions are Inverter type, LG or equivalent brand, All indoor unit should be ceiling cassette type. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1 | CT Room, 36000BTU with 1 wired remote connect both AC. | Item | 2 |  |  | 0 | 0
2 | Control Room, 12000BTU with 1 wired remote. | Item | 1 |  |  | 0 | 0
3 | Memography, 12000BTU with 1 wired remote. | Item | 1 |  |  | 0 | 0
4 | Radiologist, 12000BTU with 1 wired remote. | Item | 1
5 | UPS Room, 18000BTU with 1 wired remote connect both AC. | Item | 2 |  |  |  | 0
6 | Waiting area, 12000BTU with 1 wired remote connect both AC. | Item | 1
BILL No: 9 -AIR CONDITIONING SYSTEM
TOTAL OF BILL No: 9 - Carried over to summary
BILL No:10
| TENDERER'S ADJUSTMENTS |  |  |  |  | 0 | 0
| (a) Provide detail description of work items under each bill and insert extra pages if required. |  |  |  |  | 0 | 0
10.1 | Additions |  |  |  |  | 0 | 0
1 | PRELIMINARIES, Bill no. 01 |  |  |  |  | 0 | 0
2 | MASONRY AND PLASTERING, Bill no. 02 |  |  |  |  | 0 | 0
3 | DOORS AND WINDOWS, Bill no. 03 |  |  |  |  | 0 | 0
4 | TILING, Bill no. 04 |  |  |  |  | 0 | 0
5 | CEILINGS, Bill no. 05 |  |  |  |  | 0 | 0
6 | PAINTING, Bill no. 06 |  |  |  |  | 0 | 0
7 | ELECTRICAL INSTALLATIONS, Bill no. 7 |  |  |  |  | 0 | 0
8 | WOOD QWORKS, Bill no. 8 | [5 empty] | 0
9 | AIR CONDITIONING SYSTEM, Bill no. 10
10 | TENDERER'S ADJUSTMENTS, Bill no. 11
| ADDITIONS TOTAL |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
10.2 | Omissions |  |  |  |  | 0 | 0
1 | PRELIMINARIES, Bill no. 01 |  |  |  |  | 0 | 0
2 | MASONRY AND PLASTERING, Bill no. 02 |  |  |  |  | 0 | 0
3 | DOORS AND WINDOWS, Bill no. 03 |  |  |  |  | 0 | 0
4 | TILING, Bill no. 04 |  |  |  |  | 0 | 0
5 | CEILINGS, Bill no. 05 |  |  |  |  | 0 | 0
6 | PAINTING, Bill no. 06 |  |  |  |  | 0 | 0
7 | ELECTRICAL INSTALLATIONS, Bill no. 7 |  |  |  |  | 0 | 0
8 | WOOD QWORKS, Bill no. 8 | [5 empty] | 0
9 | AIR CONDITIONING SYSTEM, Bill no. 10
10 | TENDERER'S ADJUSTMENTS, Bill no. 9 | [5 empty] | 0
OMISSIONS TOTAL
| BILL No: 10 - TENDERER'S ADJUSTMENTS | [5 empty] | 0
TOTAL OF BILL No: 10 - Carried over to summary