{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["COVER SHEET","SUMMARY","BoQ"],"not_rendered":{"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"COVER SHEET","index":0,"n_rows":5,"n_cols":11,"rows_kept":5,"merged":[[1,0,1,11]],"flags":["formulas_cached_only"]}
[]
[]
[{"$nulls":10}," BILL OF QUANTITIES "]
[]
[{"$nulls":10},"CONSTRUCTION OF EXTENSION BUILDING AT N.  HOLHUDHOO HEALTH CENTER."]

{"sheet":"SUMMARY","index":1,"n_rows":22,"n_cols":5,"rows_kept":22,"merged":[[1,0,1,4],[2,0,2,4]],"flags":["formulas_cached_only"]}
[]
["SUMMARY OF BILLS OF QUANTITIES"]
["CONSTRUCTION OF EXTENSION BUILDING AT SH. NOOMARAA HEALTH CENTER."]
[]
["Bill No",null,"Description",null,"Amount"]
[]
[1,null,"PRELIMINARIES","Bill no. 01"]
[2,null,"GROUND  WORKS","Bill no. 02"]
[3,null,"CONCRETE","Bill no. 03"]
[4,null,"MASONRY AND PLASTERING","Bill no. 04"]
[5,null,"ROOFING","Bill no. 05"]
[6,null,"DOORS AND WINDOWS","Bill no. 06"]
[7,null,"TILING","Bill no. 07"]
[8,null,"CEILINGS","Bill no. 08"]
[9,null,"PAINTING","Bill no. 09"]
[10,null,"ELECTRICAL INSTALLATIONS","Bill no. 10"]
[11,null,"HYDRAULICS & DRAINAGE","Bill no. 11"]
[12,null,"AIR CONDITIONING SYSTEM","Bill no. 12"]
[13,null,"TENDERER'S ADJUSTMENTS","Bill no. 13"]
[null,null,"Sub total"]
[null,null,"GST 6%"]
[null,null,"GRAND TOTAL carried to form of bid"]

{"sheet":"BoQ","index":2,"n_rows":548,"n_cols":8,"rows_kept":548,"merged":[[4,0,5,0],[4,1,5,1],[4,2,5,2],[4,3,5,3],[4,7,5,7]],"flags":["formulas_cached_only"]}
["BILL OF QUANTITIES"]
["CONSTRUCTION OF EXTENSION BUILDING AT SH. NOOMARAA HEALTH CENTER."]
[]
[]
["Item","Description","Unit","Quantity","Rate/ Unit ","Rate/ Unit ","Total Unit Rate","Amount"]
[{"$nulls":4},"Material","Labour","Rates per Units"]
[null,"BILL No: 01"]
[null,"PRELIMINARIES"]
[]
[1.1,"General Notes"]
["(1)","Abbreviations"]
[null,"m - meter"]
[null,"No - numbers"]
[null,"m³ - cubic meter"]
[null,"m² - square meter"]
[null,"Lm - Linear meter"]
[null,"KG - Kilograms"]
[null,"incl - including"]
[null,"mm - millimeter"]
[null,"dia - diameter"]
[null,"SS - Stainless Steel"]
[null,"GI - Galvanized Iron"]
[]
[]
[1.4,"Clean-up"]
[{"v":1,"d":"(1)"},"Allow for clean-up of completed works and site upon completion.","Item",{"v":1,"d":"1.00"}]
[]
[]
[1.5,"INSPECTION TRIPS"]
[{"v":1,"d":"(1)"},"Arrange inspection trip to PMU team. Each inspection trip takes 2 days.\nContractor has to arrange following for trips;\n(a) Air tickets for 2 person: Male'/Sh. Funadhoo/Male' by air (normal fair), \n(b) Speed boat transfer from Sh. Funadhoo/Sh. Noomaraa/Sh. Funadhoo.\n(c) Accommodations (2 Air-condition room) per trip.","Item",{"v":3,"d":"3.00"}]
[]
[]
[]
[null,"BILL No: 01 PRELIMINARIES"]
[null,"TOTAL OF BILL No: 01 - Carried over to summary"]
[null,"BILL No: 02"]
[null,"GROUND  WORKS"]
[]
[2.1,"General"]
[null,"(a) Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating and disposing surplus soil."]
[]
[2.2,"Site Clearing"]
[{"v":1,"d":"(1)"},"Includes clearing of all trees and bushes complete with stems, roots, Flooring, and the reimbursement fees if applicable. The contractor is to advised to survey the construction site and ensure that all necessary works for site clearing are included and on completion of works.\nRates must include diverting all the pipes laid underground within the new building area (Sewer, wastewater, freshwater line and inspection chambers). Also, reallocate all AC outdoor units installed with the new building area.","m²",219.52]
[]
[2.3,"Excavation"]
[null,"Excavation shall be carried out in all type of materials and by whatever means are necessary accurately to the lines and levels shown in the approved drawing. No blasting of any kind will be permitted. Excavation for foundations and will include timbering of soil faces and dewatering.   Excavation quantities are measured to the faces of concrete members. Rates shall include for dewatering, leveling, grading, trimming compacting to faces of excavation, keeping sides plumb, backfilling, consolidating and disposing surplus soil and include for all additional excavation required to place the formwork / shuttering and dewatering the trench for the required days."]
[]
[{"v":1,"d":"(1)"},"Excavation for Footings (F1)","m³",4.86]
[{"v":2,"d":"(2)"},"Excavation for Tie beam beams (TB)","m³",17.01]
[]
[2.4,"Back Filling up to ground level."]
[{"v":1,"d":"(1)"},"Rates shall include for: leveling, grading, trimming and compacting as specified.","Item",{"v":1,"d":"1.00"}]
[]
[2.3,"Basement filling Above ground level."]
[{"v":1,"d":"(1)"}," Back filling above ground level in 100mm thick compacted layers of approved back fill soil and disposal of any excess soil and including ramp: rates shall include for leveling, grading, trimming and compaction in 100mm layers of filled areas of excavation ","m³",76.83]
[]
[2.4,"Damp Proof Membrane"]
[null,"Cutting and laying in position heavy duty polythene sheets of gauge 500 (not less than 1.5mm thick). Rates shall include for: dressing around and sealing to all penetrations. Apply slurry type waterproofing to all surfaces of concrete below ground level in accordance with manufacturer's instructions."]
[{"v":1,"d":"(1)"},"Damp proof membrane above lean concrete , Footings and Tie beams.","m",44.28]
[{"v":2,"d":"(2)"},"Damp proof membrane below floor slab","m²",219.52]
[{"v":3,"d":"(3)"},"Bituminous application to 3 sides of footings, Tie beams  & all the side of columns below ground level.","m²",108.07]
[]
[]
[]
[null,"BILL No: 02 - GROUND WORKS"]
[null,"TOTAL OF BILL No: 02 - Carried over to summary"]
[null,"BILL No: 03"]
[null,"CONCRETE"]
[3.1,"General"]
[null,"Rates shall include for cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wire and other supports, laps and wastage, all reinforcement bars except 6 mm dia bars shall be of deformed high strength bars. 6 mm bar shall be round mild steel bars. Binding wire shall be of 1.6 mm or 1.4 mm soft iron wire.\nReinforcement bars shall be cleaned before use i.e. should be free from rust, oil, din, or other coatings that reduces bonds, all reinforced bars and binding wires shall be stored under cover of at least 450 mm above the ground, cutting and bending according to approved manner & the approved working drawing, placing and fixing in position and binding should be as per the approved working drawing, laps in the bars shall be staggered, concrete cover for reinforcement shall not less than 50 mm for substructure, 40 mm for columns & side beams  and not more than 30 mm for slab and beam bottoms.  \nDesalinated water shall be used for all purposes, ground water shall not be used."]
[]
[3.2,"Lean Concrete"]
[null,"Lean concrete shall be 50mm thick & mix ratio shall be 1:2:6 by dry volume. Lean concrete placed at bottom of footing and foundation beam and below plinth for protection according to line and length mentioned in the approved drawing.  Quantity measured to the edges of concrete foundation members. Rate shall include of placing any formwork where necessary, batching, mixing, casting in all required items pouring & compacting and curing for 3 days and removal of any formwork include for provision casting of  required items & finishing after removal of formwork and additional concrete required to confirm to structural and excavated tolerances and rates shall include supply of all required works"]
[]
[{"v":1,"d":"(1)"},"50 mm thick lean concrete under the footings / strip footing and tie beam with a mix of 1:2:6","m³",1.89]
[]
[3.3,"Reinforced Concrete"]
[null,"In-situ reinforced concrete to:"]
[null,"*Add water proofing compound / admixture to concrete mix for walls GL and Roof Slabs"]
["3.3.1","Foundations"]
[{"v":1,"d":"(1)"},"Footings, F1 600x600x300mm","m³",{"v":1.9,"d":"1.90"}]
[{"v":2,"d":"(2)"},"Tie Beam, TB 200x250mm","m³",{"v":6.3,"d":"6.30"}]
[]
["3.3.2","Ground Floor"]
[{"v":1,"d":"(1)"},"RCC Ground Slab 100 mm thick,  (Rate shall include for reinforcement and shuttering required as per the drawings)","m³",21.95]
[{"v":2,"d":"(2)"},"Concrete columns C1, 200 x 200mm","m³",3.02]
[{"v":3,"d":"(3)"},"Completion of wheel chair ramp and steps at main entrance and garage area.","Item",{"v":1,"d":"1.00"}]
[{"v":4,"d":"(4)"},"Concrete Lintel beams, 150 x 150mm","m³",{"v":0.5,"d":"0.50"}]
[{"v":5,"d":"(5)"},"Concrete Sill beams, 150 x 150mm","m³",{"v":0.4,"d":"0.40"}]
[]
["3.3.3","Roof Level"]
[{"v":1,"d":"(1)"},"Roof beam, RB, 200x200mm","m³",5.38]
[{"v":2,"d":"(2)"},"Concrete columns C2, 200 x 200mm","m³",0.23]
[]
[3.3,"Formwork"]
[null,"(a) Rates shall include for all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes and removal of formwork.\nAll materials such as plywood, shutter oils and other items and transportation to work place and secure the formwork in highly precise manner guaranteeing straight and smooth concrete edges. \nCutting, fixing, bracing and oiling according to line and length as per approved working drawings removal of it after concrete has set without damaging the concrete faces."]
[]
["3.3.1","Foundations"]
[{"v":1,"d":"(1)"},"Footings, F1 600x600x300mm, (50% of form work) same form work to be use balance  50% Footings","m²",6.48]
[{"v":2,"d":"(2)"},"Tie beam, TB 200X250mm","m²",{"v":63,"d":"63.00"}]
["3.4.2","Ground Floor"]
[{"v":1,"d":"(1)"},"Concrete columns C1, 200 x 200mm, (50% of form work) same form work to be use balance  50% column","m²",30.24]
[]
["3.4.2","Roof level"]
[{"v":1,"d":"(1)"},"Roof beam, RB, 200x200 ","m²",80.64]
[{"v":2,"d":"(2)"},"Concrete columns C2, 200 x 200mm, (50% of form work) same form work to be use balance  50% column","m²",{"v":2.3,"d":"2.30"}]
[]
["3.4.3","Lintel & Sill Beams"]
[{"v":1,"d":"(1)"},"Lintel beams and Sill beams, 150x150mm, ","m³",1.42]
[]
[3.5,"Reinforcement"]
[null,"GENERAL : Rates shall include for cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wire and other supports, laps and wastage, all reinforcement bars except 6 mm dia bars shall be of deformed high strength bars. 6 mm bar shall be round mild steel bars. Binding wire shall be of 1.6 mm or 1.4 mm soft iron wire.\nReinforcement bars shall be cleaned before use i.e. should be free from rust, oil, din, or other coatings that reduces bonds, all reinforced bars and binding wires shall be stored under cover of at least 450 mm above the ground, cutting and bending according to approved manner & the approved working drawing, placing and fixing in position and binding should be as per the approved working drawing, laps in the bars shall be staggered, concrete cover for reinforcement shall not less than 50 mm for substructure, 40 mm for columns & side beams  and not more than 30 mm for slab and beam bottoms. "]
[null,"(b) All reinforcing bars shall be high strength bars."]
[]
["3.5.1","Substructure"]
[null,"Footings, F1 600x600x300mm"]
[{"v":1,"d":"(1)"},"Steel deformed bars, 12mm dia  x 6m","Bars",{"v":21,"d":"21.00"}]
[]
[null,"Tie beam, TB 200x200mm"]
[{"v":1,"d":"(1)"},"Steel deformed bars, 12mm dia  x 6m","Bars",{"v":93,"d":"93.00"}]
[{"v":2,"d":"(2)"},"Steel ring bars, 6mm dia x 6m","Bars",{"v":81,"d":"81.00"}]
[]
["3.5.2","Ground Floor"]
[null,"Concrete columns C1, 200 x 200mm"]
[{"v":1,"d":"(1)"},"Steel deformed bars, 12mm dia x 6m","Bars",{"v":52,"d":"52.00"}]
[{"v":2,"d":"(2)"},"Steel ring bars, 6mm dia x 6m","Bars",{"v":43,"d":"43.00"}]
[]
["3.5.3","Roof level"]
["3.5.3.1","Attached Beams,  "]
[null,"Roof beam, RB, 250x200 mm"]
[{"v":1,"d":"(1)"},"Steel deformed bars, 12mm dia  x 6m","Bars",{"v":90,"d":"90.00"}]
[{"v":2,"d":"(2)"},"Steel ring bars, 6mm dia x 6m","Bars",{"v":75,"d":"75.00"}]
["3.5.3.2","Concrete columns C2, 200 x 200mm"]
[{"v":1,"d":"(1)"},"Steel deformed bars, 12mm dia x 6m","Bars",{"v":4,"d":"4.00"}]
[{"v":2,"d":"(2)"},"Steel ring bars, 6mm dia x 6m","Bars",{"v":4,"d":"4.00"}]
[]
["3.5.5","Floor Slab"]
[{"v":1,"d":"(1)"},"10 mm dia bars @250 C/C, For ground slab","bars",{"v":292,"d":"292.00"}]
[]
["3.5.4","OTHER CONCRETE WORKS"]
[]
[{"v":1,"d":"(1)"},"Fabrication of Concrete sink cupboard at Pantry,  1.2 Meter length and 600mm width as per drawings, Rates shall include, concrete works  tiling of  all surfaces, installation of Single ball SS sink with faucet. And Rates shall also include all hydraulic works related to this item. Also rates shall include fixing of timber door panel and shelves. ","Item",{"v":1,"d":"1.00"}]
{"$rows_empty":7}
[null,"BILL No: 03 - CONCRETE WORKS"]
[null,"TOTAL OF BILL No: 03 - Carried over to summary"]
[null,"BILL No: 04"]
[null,"MASONRY AND PLASTERING"]
[]
[4.1,"General"]
[null,"Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of \nfloor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding\nframes or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good.\nBedding mortar (mixing ratio 1:4 i.e. cement: manufactured sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance.\nMasonry work shall be done with approved Machine compact cement blocks (300X150X150) with no defects. Lay in line and length as per approved working drawing\nBlock making (mixing ratio 1:4 i.e. cement: Local sand, Free form salt) shall be of OPC & free form salt."]
[null,"floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding "]
[null,"Rates shall include for: 25mm groove lines on external surfaces as shown on the drawing.\nDesalinated water shall be used for all purposes, ground water shall not be used."]
[]
[4.2,"Cement block work"]
[null,"External and external walls"]
["4.2.1","150mm wide Hollow blocks, laid on and incl. 1:5 Cement Mortar, tie rods, compression gap filler, nylon / plastic mesh as specified. (mixing ratio 1:4 i.e. cement: river sand, )"]
[{"v":1,"d":"(1)"},"Ground Floor (external walls and laundry internal walls)","m²",{"v":349,"d":"349.00"}]
[]
[4.3,"Plastering"]
[]
[null,"GENERAL: Interior and Exterior:  Plaster All masonry wall have smooth finishing of 18 mm thick cement plastering with mix ratio 1:4 (i.e. cement: River Sand), plastering material shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Plastic net should be provided wherever concrete surface and masonry meets, and cracks are unacceptable. Regular curing up to 7 days must be done, edges of doors, windows and ventilators included."]
[]
["4.3.1","25mm thick cement plastering (2 coat) on external walls and 18mm thick cement plastering on internal walls and concrete surfaces with 1:4 Cement mortar mix as specified incl. wire mesh at joints of concrete surfaces and walls (first, second coats)."]
[{"v":1,"d":"(1)"},"Ground floor","m²",{"v":698,"d":"698.00"}]
[]
[4.4,"Cement Screed Finish"]
["4.4.1","50mm thick Cement screeding on the"]
[null,"concrete floor with 1:4 cement mortar, (mixing ratio 1:4 i.e. cement: River sand)"]
[null,"mix incl. trowel finish; General Areas"]
[{"v":1,"d":"(1)"},"Ground Floor","m²",{"v":219,"d":"219.00"}]
[]
[4.5,"Dry wall partition"]
[null,"100mm thick dry wall partition, 50X75mm Timber frame (600mm c/c Vertical, 1200mm c/c Horizontal) with 9mm thick Shera board. Rates includes to fabricate partition as per manufactures instructions as well as puttying and Anti bacterial and washable paint on both side and etc."]
[{"v":1,"d":"(1)"},"Partition wall , up to the ceiling. ","m²",{"v":113,"d":"113.00"}]
[]
[4.6,"Curtain wall Partition"]
[null,"Minimum 80 Micron Aluminum (Dark sandy grey powder coated) partition wall with 6mm thick clear glass partition up to the ceiling. Aluminum frame (600mm c/c Vertical,  Rates includes to fabricate partition as per manufactures instructions as well as puttying and Anti bacterial and washable paint on both side and etc."]
[{"v":1,"d":"(1)"},"Partition wall , up to the ceiling. ","m²",{"v":29,"d":"29.00"}]
[]
[4.5,"Supplying and installation of Furniture"]
[null,"Supply and Complete installation of Furniture's."]
[{"v":1,"d":"(1)"},"Office Table with partition, 1200mm ( table should be solid wood).","No",{"v":6,"d":"6.00"}]
[{"v":2,"d":"(2)"},"Office Table 1500mm ( table should be solid wood).","No",{"v":2,"d":"2.00"}]
[{"v":3,"d":"(3)"},"Secretary chair , high back.","No",{"v":6,"d":"6.00"}]
[{"v":4,"d":"(4)"},"Secretary chair , Low back.","No",{"v":6,"d":"6.00"}]
[{"v":5,"d":"(5)"},"Meeting room chair \nMaterial: Iron/Aluminum\nSurface treatment: Spray painting finished.\nSeat and back: Hight-density sponge, minimum 2.5\" thick seat cushion ","No",{"v":30,"d":"30.00"}]
[{"v":6,"d":"(6)"},"Folding Meeting Table, 1400X600mm, \nSpecifications: Lockable castorsm Aluminum components\nFeature: Chrome with polished aluminum feet, Easy tilt mechanism for compact storage, \nTable surface: Scratch resistant, Natural Ash.","No",{"v":4,"d":"4.00"}]
[{"v":7,"d":"(7)"},"Supply and installation of 4 seater Airport Bench set, Armrest/Leg/bracket: Die-casting molding of high strength aluminum alloy. \nSeat: Numerical control hydraulic molding of high quality cold rolling steel plate. \nSponge: Cold consolidation and foam-forming of high density and super soft PU. \nBeam: metal tube with a diamond shape. \nCoating: Electrostatic coating after Rust-proof treatment, electroplated polishing.  ","No",{"v":6,"d":"6.00"}]
[]
[null,"BILL No: 04 - MASONRY AND PLASTERING"]
[null,"TOTAL OF BILL No: 04 - Carried over to summary"]
[null,"BILL No: 05"]
[null,"ROOFING"]
[]
[5.1,"General"]
[null,"(a) Rates shall include for: fair edges, dressing over angel fillets, turning into grooves, all other labors, circular edges, nails, screws and other fixings and laps."]
[null,"(b) Rates shall include to apply Wood preservative to  all the surface of timbers (Roof structure)."]
[null,"(b) Rates shall include to remove existing end cap, fascia board and necessary roofing sheets and necessary works to connect new roof to existing roof. "]
[]
[5.2,"Roof Coverings"]
[{"v":1,"d":"(1)"},"Roofing sheets: Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick - Aqua marine or equivalent for Main building and connection area.","m²",{"v":299,"d":"299.00"}]
[]
[5.3,"Capping and Flashings"]
[{"v":1,"d":"(1)"},"Ridge Capping/ flashing as per drawing:  Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick- Aqua marine or equivalent","m",{"v":12.5,"d":"12.50"}]
[{"v":2,"d":"(2)"},"Hip Capping (Roof hips):  Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick- Aqua marine or equivalent","m",{"v":25.6,"d":"25.60"}]
[]
[5.4,"Gutter"]
[null,"(a) MSP Color bond flat sheet gutter 200X200mm, Total coated thickness minimum 0.47mm thick,  including framing, and supports, straps, brackets, clips, stop ends, overflow, downpipe outlets, mesh flashings and all fixings and fastenings."]
[{"v":1,"d":"(1)"},"GUTTER: Blue scope steel international MSP- Aqua marine or equivalent ","m",{"v":74,"d":"74.00"}]
[]
[5.5,"Down Pipes"]
[{"v":1,"d":"(1)"},"75 mm dia uPVC down pipes including bends, junctions, straps, brackets, clips, roof drain strainer and all fixings.","m",{"v":42,"d":"42.00"}]
[]
[5.7,"Roof Structure"]
[{"v":1,"d":"(1)"},"(a) Rates shall include for: all labor in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws.\n(b) Rates includes to applying solignam wood preservative oil to all the surface of roof structure.\n(c) Rates include to fixing galvanized bolt, washers, nuts and 3mm thick MS gusset plates as show on the drawings."]
[]
[{"v":1,"d":"(1)"},"Timber rafters 50 X 150mm ","m",{"v":650,"d":"650.00"}]
[{"v":2,"d":"(2)"},"Timber purling 50 X 50mm  ","m",{"v":743,"d":"743.00"}]
[{"v":3,"d":"(3)"},"Timber Ridge beam 100 X 200mm ","m",{"v":13,"d":"13.00"}]
[{"v":4,"d":"(4)"},"Timber Hip Rafter 100 X 200mm ","m",{"v":30,"d":"30.00"}]
[{"v":5,"d":"(5)"},"Facia board, 18mm thick SHERA board 18 X 250mm","m",{"v":74,"d":"74.00"}]
[{"v":6,"d":"(6)"},"Applying Solignum wood preservative or equivalent  for all roof structure","item",{"v":1,"d":"1.00"}]
[]
[5.8,"Roof Insulation"]
[{"v":1,"d":"(1)"},"50mm thick Mineral wool installation with both side reflective foil on Fixed to underside of roofing with 12.5X12.5mm plastic mesh, Connection and edges of the foil to be sealed properly with a approved tape approved from consultant.","m²",{"v":299,"d":"299.00"}]
[]
[5.9,"Shelves"]
[{"v":1,"d":"(1)"},"Design and Fabrication of Wooden shelves at Medical Store room, length of Shelf is 1.2M, Width is 0.4m and heigh is 2M, 18mm thick Plywood with both side paint to be used. Frame with 4 shelf,","Item",{"v":15,"d":"15.00"}]
[]
[{"v":5.1,"d":"5.10"},"Casing of Column"]
[{"v":1,"d":"(1)"},"Boxing of existing column at center of Admin area as per drawing, ","Item",{"v":1,"d":"1.00"}]
[]
[null,"BILL No: 05 - ROOFING"]
[null,"TOTAL OF BILL No: 05 - Carried over to summary"]
[null,"BILL N0: 06"]
[null,"DOORS AND WINDOWS"]
[]
[6.1,"General"]
[null,"Aluminum Doors and windows, Fabricate and fix in position the aluminum doors and window frame  - aluminum doors and window (white powder coated, 60-80 micron, 1.5mm profile thickness) using recommended material with specified fixtures as shown in approved working drawings and installation should be as per technical specifications. Rates shall include for locks, latches, closures, push plates, pull handles, bolts, kick plates hinges, screws, washer and all door and window hardware and these materials should be of ss steel according to drawing and of superior quality."]
[null,"(a) All door and window frames and panels shall be as specified in the drawing and timber boarder to be fixed all timber doors."]
[null,"(b) All glazing shall be 6mm  Tinted."]
[null,"(Profiles to be chosen by client)."]
[]
[6.2,"Door / Windows units"]
[]
[{"v":1,"d":"(1)"},"D1,  Minimum 80 Micron Aluminum, Dark sandy grey powder coated Door 2600X1800mm with panels as per drawings. ","no",{"v":1,"d":"1.00"}]
[{"v":2,"d":"(2)"},"D2, Solid timber Door 2150X950mm with panels as per drawings. With timber border on both side of door leaf.","no",{"v":5,"d":"5.00"}]
[{"v":3,"d":"(3)"},"D3,  Minimum 80 Micron Aluminum, Dark sandy grey powder coated Door 2600X1800mm with panels as per drawings. ","no",{"v":7,"d":"7.00"}]
[{"v":4,"d":"(4)"},"D4, Solid timber Door 2150X950mm with panels as per drawings. With timber border on both side of door leaf.","no",{"v":2,"d":"2.00"}]
[{"v":6,"d":"(6)"},"D5,  Minimum 80 Micron Aluminum, Dark sandy grey powder coated Door 2600X1000mm with panels as per drawings. ","no",{"v":1,"d":"1.00"}]
[{"v":7,"d":"(7)"},"D1,  Minimum 80 Micron Aluminum, Dark sandy grey powder coated Door 2600X1800mm with panels as per drawings at Existing Health center, Rates must includes to remove existing main Entrance door at health  center and install new door.","no",{"v":1,"d":"1.00"}]
[]
[{"v":8,"d":"(8)"},"W1, Minimum 80 Micron Aluminum, Dark sandy grey powder coated window 2300x1300mm with panels as per drawing.  (also include Aluminum grill).","no",{"v":5,"d":"5.00"}]
[{"v":9,"d":"(9)"},"W2, Minimum 80 Micron Aluminum, Dark sandy grey powder coated window 1700x1300mm with panels as per drawings (also include Aluminum grill).","no",{"v":7,"d":"7.00"}]
[{"v":10,"d":"(10)"},"W3, Minimum 80 Micron Aluminum, Dark sandy grey powder coated window 1700x675mm with panels as per drawings (also include Aluminum grill).","no",{"v":2,"d":"2.00"}]
[{"v":11,"d":"(11)"},"V1, Minimum 80 Micron Aluminum, Dark sandy grey powder coated window 500x675mm with panels as per drawings ,  (also include Aluminum grill).","no",{"v":3,"d":"3.00"}]
[]
[]
[6.4,"Vertical Blinds"]
[null,"Supply and installation of Vertical Blinds for following windows, quality of vertical blinds should be high quality sun protected , Rates should be complete installation of Vertical blinds with railing and ect.."]
[{"v":1,"d":"(1)"},"W1 windows , size of finished blinds should be 2.6m height, X1.3meter width.","No",{"v":5,"d":"5.00"}]
[{"v":2,"d":"(2)"},"W2 windows , size of finished blinds should be 2.6m height, X1.8 meter width.","No",{"v":7,"d":"7.00"}]
[{"v":2,"d":"(2)"},"W3 windows , size of finished blinds should be 2.6m height, X1.1 meter width.","No",{"v":2,"d":"2.00"}]
[]
[6.5,"BED SIDE CURTAINS"]
[null,"Supply and complete installation of top quality Hospital grade bed side curtain including railing/Track. Length of rail/track is 6870mm, and height of curtain would be 2.4 meter."]
[{"v":1,"d":"(1)"},"General ward","Item",{"v":6,"d":"6.00"}]
[]
[]
[6.6,"Registration counter"]
[{"v":1,"d":"(1)"},"Design and Fabrication of Registration counter as per drawings, Fabrication of counter to be timber and appropriate thick plywood with PVC  fomica.","No",{"v":1,"d":"1.00"}]
[]
[]
[]
[]
[]
[null,"BILL N0: 06 -  DOORS AND WINDOWS"]
[null,"TOTAL OF BILL No: 06 - Carried over to summary"]
[null,"BILL N0: 07"]
[null,"TILING"]
[]
[7.1,"General"]
[null,"Prepare surface for approved bedding tiles with reach bedding materials as per the technical specifications & approved working drawings, fix tiles with ct grout in a precise manner to maintain correct alignment, applying tile grout and wiping any excess grout to ensure the required standards of finished works.\nRates shall include for: fixing, bedding, grouting, and pointing materials; making good around pipes, sanitary fixtures, and similar; cleaning down and polishing any other similar works to ensure the required finish.\nAll tiles shall be Full body homogeneous tiles or equivalent."]
[]
[7.2,"Floor finish"]
[]
["7.2.1","600x600 skid resistant full body homogeneous mat finish floor tiles, "]
[{"v":1,"d":"(1)"},"General floor tiling ","m²",{"v":188,"d":"188.00"}]
[{"v":2,"d":"(2)"},"Ramp area and front steps (office entrance)","m²",16.61]
[{"v":3,"d":"(3)"},"Toilet floor tiling","m²",{"v":9,"d":"9.00"}]
[]
[7.3,"Wall finish"]
["7.3.1","300x600 mm full body homogeneous wall tile,"]
[{"v":1,"d":"(1)"},"Admin area toilet 2.4 meter from floor finish level","m²",{"v":14.9,"d":"14.90"}]
[{"v":2,"d":"(2)"},"PHU area toilet 2.4 meter from floor finish level","m²",{"v":14.9,"d":"14.90"}]
[{"v":3,"d":"(3)"},"Staff toilet  ( out side of the building) 2.4 meter from floor finish level","m²",{"v":14.8,"d":"14.80"}]
[{"v":4,"d":"(4)"},"Laundry room 2.4 meter from floor finish level","m²",{"v":28.8,"d":"28.80"}]
[{"v":5,"d":"(5)"},"Tile skirting 150mm height.","m",{"v":120,"d":"120.00"}]
[]
[null,"BILL No: 7 - TILING"]
[null,"TOTAL OF BILL No: 7 - Carried over to summary"]
[null,"BILL No: 8"]
[null,"CEILINGS"]
[]
[8.1,"Interior Ceilings"]
[null,"Interior ceiling consist of  50X50mm Timber frame  @ 1200mm c/c vertical and 600mm c/c horizontal frame with 10mm thick Gypsum board suspended ceiling, including framing beading nails and screws as per manufactures instruction."]
[{"v":1,"d":"(1)"},"Design and installation of  ceiling for Conference room ( Double layer ceiling with LED strip) as per drawing.","m²",{"v":29.4,"d":"29.40"}]
[{"v":2,"d":"(2)"},"Ground floor","m²",190.12]
[{"v":3,"d":"(3)"},"Cornice Border ","Item",{"v":1,"d":"1.00"}]
[]
[8.2,"Exterior Ceilings"]
[null,"Exterior ceiling consist of 6mm thick Shera board suspended ceiling, including framing beading nails and screws. Grid of the frame to be 600 X 600 with timber supports to roof structure at every 1200 mm on the main entrance ceiling & 600X900 mm at eaves of roof ceiling, timber framing and supports shall  50 x 50mm size shall be seasoned red meranti timber as per given drawing."]
[]
[{"v":1,"d":"(1)"},"Ground floor","m²",{"v":69.6,"d":"69.60"}]
[]
[null,"BILL N0: 8 CEILINGS"]
[null,"TOTAL OF BILL No:8 - Carried over to summary"]
[null,"BILL No: 9"]
[null,"PAINTING"]
[]
[9.1,"General"," "]
[null,"Exterior wall shall be of 1 coat of oil based textured paint and 2 coats of Kansani weather bond paint ( oil based ) over 1 coat of oil based sealer ( white) or equivalent (according to technical specifications or approved drawings). Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams. "]
[null,"Interior wall shall be of 2-3 coats over 1 coat of water based sealer. Rates includes Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint, Kansani or equivalent as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams."]
[]
[null,"Exterior & Exterior Ceiling  (interior and exterior) shall be of 2 coats of (wood paint over 1 coat of wood primer, Kansani or equivalent. Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for the provision and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and or masking floors fittings and similar work removing and replacing door window furniture. "]
[null,"All painting work shall be carried in accordance with the Specifications"]
[]
[9.2,"Wall painting"]
[]
["9.2.1","External painting 1 coat of wall sealer, 1 coat texture compound & 2 coats of paints ( all coats to be oil based and external paint)."]
[null,"Internal Painting 1 coat of wall sealer & 2 coats of paints, Emulsion paint putty finish system on plastered and concrete surfaces of internal walls. "]
[{"v":1,"d":"(1)"},"Ground floor interior and exterior painting as section above, ( Masonry walls and dry partition walls)","m²",{"v":915,"d":"915.00"}]
[]
[]
[9.3,"Interior Ceiling painting"]
["9.3.1","Emulsion paint putty finish on concrete slab and beams, plywood / cement fiber board of all internal surfaces. 1 coat of primer & 2 coats of paints."]
[{"v":1,"d":"(1)"},"Emulsion putty paint finish","m²",219.52]
[]
[9.4,"Exterior ceiling painting"]
[{"v":1,"d":"(1)"},"Exterior Ceiling painting  as per specification given.","m²",{"v":69.6,"d":"69.60"}]
[]
[null,"BILL No: 9 - PAINTING"]
[null,"TOTAL OF BILL No: 9 - Carried over to summary"]
[null,"BILL No: 10"]
[null,"ELECTRICAL INSTALLATIONS"]
[]
[10.1,"General"]
[null,"(a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories"]
[null,"(b) Rates for work in trench shall include for: excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers, warning tape and disposal of surplus spoil"]
[null,"(c) Rates shall include for electrical conduits, fittings, equipment and similar all fixings to various building surfaces"]
[null,"(d) Each Light/ light fixture and its switch is measured as one  point; similarly each fan or each socket outlet is measured as one point;"]
[null,"(e) Rates shall include for supply and complete installation "]
[]
[10.2,"Mains connection"]
[{"v":1,"d":"(1)"},"Main connection: Rates shall include for screws, nails, bolts ,nuts, standard cable, fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories. Rates shall including for electrical conduits, fittings, equipment and similar items. Three - PHASE CABLE WIRING TO D-BOARD:  All necessary work in trench shall include for excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers warning tape and disposal of surplus soil supply and laying of the cable in according to Maldives electricity bureau. ( 16mm2 4-Core Cable, Approved by respective Authorities, GI pipe, warning tape), contractor has to measure cable length from site. ","no",{"v":1,"d":"1.00"}]
[]
[10.3,"Electrical Boards"]
[{"v":1,"d":"(1)"},"Three phase electrical distribution board (wall embedded),   Supply and complete installation of   D-Boards .  Rates Shall include all required Brackets and other electrical appliance as per drawings and Maldivian Regulations ( wall embedded ) Meter to be cover with whether proof box. All the light circuit should be one DB, Sockets circuit should be one DB.","no",{"v":2,"d":"2.00"}]
[]
[10.4,"Electrical wiring"]
[null,"Three phase Electrical wiring with copper conductor Keani cable in conduits in walls and in casing on soffits of slab as specified to:"]
[{"v":1,"d":"(1)"},"Wiring with 2.5 mm² cable to 1X13amp Power points","points",{"v":18,"d":"18.00"}]
[{"v":2,"d":"(2)"},"Wiring with 2.5 mm² cable to 2X13amp Power points","points",{"v":33,"d":"33.00"}]
[{"v":3,"d":"(3)"},"Wiring with 6 mm² cable to   1 x 15 Amp Power points","points",{"v":2,"d":"2.00"}]
[{"v":4,"d":"(4)"},"Wiring with 6 mm² cable to   1 x 15 Amp Power points (for AC)","points",{"v":8,"d":"8.00"}]
[{"v":5,"d":"(5)"},"Wiring with 2.5 mm² cable to lights and fan","points",{"v":75,"d":"75.00"}]
[]
[]
[]
[10.5,"Lighting / Fan"]
[{"v":1,"d":"(1)"},"Ceiling diffusing embedded down light 200mm dia with 21W LED  bulb,  (Philips), Cool day light, (not crystal light or not Stellar bright) Total lumen 2300. or equivalent,","no",{"v":59,"d":"59.00"}]
[{"v":2,"d":"(2)"},"Ceiling Fan 900mm dia, Usha or equivalent","no",{"v":5,"d":"5.00"}]
[{"v":3,"d":"(3)"},"Whether proof wall mount light with  13W LED  bulb,  (Philips) E27, Cool day light, Total lumen 1400, for Portico area","no",{"v":11,"d":"11.00"}]
[{"v":4,"d":"(4)"},"LED Emergency light ( 2 hours Battery charge)","no",{"v":6,"d":"6.00"}]
[" ",null,null," "]
[10.6,"Socket outlets"]
[null,"(a) All socket outlets shall be \"Legrand\" or equivalent."]
[{"v":1,"d":"(1)"},"1x13Amp wall Socket outlet,  ","no",{"v":18,"d":"18.00"}]
[{"v":2,"d":"(2)"},"2x13Amp wall Socket outlet,   ","no",{"v":33,"d":"33.00"}]
[{"v":3,"d":"(3)"},"1x15Amp wall socket outlet, ","no",{"v":2,"d":"2.00"}]
[{"v":4,"d":"(4)"},"1x15Amp wall socket outlet, for AC","no",{"v":8,"d":"8.00"}]
[]
[10.7,"Light switches "]
[null,"(a) All light switches shall be \"Legrand\" or equivalent. Each light should be control by one switch."]
[]
[{"v":1,"d":"(1)"},"One gang switch ","no",{"v":2,"d":"2.00"}]
[{"v":2,"d":"(2)"},"Two gang switch ","no",{"v":11,"d":"11.00"}]
[{"v":3,"d":"(3)"},"Three gang switch ","no",{"v":12,"d":"12.00"}]
[{"v":4,"d":"(4)"},"Fan Controller","no",{"v":5,"d":"5.00"}]
[{"v":5,"d":"(5)"},"Out door photo cell switch","no",{"v":3,"d":"3.00"}]
[]
[10.8,"Telephone Network"]
[null,"Design and supply and complete installation of Telephone network (Including cabling and sockets) and connect to existing PABX. Cat6 cable to be used for laying telephone network."]
[{"v":1,"d":"(1)"},"Completion of Telephone outlet points , rates includes to connect existing telephone network.","No",{"v":21,"d":"21.00"}]
[{"v":2,"d":"(2)"},"Supply and complete installation of PABX, minimum 30 Extension and 4 lines, ","Item",{"v":1,"d":"1.00"}]
[{"v":3,"d":"(3)"},"Supply and complete installation of Telephone","No",{"v":10,"d":"10.00"}]
[]
[]
[10.9,"Computer Network"]
[null,"Design, Supply and Complete Installation of computer networking, including CAT6 Cabling, Sockets and double layer switches,  Allow for the provision of a completed and detailed set of shop drawings "]
[{"v":1,"d":"(1)"},"Completion of  Data Network points","No",{"v":21,"d":"21.00"}]
[{"v":2,"d":"(2)"},"Supply and complete installation of 24 port, Double layer Manageable network switch D-Link or equivalent and connect to the Health Center network.","No",{"v":1,"d":"1.00"}]
[{"v":3,"d":"(3)"},"Supply and complete installation of Computer system as per specifications","No",{"v":6,"d":"6.00"}]
[{"v":4,"d":"(4)"},"Supply and complete installation of 75\" QLED TV, LG or Equivalent at meting room. Any cast or chrome cast must support.","No",{"v":1,"d":"1.00"}]
[{"v":5,"d":"(5)"},"Supplying of Canon Monochrome Multi-Functional Device, Image runner iR 2630i, (A4 & A3 sze) 3 in 1 printer or equivalent.","No",{"v":1,"d":"1.00"}]
[]
[{"v":10.1,"d":"10.10"},"Lightening Protection System"]
[{"v":1,"d":"(1)"},"Design, supply, and Complete installation of Erco, Eritech or equivalent lightening Protection System to cover the whole building as per local regulations (Rate shall include for all fixing of the system and down conductor to earthing) Coverage of lightning protection should be minimum 100 Meter Radius. Pric also include to install Marine grade SS post.","Item",{"v":1,"d":"1.00"}]
[]
[10.11,"Earthing"]
[null,"Earth pit with resistance less than 2 ohms"]
[null,"3/4 earth rods must be used and must have clamps at the end"]
[null,"Earth pit should be covered junction with cover."]
[{"v":1,"d":"(1)"},"Completion of  earth pit with earthing cable and completion of earthing as per the above requirements.","Item",{"v":1,"d":"1.00"}]
[]
[10.12,"SOLAR PV SYSTEM"]
[null,"Design supply and complete installation on 10KW Solar PV system. Rates includes to complete the system and connect to the grid with net metering as per specification. ( junction box specs, Solar AC&DC cable specs, solar bracket specs, inverter specs & solar panel must be same as specification).","Item",{"v":1,"d":"1.00"}]
[]
[10.13,"Fire Fighting"]
[{"v":1,"d":"(1)"},"CO2 Extinguisher","Item",{"v":3,"d":"3.00"}]
[{"v":2,"d":"(2)"},"H2O Extinguisher","Item",{"v":3,"d":"3.00"}]
[]
[null,"BILL No: 10 - ELECTRICAL INSTALLATIONS"]
[null,"TOTAL OF BILL No: 10 - Carried over to summary"]
[]
[null,"BILL No: 11"]
[null,"HYDRAULICS & DRAINAGE"]
[]
[11.1,"Hydraulics"]
["11.1.1","General"]
[null,"(a)  Rates shall include for excavation, laying pipes and backfilling trenches, maintaining faces of drainpipe trenches and pits, backfilling, disposal of surplus soil, bends, junctions, reducers, expansion joints brackets, joints, straps, hangers, screws, nails and fixing complete, and all joints and other incidental material, All Pipes and fittings area high pressure uPVC  pipes"]
[null,"fixing complete, including cutting and forming holes; excavating, laying pipes and backfilling trenches."]
[null,"(b) All pipe work shall be uPVC."]
[]
["11.1.2","Fresh water supply pipe work"]
[{"v":1,"d":"(1)"},"Completion of pipe works and Connect ground water supply pipe work to Fresh water network installed at hospital.","Item",{"v":1,"d":"1.00"}]
[]
["11.1.3","Ground water supply pipe work"]
[{"v":1,"d":"(1)"},"Completion of pipe works and Connect ground water supply pipe work.","Item",{"v":1,"d":"1.00"}]
[]
["11.1.4","Sanitary fixtures & accessories"]
[null,"Sanitary fixtures & Accessories: Sanitary fixtures complete including brackets, flush pipes, valves, overflows, plugs and washers, as specified."]
[{"v":1,"d":"(1)"},"Water closet (American standard, Neo Modern,  Anti bacterial type) or equivalent, (dual top flush)","no",{"v":3,"d":"3.00"}]
[{"v":2,"d":"(2)"},"Wash basin with pedestal (American Standard) or equivalent","no",{"v":3,"d":"3.00"}]
[{"v":3,"d":"(3)"},"Floor drain with gully & water trap.","no",{"v":4,"d":"4.00"}]
[{"v":4,"d":"(4)"},"Water tap for wash basin , ( Cotto) or equivalent","no",{"v":3,"d":"3.00"}]
[{"v":5,"d":"(5)"},"Muslim Shower with Stop valve, ( Cotto) or equivalent","no",{"v":3,"d":"3.00"}]
[{"v":6,"d":"(6)"},"Floor waste with SS gully trap ( toilet and laundry area)","no",{"v":4,"d":"4.00"}]
[{"v":7,"d":"(7)"},"Stop Valves, ( Cotto) or equivalent","no",{"v":20,"d":"20.00"}]
[{"v":8,"d":"(8)"},"Wall cabinet ( Mirror and towel bar) Cotto and equivalent","no",{"v":3,"d":"3.00"}]
[{"v":9,"d":"(9)"},"Water tap for laundry area , ( Cotto) or equivalent","no",{"v":2,"d":"2.00"}]
[{"v":10,"d":"(10)"},"Water tap for Gardening , ( Cotto) or equivalent","no",{"v":2,"d":"2.00"}]
[]
[11.2,"Drainage"]
["11.2.1","General"]
[null,"(a) Rates shall include for: excavation, maintaining faces of drain pipe trenches and pits, backfilling, disposal of surplus spoil; bends, junctions, reducers, expansion joints and all joints and other incidental materials."]
[null,"(b) All pipe work shall be UPVC"]
[{"v":1,"d":"(1)"},"Constructing  Concrete Inspection Chamber of required size with all provisions to connect pipelines as per drawing.","Item",{"v":4,"d":"4.00"}]
[]
[11.3,"Pipe work"]
[]
[{"v":1,"d":"(1)"},"Completion of pipe works and Connect Waste disposal pipe 75mm dia to Sewer network installed at existing system.","Item",{"v":1,"d":"1.00"}]
[{"v":2,"d":"(2)"},"Completion of pipe works and Connect Sewers pipe 100mm dia UPVC to   Sewer network installed at existing system. Rates includes to install inspection chamber as per consultants instructions.","Item",{"v":1,"d":"1.00"}]
[{"v":3,"d":"(3)"},"Completion of pipe works and Connect Sewers pipe 100mm dia UPVC to   Sewer network installed at existing system. Rates includes to install inspection chamber as per consultants instructions.","Item",{"v":1,"d":"1.00"}]
[]
[]
[]
[null,"BILL No: 11 - HYDRAULICS & DRAINAGE"]
[null,"TOTAL OF BILL No: 11 - Carried over to summary"]
[]
[null,"BILL No: 12"]
[null,"AIR CONDITIONING SYSTEM"]
[]
[12.1,"General"]
[null,"(a) Rates shall include for detail design, supply and complete installation of  A/C units pipework, insulation, fixings, electrical wiring, drain pipes etc."]
[null,"(b) The Contractor shall provide detailed and complete set of shop drawings"]
[null,"c) The contractor shall submit shop drawings of AC  and Exhaust System. The capacity shall be determined by the contractor. "]
[null,"d) Rate shall include complete installation of indoor units and outdoor units."]
[]
[12.2,"Air Condition"]
["12.2.1","Design, supply and complete installation of indoor and out door unit, \nAll AC unit is DAIKIN or equivalent (INVERTER TYPE). "]
[null,"The whole of the liquid and suction refrigerant lines including all fittings, valves etc. shall be insulated with 25mm thick insulation for all copper sizes. Insulation shall be closed cell elastomeric nitrile rubber."]
[null,"Protection of exposed Refrigerant Pipe Insulation:\nTo protect nitrile rubber of exposed piping from degrading due ultra violet rays & atmospheric conditions, it shall be covered polychelid coating with at least two coats of resin and hardener (Make-Polybond /Paramount Polytreat). Fiberglass tape shall be helically wound & painted with two coats of resin with hardener to give smooth & plain finish. "]
[null,"The brand of AC Equipment proposed should have an outdoor or outdoor sets with a\nmaximum Energy Efficiency Ratio of (EER) kw/kw 3.5."]
[null,"The Outdoor Unit Shall be Factory assembled with Weather Proof casing, constructed from Heavy Gauge Mild Steel Panels and coated with Anti Corrosive Epoxy resin finish. The unit should be completely factory wired and tested and shall be fitted with all necessary controls and switch gear."]
[null,"All outdoor units needs to have aluminum fins with 105+2 μm thickness, with special Anti corrosive coating of 1.3 ± 0. 35 μm thickness and an outside Hydrophilic layer coating of 0.35 ± 0. 07 μm thickness."]
[null,"All outdoor units shall be equipped with high efficiency optimized heat exchangers with variable heat exchanger circuits"]
[null,"All the outdoor unit must be fixed back side of the Building."]
[]
[null,"AC to be install Following rooms, all the indoor unit should be spilt type. "]
[]
[{"v":1,"d":"(1)"},"General office area, 48,000 BTU  spilt type Ceiling cassette air conditioner (with wired remote) DAIKIN or equivalent.","Item",{"v":1,"d":"1.00"}]
[{"v":1,"d":"(1)"},"PHU area, 34,000 BTU  spilt type Ceiling cassette air conditioner (with wired remote) DAIKIN or equivalent.","Item",{"v":1,"d":"1.00"}]
[{"v":2,"d":"(2)"},"Counselling room, 9000BTU  spilt type wall mount air conditioner DAIKIN or equivalent","Item",{"v":1,"d":"1.00"}]
[{"v":3,"d":"(3)"},"Meeting room, 18000BTU  spilt type Ceiling cassette air conditioner (with wired remote) DAIKIN or equivalent.","Item",{"v":1,"d":"1.00"}]
[{"v":4,"d":"(4)"},"In charge room, 9000BTU  spilt type Wall mount air conditioner (with wired remote) DAIKIN or equivalent.","Item",{"v":1,"d":"1.00"}]
[{"v":5,"d":"(5)"},"in charge-1 room, 9000BTU  spilt type Wall mount air conditioner (with wired remote) DAIKIN or equivalent.","Item",{"v":1,"d":"1.00"}]
[{"v":6,"d":"(6)"},"General Store, 18000BTU  spilt type Ceiling cassette air conditioner DAIKIN or equivalent","Item",{"v":1,"d":"1.00"}]
[{"v":7,"d":"(7)"},"Existing ward, 36000BTU spilt type Ceiling cassette air conditioner (with wired remote) DAIKIN or equivalent.. Rates includes to install additional power point to connect AC units.","Item",{"v":2,"d":"2.00"}]
[]
[null,"BILL No: 12 -AIR CONDITIONING SYSTEM"]
[null,"TOTAL OF BILL No: 12 - Carried over to summary"]
[]
[null,"BILL No:13"]
[null,"TENDERER'S ADJUSTMENTS"]
[]
[{"v":13,"d":"13.0"},"Any adjustments that the contractor may consider necessary should be written below and on similar continuation sheets if required, and the net amount of the adjustments is to be carried to the summary."]
[null,"(a) Provide detail description of work items under each bill and insert extra pages if required."]
[13.2,"Additions"]
[{"v":1,"d":"(1)"},"PRELIMINARIES, Bill no. 01"]
[{"v":2,"d":"(2)"},"GROUND  WORKS, Bill no. 02"]
[{"v":3,"d":"(3)"},"CONCRETE, Bill no. 03"]
[{"v":4,"d":"(4)"},"MASONRY AND PLASTERING, Bill no. 04"]
[{"v":5,"d":"(5)"},"METAL WORKS, Bill no. 05"]
[{"v":6,"d":"(6)"},"DOORS AND WINDOWS, Bill no. 06"]
[{"v":7,"d":"(7)"},"TILING, Bill no. 07"]
[{"v":8,"d":"(8)"},"CEILINGS, Bill no. 08"]
[{"v":9,"d":"(9)"},"PAINTING, Bill no. 09"]
[{"v":10,"d":"(10)"},"HYDRAULICS & DRAINAGE, Bill no. 10"]
[{"v":11,"d":"(11)"},"ELECTRICAL INSTALLATIONS, Bill no. 11"]
[{"v":12,"d":"(12)"},"AIR CONDITIONING SYSTEM, Bill no. 12"]
[{"v":13,"d":"(13)"},"TENDERER'S ADJUSTMENTS,  Bill no. 13"]
[null,"ADDITIONS TOTAL"]
[]
[13.3,"Omissions"]
[{"v":1,"d":"(1)"},"PRELIMINARIES, Bill no. 01"]
[{"v":2,"d":"(2)"},"GROUND  WORKS, Bill no. 02"]
[{"v":3,"d":"(3)"},"CONCRETE, Bill no. 03"]
[{"v":4,"d":"(4)"},"MASONRY AND PLASTERING, Bill no. 04"]
[{"v":5,"d":"(5)"},"METAL WORKS, Bill no. 05"]
[{"v":6,"d":"(6)"},"DOORS AND WINDOWS, Bill no. 06"]
[{"v":7,"d":"(7)"},"TILING, Bill no. 07"]
[{"v":8,"d":"(8)"},"CEILINGS, Bill no. 08"]
[{"v":9,"d":"(9)"},"PAINTING, Bill no. 09"]
[{"v":10,"d":"(10)"},"HYDRAULICS & DRAINAGE, Bill no. 10"]
[{"v":11,"d":"(11)"},"ELECTRICAL INSTALLATIONS, Bill no. 11"]
[{"v":12,"d":"(12)"},"AIR CONDITIONING SYSTEM, Bill no. 12"]
[{"v":13,"d":"(13)"},"TENDERER'S ADJUSTMENTS,  Bill no. 13"]
[null,"OMISSIONS TOTAL"]
[]
[null,"BILL No: 13 - TENDERER'S ADJUSTMENTS"]
[null,"TOTAL OF BILL No: 13 - Carried over to summary"]