## ECM4PV_HUA
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
ECM4PV_HUA: Electrical model for renewable machine | [5 empty] | Generador: |  |  |  | Fecha: | diciembre 2023
¿Por quien fue escrito el modelo?
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description |  |  | STATEs | # | Description
J |  |  |  | Trv - Filter time constant for voltage measurements [s] |  |  | K |  | PT1 V meas
J+1 |  |  |  | Tp - Filter time constant for power measurement [s] |  |  | K+1 |  | PT1 P meas
J+2 |  |  |  | Vdip - Undervoltage condition trigger voltage [pu] |  |  | K+2 |  | Piaw of Qctrl
J+3 |  |  |  | Vup - Overvoltage condition trigger voltage [pu] |  |  | K+3 |  | Piaw of Vctrl
J+4 |  |  |  | Qmin - Reactive power limit minimum [pu] |  |  | K+4 |  | PT1 of Constant Qctrl
J+5 |  |  |  | Qmax - Reactive power limit maximum [pu] |  |  | K+5 |  | PT1aw of Pctrl
J+6 |  |  |  | Kqp - Proportional gain Qctrl [pu] |  |  | K+6 |  | CurrLimitLogic_Int1
J+7 |  |  |  | Kqi - Integral gain Qctrl [pu] |  |  | K+7 |  | CurrLimitLogic_Int2
J+8 |  |  |  | Vmax - Voltage control maximum [pu] |  |  | K+8 |  | IpcmdBeforeDip
J+9 |  |  |  | Vmin - Voltage control minimum [pu]
J+10 |  |  |  | Kvp - Proportional gain Vctrl [pu] |  |  | VARs | # | Description
J+11 |  |  |  | Kvi - Integral gain Vctrl [pu] |  |  | L |  | QV inj ref
J+12 |  |  |  | Tiq - Time constant on lag delay [s] (Tiq>0) |  |  | L+1 |  | Pfref
J+13 |  |  |  | db1 - Voltage deadband for overvoltage iq injection [pu] |  |  | L+2 |  | Vbias
J+14 |  |  |  | db2 - Voltage deadband for undervoltage iq injection [pu] |  |  | L+3 |  | Qref
J+15 |  |  |  | Kqv - Gain for reactive current injection during fault [pu] |  |  | L+4 |  | Pref
J+16 |  |  |  | Iql1 - Minimum limit of reactive current injection [pu] |  |  | L+5 |  | PickDrop_THLD
J+17 |  |  |  | Iqh1 - Maximum limit of reactive current injection [pu] |  |  | L+6 |  | PickDrop_THLD_Time
J+18 |  |  |  | Thld - Reactive current injection delay after voltage dip [s] |  |  | L+7 |  | P_Ratelimiter
J+19 |  |  |  | dPmax - Ramp rate on power reference [pu/s] |  |  | L+8 |  | PD_VD_1
J+20 |  |  |  | dPmin - Ramp rate on power reference [pu/s] |  |  | L+9 |  | PD_VD_1_Time
J+21 |  |  |  | Pmax - Maximum power reference [pu] |  |  | L+10 |  | PD_VD_2
J+22 |  |  |  | Pmin - Minimum power reference [pu] |  |  | L+11 |  | PD_VD_2_Time
J+23 |  |  |  | Tpord - Time constant Pctrl [s] |  |  | L+12 |  | VD_Flipflop
J+24 |  |  |  | Tadip - Flipflop time after dip (VDT) [s] |  |  | L+13 |  | IpcmdFaultFlipFlop
J+25 |  |  |  | Imax - Maximum converter current limit [pu] |  |  | L+14 |  | IpcmdFaultPickDrop
J+26 |  |  |  | Vq1 - Reactive Power V-I pair, voltage [pu] |  |  | L+15 |  | IpcmdFaultPickDropTime
J+27 |  |  |  | Iq1 - Reactive Power V-I pair, current [pu] |  |  | L+16 |  | IqcmdInjFault
J+28 |  |  |  | Vq2 - (Vq2>=Vq1), Reactive Power V-I pair, voltage [pu] |  |  | L+17 |  | IQCMD
J+29 |  |  |  | Iq2 -Reactive Power V-I pair, current [pu] |  |  | L+18 |  | IPCMD
J+30 |  |  |  | Vq3 - (Vq3>=Vq2), Reactive Power V-I pair, voltage [pu] |  |  | L+19 |  | Et before clean dip (Internal)
J+31 |  |  |  | Iq3 - Reactive Power V-I pair, current [pu] |  |  | L+20 |  | Et before volt dip (Internal)
J+32 |  |  |  | Vq4 - (Vq4>=Vq3), Reactive Power V-I pair, voltage [pu] |  |  | L+21 |  | Ratelim Ipcmd
J+33 |  |  |  | Iq4 - Reactive Power V-I pair, current [pu] |  |  | L+22 |  | Voltage_Dip
J+34 |  |  |  | Vq5 - (Vq5>=Vq4), Reactive Power V-I pair, voltage [pu] |  |  | L+23 |  | FlipFlop_Ipcmd
J+35 |  |  |  | Iq5 -Reactive Power V-I pair, current [pu] |  |  | L+24 |  | Falling Edge Detector
J+36 |  |  |  | Vq6 - (Vq6>=Vq5), Reactive Power V-I pair, voltage [pu] |  |  | L+25 |  | PickDrop_Ipcmd
J+37 |  |  |  | Iq6 - Reactive Power V-I pair, current [pu] |  |  | L+26 |  | PickDrop_Ipcmd
J+38 |  |  |  | Vq7 - (Vq7>=Vq6), Reactive Power V-I pair, voltage [pu]
J+39 |  |  |  | Iq7 - Reactive Power V-I pair, current [pu]
J+40 |  |  |  | Vq8 - (Vq8>=Vq7), Reactive Power V-I pair, voltage [pu]
J+41 |  |  |  | Iq8 -Reactive Power V-I pair, current [pu]
J+42 |  |  |  | Vq9 - (Vq9>=Vq8), Reactive Power V-I pair, voltage [pu]
J+43 |  |  |  | Iq9 - Reactive Power V-I pair, current [pu]
J+44 |  |  |  | Vq10 - (Vq10>=Vq9), Reactive Power V-I pair, voltage [pu]
J+45 |  |  |  | Iq10 - Reactive Power V-I pair, current [pu]
J+46 |  |  |  | Vp1 - Real Power V-I pair, voltage [pu]
J+47 |  |  |  | Ip1 - Real Power V-I pair, current [pu]
J+48 |  |  |  | Vp2 - (Vp2>=Vp1), Real Power V-I pair, voltage [pu]
J+49 |  |  |  | Ip2 - Real Power V-I pair, current [pu]
J+50 |  |  |  | Vp3 - (Vp3>=Vp2), Real Power V-I pair, voltage [pu]
J+51 |  |  |  | Ip3 - Real Power V-I pair, current [pu]
J+52 |  |  |  | Vp4 - (Vp4>=Vp3), Real Power V-I pair, voltage [pu]
J+53 |  |  |  | Ip4 - Real Power V-I pair, current [pu]
J+54 |  |  |  | Vp5 - (Vp5>=Vp4), Real Power V-I pair, voltage [pu]
J+55 |  |  |  | Ip5 - Real Power V-I pair, current [pu]
J+56 |  |  |  | Vp6 - (Vp6>=Vp5), Real Power V-I pair, voltage [pu]
J+57 |  |  |  | Ip6 - Real Power V-I pair, current [pu]
J+58 |  |  |  | Vp7 - (Vp7>=Vp6), Real Power V-I pair, voltage [pu]
J+59 |  |  |  | Ip7 - Real Power V-I pair, current [pu]
J+60 |  |  |  | Vp8 - (Vp8>=Vp7), Real Power V-I pair, voltage [pu]
J+61 |  |  |  | Ip8 - Real Power V-I pair, current [pu]
J+62 |  |  |  | Vp9 - (Vp9>=Vp8), Real Power V-I pair, voltage [pu]
J+63 |  |  |  | Ip9 - Real Power V-I pair, current [pu]
J+64 |  |  |  | Vp10 - (Vp10>=Vp9), Real Power V-I pair, voltage [pu]
J+65 |  |  |  | Ip10 - Real Power V-I pair, current [pu]
J+66 |  |  |  | Kdp - Injection gain of active current when voltage dip is cleaning [pu]
J+67 |  |  |  | Kdq - Injection gain of reactive current when voltage dip is cleaning [pu]
J+68 |  |  |  | Tramp: Power ramp recovery time for LVRT/HVRT [s]
ICONs | # |  | Value | Description
M |  |  |  | Ctrl - Local or remote (PPC) control (local control if 0)
M + 1 |  |  |  | PQflag - P/Q priority flag for current limit (0-Qpriority / 1-Ppriority)
M + 2 |  |  |  | Qflag - Reactive Power Flag Ctrl (0-Constant PF or Qctrl / 1-V or Qctrl)
M +3 |  |  |  | Vflag - Voltage Flag Control (0-Vctrl / 1-Qctrl)
M +4 |  |  |  | PFflag - Power Factor Control Flag (1-Qctrl / 0-PFctrl)
M +5 |  |  |  | Pflag - Active Power Flag Ctrl (0-No dependency / 1-SPD dependency)
IBUS, 'USRMDL', ID, ECM4PV_HUA, 102, 0, 6, 69, 9, 27, ICON(M), CON(J) to CON(J+68)/
Diagrama de Bloques
ECM4PV_HUA
WQCMND
WPCMND
WIPCMD
WIQCMD