## GEGT3
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
GEGT3: Turbine-Governor Model Data Sheets | [5 empty] | Generador: |  | CVOTG12 |  | Fecha: | Sept 2015
Modelo escrito por el Usuario
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
CONs | # |  | Value | Description |  | STATEs | # |  | Description
J |  |  |  | KSTEAM, Proportion of power from steam turbine |  | K |  |  | Power Transducer Output
J+1 |  |  |  | RPELEC, Governor Droop |  | K+1 |  |  | Speed Governor Integral
J+2 |  |  |  | TPELEC, Time constant for Power Transducer (sec) |  | K+2 |  |  | Not Used
J+3 |  |  |  | KPGOV, Speed governor proportional gain |  | K+3 |  |  | Temperature Controller
J+4 |  |  |  | TGOV, Speed governor feedback time constant (sec) |  | K+4 |  |  | Fuel Valve Position
J+5 |  |  |  | TGOV2, Speed governor feedback time constant for off-line (sec) |  | K+5 |  |  | Gas Turbine Power
J+6 |  |  |  | KISOC, Isochronous Governor Gain |  | K+6 |  |  | Isochronous Control
J+7 |  |  |  | TTEMP, Temperature Limiter Feedback time Constant |  | K+7 |  |  | Thermal Couple Output
J+8 |  |  |  | KTEMP, Temperature Limiter Proportional Gain |  | K+8 |  |  | Radiation Shield
J+9 |  |  |  | ASET, Acceleration Controller Limit Setting |  | K+9 |  |  | Inlet Guide Vane Position
J+10 |  |  |  | KA, Acceleration Controller Proportional Gain |  | K+10 |  |  | IGV Control
J+11 |  |  |  | TA, Acceleration Controller Lead Time Constant (sec) |  | K+11 |  |  | Acceleration Limiter Rate
J+12 |  |  |  | WFNL, No Load Fuel Flow |  | K+12 |  |  | Override signal for governor
J+13 |  |  |  | FSRMIN, Minimum Fuel Stroke Reference |  | K+13 |  |  | Not Used
J+14 |  |  |  | TF, Fuel Valve Time Constant (sec) |  | K+14 |  |  | Forced Closing Valve Position
J+15 |  |  |  | KTURB, Turbine Gain |  | K+15 |  |  | Steam Turbine Power
J+16 |  |  |  | TTURB, Turbine Time Constant (sec)
J+17 |  |  |  | DB, Speed Dead band (pu)
J+18 |  |  |  | EMAX, Governor Error Limit (pu)
J+19 |  |  |  | RRAX, Load Reference Rate Limit (pu/sec)
J+20 |  |  |  | FSROL, Fuel Stroke Reference Over Ride (Not Used) |  | VARs | # |  | Description
J+21 |  |  |  | TAMB, Ambient Temperature (°C or °F) |  | L |  |  | FSRN
J+22 |  |  |  | Elevation, (Meters or Feet) |  | L+1 |  |  | FSRT
J+23 |  |  |  | FGCV, Forced Closing of Fuel Valve (pu) |  | L+2 |  |  | FSRA
J+24 |  |  |  | TGCV, Time Constant for Forced Closing (sec) |  | L+3 |  |  | FSR
J+25 |  |  |  | T1, Frequency Injection Table Time at Point #1 |  | L+4 |  |  | Compressor Pressure Ratio
J+26 |  |  |  | T2, Frequency Injection Table Time at Point #2 |  | L+5 |  |  | Ambient Pressure
J+27 |  |  |  | T3, Frequency Injection Table Time at Point #3 |  | L+6 |  |  | Air Flow
J+28 |  |  |  | T4, Frequency Injection Table Time at Point #4 |  | L+7 |  |  | Exhaust Temperature
J+29 |  |  |  | T5, Frequency Injection Table Time at Point 1#5 |  | L+8 |  |  | TNR, Load, speed reference
J+30 |  |  |  | N1, Frequency Injection Table Speed at Point #1 |  | L+9 |  |  | Starting Time for Frequency Inject
J+31 |  |  |  | N2, Frequency Injection Table Speed at Point #2 |  | L+10 |  |  | TNR
J+32 |  |  |  | N3, Frequency Injection Table Speed at Point #3 |  | L+11 |  |  | Speed Rate Limiter
J+33 |  |  |  | N4, Frequency Injection Table Speed at Point #4 |  | L+12 |  |  | IGV Rate Limit
J+34 |  |  |  | N5, Frequency Injection Table Speed at Point #5 |  | L+13 |  |  | Main Temperature Reference
J+35 |  |  |  | SLLO, Speed deviation limit (pu) |  | L+14 |  |  | IGV Temperature Reference
J+36 |  |  |  | PFRF, PFR Power Limit (pu) |  | L+15 |  |  | Sum of VAR(L+16) & TNHF/R
J+37 |  |  |  | Pulse, Speed Reference Rate (pu/sec) |  | L+16 |  |  | Initial Power Transducer Output
J+38 |  |  |  | LIMMW, Dead Band for Speed Reference
J+39 |  |  |  | TNKVR, Rate Limit for Speed Change |  | IBUS, ‘USRMDL’, ID, ’GEGT1’, 5, 0,10, 42, 16, 19
J+40 |  |  |  | TNKLI, Lower Limit for Speed Change |  | CON(J) to CON(J+41) /
J+41 |  |  |  | TNKLD, Upper Limit for Speed Change
ICONs | # |  | Value | Description
M |  |  |  | Internal Usage
M+1 |  |  |  | 0 for FSR*SPEED, 1 for FSR*1
M+2 |  |  |  | Internal Usage
M+3 |  |  |  | Gas Turbine Model
M+4 |  |  |  | 0 for FSR*SPEED, 1 for FSR*1
M+5 |  |  |  | Unit for Elevation, 0 for feet, 1 for meters
M+6 |  |  |  | Frequency Injection, 0 for turned off, 1 to turn on
M+7 |  |  |  | Internal Usage
M+8 |  |  |  | 0 for fixed guide vane, 1 for movable guide vane
M+9 |  |  |  | 0 for disable speed rate limit, 1 for enable speed rate limit
GEGT3
PELEC
PMECH
