## GEPVE
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
| GEPVE | [5 empty] | Generador: |  |  | Fecha: | 08/2018
GE PV Electrical Control
| This model is located at system bus |  |  |  |  | IBUS
| Machine identifier |  |  |  |  | ID
| This model uses CONs starting with |  |  |  |  | J
| and STATEs starting with |  |  |  |  | K
| and VARs starting with |  |  |  |  | L
| and ICONs starting with |  |  |  |  | M
| CONs | # |  | Value | Description
| J |  |  |  | Tfv, Filter time constant in voltage regulator (sec)
| J+1 |  |  |  | Kpv, Proportional gain in Voltage regulator (pu)
| J+2 |  |  |  | Kiv, Integrator gain in Voltage regulator (pu)
| J+3 |  |  |  | Rc, Line drop compensation resistance (pu)
| J+4 |  |  |  | Xc, Line drop compensation reactance (pu)
| J+5 |  |  |  | Qmx, Max limit in Voltage regulator (pu)
| J+6 |  |  |  | Qmn, Min limit in Voltage regulator (pu)
| J+7 |  |  |  | IPmax, Max active current limit (pu)
| J+8 |  |  |  | Trv, voltage sensor time constant (sec)
| J+9 |  |  |  | Kqi, Volt/MVAR gain
| J+10 |  |  |  | Vmincl, min voltage limit
| J+11 |  |  |  | Vmaxcl, max voltage limit
| J+12 |  |  |  | Kvi, Int. Volt/Term. Voltage gain
| J+13 |  |  |  | XIqmin, min limit
| J+14 |  |  |  | XIqmax, max limit
| J+15 |  |  |  | Tv, Lag in SolarCONTROL controller
| J+16 |  |  |  | Tp, Pelec filter in fast PF controller
| J+17 |  |  |  | Fn, A portion of on-line wind turbines
| J+18 |  |  |  | ImaxTD, converter current limit
| J+19 |  |  |  | Iphl, Hard active current limit
| J+20 |  |  |  | Iqhl, Hard reactive current limit
| J+21 |  |  |  | TIpqd, Reactive droop time constant
| J+22 |  |  |  | Kqd, Reactive droop gain
| J+23 |  |  |  | Xqd, Reactive droop Synthesizing Impedance
| J+24 |  |  |  | Vermx, Reactive power control maximum error signal
| J+25 |  |  |  | Vermn, Reactive power control minimum error signal
| J+26 |  |  |  | Vfrz, Reactive power control freeze voltage
| ICONs | # |  | Value | Description
| M |  |  |  | Remote bus # for voltage control
| M+1 |  |  |  | Memory
| M+2 |  |  |  | PFAFLG: =1 if fast PF control enabled
| M+3 |  |  |  | VARFLG: =1 if Qord is provided by SolarCONTROL If VARFLG=PFAFLG=0 then Qordr is provided as a Qref=const
| M+4 |  |  |  | PQFLAG: 0-Q priority, 1-P priority
| M+5 |  |  |  | Qdroop Line Branch "From Bus"
| M+6 |  |  |  | Qdroop Line Branch "To Bus"
| M+7 |  |  |  | Qdroop Line Branch ID
| STATEs | # |  | Description |  |  | VARs | # | Description
| K |  |  | Filter in Voltage regulator |  |  | L |  | Remote bus ref. voltage
| K+1 |  |  | Integrator in Voltage regulator |  |  | L+1 |  | Q ref. if PFAFLG=0 &VARFLG=0
| K+2 |  |  | Voltage sensor |  |  | L+2 |  | PF angle ref if PFAFLG=1
| K+3 |  |  | MVAR/Volt integrator |  |  | L+3 |  | Branch MW for Qdroop
| K+4 |  |  | Volt/MVAR integrator |  |  | L+4 |  | Branch MVAr for Qdroop
| K+5 |  |  | Lag of the SolarCONTROL |  |  | L+5 |  | Branch MVA for Qdroop
| K+6 |  |  | Input filter of PELEC for fast PF controller |  |  | L+6 |  | Auxiliary test signal
| K+7 |  |  | Filter in Reactive Droop |  |  | L+7 |  | Porder
IBUS, 'USRMDL', ID, 'GEPVE', 4, 0, 8, 27, 8, 8, ICONs from (M) to (M+7), CONs from (J) to (J+26)/
Four possible configurations:
1
Current North American configuration with SolarCONTROL:
VARFLG=1, PFAFLG=0, KQi small (e.g., KQi = 0.1)
2
Current North American configuration without SolarCONTROL:
VARFLG=0, PFAFLG=0, KQi very small (e.g., KQi = 0.001)
3
European (PFA control) with SolarCONTROL:
VARFLG=1, PFAFLG=0, KQi large (e.g., KQi = 0.5), KVi large
4
European (PFA control) without SolarCONTROL:
VARFLG=0, PFAFLG=1, Specify desired PFA, KQi large (e.g., KQi = 0.5), KVi large
Diagrama de Bloques