## GGOV1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
GGOV1: Turbine-Governor Model Data Sheets | [6 empty] | Generador: |  |  | Fecha: | Julio 2011
GE General Governor/Turbine Model
This model is located at system bus | [5 empty] | IBUS
Machine identifier | [5 empty] | ID
This model uses CONs starting with | [5 empty] | J
and STATEs starting with | [5 empty] | K
and VARs starting with | [5 empty] | L
and ICONs starting with | [5 empty] | M
CONs |  | # |  | Value | Description
J |  |  |  |  | R, Permanent droop, pu
J+1 |  |  |  |  | Tpelec, Electrical power transducer time constant, sec
J+2 |  |  |  |  | maxerr, Maximum value for speed error signal
J+3 |  |  |  |  | minerr, Minimum value for speed error signal
J+4 |  |  |  |  | Kpgov, Governor proportional gain
J+5 |  |  |  |  | Kigov, Governor integral gain
J+6 |  |  |  |  | Kdgov, Governor derivative gain
J+7 |  |  |  |  | Tdgov, Governor derivative controller time constant, sec
J+8 |  |  |  |  | vmax, Maximum valve position limit
J+9 |  |  |  |  | vmin, Minimum valve position limit
J+10 |  |  |  |  | Tact, Actuator time constant, sec
J+11 |  |  |  |  | Kturb, Turbine gain
J+12 |  |  |  |  | Wfnl, No load fuel flow, pu
J+13 |  |  |  |  | Tb, Turbine lag time constant, sec
J+14 |  |  |  |  | Tc, Turbine lead time constant, sec
J+15 |  |  |  |  | Teng, Transport lag time constant for diesel engine, sec
J+16 |  |  |  |  | Tfload, Load Limiter time constant, sec
J+17 |  |  |  |  | Kpload, Load limiter proportional gain for PI controller
J+18 |  |  |  |  | Kiload, Load limiter integral gain for PI controller
J+19 |  |  |  |  | Ldref, Load limiter reference value pu
J+20 |  |  |  |  | Dm, Mechanical damping coefficient, pu
J+21 |  |  |  |  | Ropen, Maximum valve opening rate, pu/sec
J+22 |  |  |  |  | Rclose, Maximum valve closing rate, pu/sec
J+23 |  |  |  |  | Kimw, Power controller (reset) gain
J+24 |  |  |  |  | Aset, Acceleration limiter setpoint, pu/sec
J+25 |  |  |  |  | Ka, Acceleration limiter gain
J+26 |  |  |  |  | Ta, Acceleration limiter time constant, sec ( > 0)
J+27 |  |  |  |  | Trate, Turbine rating (MW)1
J+28 |  |  |  |  | db, Speed governor deadband
J+29 |  |  |  |  | Tsa, Temperature detection lead time constant, sec
J+30 |  |  |  |  | Tsb, Temperature detection lag time constant, sec
J+31 |  |  |  |  | Rup, Maximum rate of load limit increase
J+32 |  |  |  |  | Rdown, Maximum rate of load limit decrease
1If the turbine rating [CON(J+27)] is greater than zero, the input PELEC is converted in the model
to per unit on turbine rating base, else PELEC is converted to per unit on machine base.
ICONs |  | # |  | Value | Description
M |  |  |  |  | Rselect, Feedback signal for governor droop: 1 electrical power 0 none (isochronous governor) -1 fuel valve stroke (true stroke) -2 governor output (requested stroke)
M+1 |  |  |  |  | Flag Switch for fuel source characteristic: 0 fuel flow independent of speed 1 fuel flow proportional to speed
STATEs |  | # |  | Description |  |  | VARs | # | Description
K |  |  |  | Machine Electrical Power Measurement |  |  | L |  | Load Reference
[7 empty] | L+1 |  | Output of Load Limiter PI Control
K+1 |  |  |  | Governor Differential Control |  |  | L+2 |  | Output of Governor PID Control
K+2 |  |  |  | Governor Integral Control |  |  | L+3 |  | Low Value Select Output
K+3 |  |  |  | Turbine Actuator |  |  | L+4 |  | Output of Turbine Actuator
K+4 |  |  |  | Turbine Lead-Lag |  |  | L+5 |  | Output of Turbine Lead-Lag
K+5 |  |  |  | Turbine load limiter measurement |  |  | L+6 |  | Supervisory Load Controller Setpoint, Pmwset
K+6 |  |  |  | Turbine Load Limiter Integral Control
[7 empty] | L+7 |  | Delay Table
K+7 |  |  |  | Supervisory Load Control |  |  | …
K+8 |  |  |  | Acceleration Control |  |  | L+19
K+9 |  |  |  | Temperature Detection Lead-Lag |  |  | L+20 |  | Dead Band
IBUS, ’GGOV1’, ID, ICON(M) and ICON(M+1), CON(J) to CON(J+32) /
Diagrama de Bloques
Notes:
a. This model can be used to represent a variety of prime movers controlled by PID governors. It is suitable, for example, for representation of:
• gas turbine and single shaft combined cycle turbines • diesel engines with modern electronic or digital governors • steam turbines where steam is supplied from a large boiler drum or a large header whose pressure is substantially constant over the period under study • simple hydro turbines in dam configurations where the water column length is short and water inertia effects are minimal
b. Per unit parameters are on base of the turbine MW base (Trate). If no value is entered for Trate, parameters are specified on generator MVA base. c. The range of fuel valve travel and of fuel flow is unity. Thus the largest possible value of Vmax is 1.0 and the smallest possible value of Vmin is zero. Vmax may, however, be reduced below unity to represent a loading limit that may be imposed by the operator or a supervisory control system. For gas turbines Vmin should nor¬mally be greater than zero and less than wfnl to represent a minimum firing limit. The value of fuel flow at maximum output must be less than, or equal to unity, depending on the value of kturb. d. The parameter Teng is provided for use in representing diesel engines where there is a small but measurable transport delay between a change in fuel flow setting and the development of torque. In the majority of cases Teng should be zero. e. The parameter Flag is provided to recognize that fuel flow, for a given fuel valve stroke, can be proportional to engine speed. This is the case for GE gas turbines and for diesel engines with positive displacement fuel injectors. Flag should be set to unity for all GE gas turbines and most diesel engines. Flag should be set to zero where it is known that the fuel control system keeps fuel flow independent of engine speed. f. The load limiter module may be used to impose a maximum output limit such as an exhaust temperature limit. To do this the time constant Tfload should be set to rep¬resent the time constant in the measurement of temperature (or other signal), and the gains of the limiter, Kpload, Kiload, should be set to give prompt stable control when on limit. The load limit can be deactivated by setting the parameter Ldref to a high value. g. The parameter Dm can represent either the variation of engine power with shaft speed or the variation of maximum power capability with shaft speed. If Dm is positive it describes the falling slope of the engine speed versus power characteristic as speed increases. A slightly falling characteristic is typical for recip¬rocating engines and some aeroderivative turbines. If Dm is negative the engine power is assumed to be unaffected by shaft speed, but the maximum permissible fuel flow is taken to fall with falling shaft speed. This is characteristic of single shaft industrial gas turbines. h. This model includes a simple representation of a supervisory load controller. This controller is active if the parameter Kimw is non-zero. The load controller is a slow acting reset loop that adjusts the speed/load reference of the turbine governor to hold the electrical power output of the unit at its initial condition value Pmwset. Pmwset is given a value automatically when the model is initialized and stored in VAR(L+6), and can be changed thereafter. The load controller must be adjusted to respond gently relative to the speed governor. A typical value for Kimw is 0.01, cor¬responding to a reset time of 100 seconds. Setting Kimw to 0.001 corresponds to a relatively slow acting load controller. i. The parameters Aset, Ka, and Ta describe an acceleration limiter. These parame¬ters may be omitted from the data list if the limiter is not active. j. The parameter db is the speed governor dead band. This parameter is in terms of per unit speed. k. Tsa and Tsb are provided to augment the exhaust gas temperature measurement subsystem in gas turbines. l. Rup and Rdown specify the maximum rate of increase and decrease of the output of the load limit controller (Kpload/Kiload).
GGOV1
SPEED
PMECH
PELEC