## GPMPPC_WMC_22_00
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
GPMPPC_WMC_22_00 | [5 empty] | Generador: |  |  |  | Fecha: | diciembre 2023
Modelo del fabricante
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description |  |  | STATEs | # | Description
J |  |  |  | Nominal Value of the PV plant in MVA (P).
J+1 |  |  |  | Nominal Value of the PV plant in MVA (Q).
J+2 |  |  |  | Maximum P delivered at POI in pu
J+3 |  |  |  | Minimum P delivered at POI in pu
J+4 |  |  |  | Maximum Q delivered at POI in pu
J+5 |  |  |  | Minimum Q delivered at POI in pu
J+6 |  |  |  | Proportional gain of reactive power PI controller.
J+7 |  |  |  | Integral gain of reactive power PI controller.
J+8 |  |  |  | Non-windup gain of reactive power PI controller.
J+9 |  |  |  | Maximum inverter reactive power injection.
J+10 |  |  |  | Minimum inverter reactive power injection.
J+11 |  |  |  | Reactive power ramp up. |  |  | VARs | # | Description
J+12 |  |  |  | Reactive power ramp down.
J+13 |  |  |  | If needed, offset to be applied to the PPC reactive control, 0 by default
J+14 |  |  |  | Value of reactive power for which the inverters do not reduce active power referenced to plant maximum, 1 by default
J+15 |  |  |  | Proportional gain of active power PI controller
J+16 |  |  |  | Integral gain of reactive power PI controller
J+17 |  |  |  | Non-windup gain of active power PI controller
J+18 |  |  |  | Maximum plant active power provided by the inverters.
J+19 |  |  |  | Minimum power where the plant can be curtailed.
J+20 |  |  |  | Active power ramp up
J+21 |  |  |  | Active power ramp down
J+22 |  |  |  | If needed, offset to be applied to the PPC active control, 0 by default
J+23 |  |  |  | Percentage of STATCOM maximum power to do reactive control.
J+24 |  |  |  | Maximum STATCOM reactive power.
J+25 |  |  |  | Maximum Capacity of each capacitor bank.
J+26 |  |  |  | Number of capacitor Banks, < 10
J+27 |  |  |  | Over-voltage control deadband
J+28 |  |  |  | Over-voltage control droop
J+29 |  |  |  | Under-voltage control deadband
J+30 |  |  |  | Under-voltage control droop
J+31 |  |  |  | Filter applied at voltage measure in Capacitor and STATCOM compensation mode.
J+32 |  |  |  | Voltage threshold for fault detection.
J+33 |  |  |  | Voltage threshold for overvoltage detection.
J+34 |  |  |  | Freezing time delay post FRT
J+35 |  |  |  | Maximum reactive power provided by the plant
J+36 |  |  |  | Minimum reactive power provided by the plant
J+37 |  |  |  | Proportional gain of voltage (Q_MODE = 3) controller
J+38 |  |  |  | Integral gain of voltage (Q_MODE = 3) PI controller
J+39 |  |  |  | Non-windup gain of voltage (Q_MODE = 3) controller
J+40 |  |  |  | Maximum expected voltage in pu during Q control mode 3
J+41 |  |  |  | Minimum expected voltage in pu during Q control mode 3
J+42 |  |  |  | Capacitor switching on/off hysteresis of nominal capacitor bank capacity
J+43 |  |  |  | Frequency to start power reduction (OF mode 1).
J+44 |  |  |  | Frequency to stop power reduction (OF mode 1).
J+45 |  |  |  | Frequency to start power reduction (OF mode 2).
J+46 |  |  |  | Frequency to start power reduction (OF mode 2).
J+47 |  |  |  | Droop of frequency control (OF mode 2).
J+48 |  |  |  | Droop of frequency control (OF mode 2).
J+49 |  |  |  | Frequency to start power increase (UF mode 1).
J+50 |  |  |  | Frequency to stop power increase (UF mode 1).
J+51 |  |  |  | Frequency to start power increase (UF mode 2).
J+52 |  |  |  | Frequency to start power increase (UF mode 2).
J+53 |  |  |  | Droop of frequency control (UF mode 2).
J+54 |  |  |  | Droop of frequency control (UF mode 2).
J+55 |  |  |  | Relative active power limit for frequency control.
J+56 |  |  |  | Reactive power offset for droop curve displacement (Q_MODE = 2)
ICONs | # |  | Value | Description
M |  |  |  | Delay caused by communication system in measurement.
M + 1 |  |  |  | Delay caused by communication system in sending commands.
M + 2 |  |  |  | PPC loop execution time.
M +3 |  |  |  | Reactive power mode: 0: Q set-point , 1: Power factor (P), 2: Q(U), 3: Voltage PI control 4: Q(P)
M +4 |  |  |  | Reactive power ramp control, enabled = 1, disabled = 0
M +5 |  |  |  | Reactive power compensation system available, Capacitor banks = 1, STATCOM = 2
M +6 |  |  |  | Over-frequency control mode 0: disabled, 1: mode 1, 2: mode 2
M +7 |  |  |  | Under-frequency control mode 0: disabled, 1: mode 1, 2: mode 2
M +8 |  |  |  | Frequency regulation characteristic Pgen=0, Pnom=1, for over and under frequency control mode 2.
M +9 |  |  |  | Active power ramp control, enabled = 1, disabled = 0
M +10 |  |  |  | Number of branch initial bus where the measurements must be taken
M +11 |  |  |  | Number of branch final bus where the measurements must be taken
M +12 |  |  |  | Circuit identifier of the branch where the measurements must be taken, -1 by default
M +13 |  |  |  | Bus of, if there are, capacitor banks to control
M +14 |  |  |  | Bus where the GPM PPC model and GPM SB model are allocated
M +15 |  |  |  | Initialization Mode: From Power Flow (flat test) = 0; 0 Power = 1; Maximum Power = 2. It is recommended to use From Power Flow Status. 0 by default
M +16 |  |  |  | Nominal frequency (typically either 50 or 60)
M +17 |  |  |  | Bus-bar for voltage measurement
M +18 |  |  |  | Bus-bar for frequency measurement
M +19 |  |  |  | Flow measurement direction, 1 when the measured flow is towards the grid, - 1 when opposite.
M +20 |  |  |  | Nominal Voltage POI in kV
M +21 |  |  |  | Active power setpoint priority in Frequency droop mode
Diagrama de Bloques