## IEEEG1SDU
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
IEEEG1SDU: IEEE Type 1 Speed-Governing Model | [5 empty] | Generador: |  |  |  | Fecha: | Noviembre 2025
Library Model
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description |  |  | STATEs | # | Description
J |  |  |  | K |  |  | K |  | First governor integrator
J+1 |  |  |  | T1 (sec) |  |  | K+1 |  | Governor output
J+2 |  |  |  | T2 (sec) |  |  | K+2 |  | First turbine integrator
J+3 |  |  |  | T3 (> 0) (sec) |  |  | K+3 |  | Second turbine integrator
J+4 |  |  |  | Uo (pu/sec) |  |  | K+4 |  | Third turbine integrator
J+5 |  |  |  | Uc (< 0) (pu/sec) |  |  | K+5 |  | Fourth turbine integrator
J+6 |  |  |  | PMAX (pu rating)
J+7 |  |  |  | PMIN (pu rating)
J+8 |  |  |  | T4 (sec)
J+9 |  |  |  | K1
J+10 |  |  |  | K2
J+11 |  |  |  | T5 (sec) |  |  | VARs | # | Description
J+12 |  |  |  | K3 |  |  | L |  | Reference, P0
J+13 |  |  |  | K4 |  |  | L+1 |  | Internal memory
J+14 |  |  |  | T6 (sec) |  |  | L+2 |  | Deadband output
J+15 |  |  |  | K5
J+16 |  |  |  | K6
J+17 |  |  |  | T7 (sec)
J+18 |  |  |  | K7
J+19 |  |  |  | K8
J+20 |  |  |  | DBH (pu), deadband for overspeed, (≥ 0)
J+21 |  |  |  | DBL (pu), deadband for underspeed, (≤ 0)
J+22 |  |  |  | TRate (MW), turbine rating, if zero, then MBASE used
Notes:
Governor gain K = 1/R is in pu on TRate. If TRate > 0, else in pu on generator MVA base
For cross-compound units, IBUS and ID are the bus number and machine identifier of the high-pressure unit,
while JBUS and JD are the bus number and machine identifier of the low pressure unit.
IBUS, ’USRMDL’, ID, ’IEEEG1SDU’ 5 0 0 23 6 3 CON(J) to CON(J+22) /
DYR Data record when governor is used for cross-compound machines
IBUS, ’USRMDL’, ID, ’IEEEG1CDU’ 11 0 0 23 6 3 JBUS JD CON(J) to CON(J+22) /
Diagrama de Bloques
IEEEG1SDU
Δω
PMECHLP
P0
PMECHHP