## OEL5CU1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
OEL5CU1: IEEE 421.5 2016 Overexcitation Limiter Model | [5 empty] | Generador: |  |  |  | Fecha: | Noviembre 2025
Library Model
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description |  |  | STATEs | # | Description
J |  |  |  | IFDpu (pu), OEL inverse time integrator pickup level |  |  | K |  | Integrator
J+1 |  |  |  | IFDlim (pu), OEL inverse time limit active level |  |  | K+1 |  | OEL Input
J+2 |  |  |  | VOELmax1 (pu), OEL inverse time integrator upper limit |  |  | K+2 |  | lead-lag
J+3 |  |  |  | TOEL (s), OEL inverse time integrator time constant (> 0) |  |  | K+3 |  | OEL PI block
J+4 |  |  |  | KIFDT (pu), OEL inverse time lag gain |  |  | K+4 |  | VFE lag block
J+5 |  |  |  | K (pu), OEL lead-lag gain |  |  | K+5 |  | VFE PI block
J+6 |  |  |  | TCoel (s), OEL lead time constant
J+7 |  |  |  | TBoel (s), OEL lag time constant
J+8 |  |  |  | IFDpulev (pu), OEL activation logic pickup level
J+9 |  |  |  | TIFDlev (s), OEL activation logic timer setpoint
J+10 |  |  |  | IFDdolev (pu), OEL activation logic drop out level
J+11 |  |  |  | IFDref1 (pu), OEL reference 1 |  |  | VARs | # | Description
J+12 |  |  |  | IFDref2 (pu), OEL reference 2 |  |  | L |  | IOELactive
J+13 |  |  |  | KPoel (pu), OEL proportional gain |  |  | L+1 |  | Iref
J+14 |  |  |  | KIoel (pu/s), OEL integral gain |  |  | L+2 |  | Timer for OEL activation logic
J+15 |  |  |  | VOELmax (pu), OEL PI control upper limit
J+16 |  |  |  | VOELmin (pu), OEL PI control lower limit
J+17 |  |  |  | KPvfe (pu), Exciter field current regulator proportional gain
J+18 |  |  |  | KIvfe (pu/s), Exciter field current regulator integral gain
J+19 |  |  |  | VVFEmax (pu), Exciter field current regulator upper limit
J+20 |  |  |  | VVFEmin (pu), Exciter field current regulator lower limit
J+21 |  |  |  | KSCALE1, Scale factor for OEL input
J+22 |  |  |  | TF1 (s), OEL input transducer time constant
J+23 |  |  |  | KSCALE2, Scale factor IFEbase/IFErated
J+24 |  |  |  | TF2 (s), Exciter field current transducer time constant
J+25 |  |  |  | VFEref (pu), Exciter field current reference setpoint
J+26 |  |  |  | Ibias (pu), OEL reference bias
ICONs | # |  | Value | Description
M |  |  |  | OEL Input Flag: 1 : Efd (field voltage), 2 : Ifd (field current), 3: Vfe (exciter filed current)
M + 1 |  |  |  | SW1 (OEL reference logic switch): 0 : Position A, 1 : Position B
M + 2 |  |  |  | K1, Exponent for inverse time function (> 0)
IBUS ’USRMDL’ ID ’OEL5CU1’ 10 0 3 27 6 3 ICON(M) to ICON(M+2) CON(J) to CON(J+26) /
Notes
1. SW1 is a user-selection option. Position A corresponds to the application to a static excitation system or
a brushless system. Position B is used for rotating exciters with collector rings.
2. OEL input is user-selected. Could be generator field current IFD or generator field voltage EFD or exciter
field current VFE.
3. Parameter KSCALE1 should be calculated to convert from the per unit base used for the OEL input signal
to a per unit base corresponding to the rated value for the selected OEL input signal. All other parameters
in the model are expressed in per unit of rated value.
4. Parameter KSCALE2 should be calculated to convert from the per unit base used for the VFE input signal
to a per unit base corresponding to the rated value for the selected OEL input signal. All other parameters
in the model are expressed in per unit of rated value.
5. The logical signal Iref is the output of the S-R flip-flop block shown in the diagram. The input signals for
the S-R flip-flop block are the result of the logical tests indicated in the block diagram.
6. The logic switch SWref uses the signal Iref shown in the block diagram. SWref is in position “A” if Iref =
0 and in position “B” if Iref = 1.
7. The OEL activation logic uses the parameters IFDpulev, IFDdolev, and TIFDlev. It also uses the signal Ipu
shown in the block diagram.
The Activation Block has a setting for pickup when the input signal exceed IFDpulev and a timer is activated.
The timer will proceed until the value of the input signal goes below the value of IFDdolev. When
that occurs the Activation Block is reset.
Note: The check of Ipu > IFDDOLEV is not shown in the IEEE 421.5 2016 OEL5C documentation. This
was added into the PSS(R)E model after discussions with the equipment vendors and in consultation
with IEEE 421.5 representatives.
IF (Ipu > IFDPULEV) for longer than TIFDlev
enable OEL, i.e., set IOELactive = 1
ELSE IF ( Ipu < IFDDOLEV)
block OEL, i.e., set IOELactive = 0
END
8. The logic switch SWOELout uses the logic signals IOELactive and Iref shown in the block diagram.
IF (Iref = 1) or (IOELactive = 1)
enable OEL, i.e., set SWOELout in position “A”
ELSE
block OEL, i.e., set SWOELout in position “B”
END
9. The output signal from OEL5C should be coordinated with the AVR output as these two signals are inputs
to a low value gate. For brushless applications of one manufacturer, there was a scale factor for the
output to reflect the scaling of the field quantities from a per unit system based on the generator air
gap values for no load, nominal voltage condition to the per unit system at rated terminal conditions.
With the present model, there is no scale factor for the output signal, and that scaling will need to be
factored into the values for the IFDREF1, IFDREF2 and VFEREF.
Diagrama de Bloques