## REAX4BU1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
REAX4BU1: Renewable Energy Auxiliary Control Model | [6 empty] | Generador: |  |  |  | Fecha: | Noviembre 2025
Library model
This model is located at system bus | [5 empty] | IBUS
Machine identifier | [5 empty] | ID
This model uses CONs starting with | [5 empty] | J
and STATEs starting with | [5 empty] | K
and VARs starting with | [5 empty] | L
and ICONs starting with | [5 empty] | M
CONs |  | # |  | Value | Description |  |  | STATEs | # | Description
J |  |  |  |  | Tw1 (s), Measurement time constant |  |  | K |  | Measurement lag (reactive part)
J+1 |  |  |  |  | Kw1 (pu on MBASE), Gain for signal in reactive path (Note 3) |  |  | K+1 |  | Measurement lag (real part)
J+2 |  |  |  |  | Kp1 (pu on MBASE), Gain for signal in real path (Note 3)
J+3 |  |  |  |  | Wmax (pu), Maximun value of W01 |  |  | VARs | # | Description
J+4 |  |  |  |  | Wmin (pu), Minimum value of W01 |  |  | L |  | wref1, Reference in reactive path (pu on MBASE)
J+5 |  |  |  |  | Pmax (pu), Maximum value of P01 |  |  | L+1 |  | W01, Model output in reactive part (pu on MBASE)
J+6 |  |  |  |  | Pmin (pu), Minimum value of P01 |  |  | L+2 |  | pref1, Reference in active path (pu on MBASE)
[8 empty] | L+3 |  | P01, Model output in active part (pu on MBASE)
ICONs |  | # |  | Value | Description
M |  |  |  |  | Bus number at which the Plant controller Model is attached
Notes:
1.This model receive input from the plant control model (PLNTBU1) which is connected at bus specified in ICON(M). If there is no plant control model attached at the bus specifiedin ICON(M), then the inputs (Wext and Pext) to the REAX4BU1 and REAX3BU1 models would be zero.
2. Model parameters are specified in pu of the machine base (machine to which this model is attached).
3. Gains Kw1 and Kp1 should be non-zero.
IBUS, 'USRMDL', ID, 'REAX4BU1', 107, 0, 1, 7, 2, 4, ICON(M), CON(J) to CON(J+6) /
Diagrama de Bloques
MODELO
Pext
W01
Wext
P01