## REECA1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
REECA1: Generic Renewable Electrical Control Model | [5 empty] | Generador: | Fecha: | Mar 2021
PSSE Renewable Energy Electrical Model
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description
J |  |  |  | Vdip (pu), low voltage threshold for reactive current injection
J+1 |  |  |  | Vup (pu), high voltage threshold for reactive current injection
J+2 |  |  |  | Trv (s), Voltage filter time constant
J+3 |  |  |  | dbd1 (pu), Voltage error dead band lower threshold (<=0)
J+4 |  |  |  | dbd2 (pu), Voltage error dead band upper threshold (>=0)
J+5 |  |  |  | Kqv (pu), Reactive current injection gain
J+6 |  |  |  | Iqhl (pu), Upper limit on reactive current injection Iqinj
J+7 |  |  |  | Iqll (pu), Lower limit on reactive current injection Iqinj
J+8 |  |  |  | Vref0 (pu), User defined reference (if 0, initialized by model)
J+9 |  |  |  | Iqfrz (pu), Value at which Iqinj is held following voltage dip
J+10 |  |  |  | Thld (s) (>=0), Time that Iqinj is held at Iqfrz following voltage dip
J+11 |  |  |  | Thld2 (s) (>=0), Time for which IPMAX is held at faulted value
J+12 |  |  |  | Tp (s), Filter time constant for electrical power
J+13 |  |  |  | QMax (pu), limit for reactive power regulator
J+14 |  |  |  | QMin (pu) limit for reactive power regulator
J+15 |  |  |  | VMAX (pu), Max. limit for voltage control
J+16 |  |  |  | VMIN (pu), Min. limit for voltage control
J+17 |  |  |  | Kqp (pu), Reactive power regulator proportional gain
J+18 |  |  |  | Kqi (pu), Reactive power regulator integral gain
J+19 |  |  |  | Kvp (pu), Voltage regulator proportional gain
J+20 |  |  |  | Kvi (pu), Voltage regulator integral gain
J+21 |  |  |  | Vbias (pu), User-defined bias (normally 0)
J+22 |  |  |  | Tiq (s), Time constant on delay s4
J+23 |  |  |  | dPmax (pu/s) (>0) Power reference max. ramprate
J+24 |  |  |  | dPmin (pu/s) (<0) Power reference min. ramprate
J+25 |  |  |  | PMAX (pu), Max. power limit
J+26 |  |  |  | PMIN (pu), Min. power limit
J+27 |  |  |  | Imax (pu), Maximum allowable total converter current limit
J+28 |  |  |  | Tpord (s), Power filter time constant
J+29 |  |  |  | Vq1 (pu), Reactive Power V-I pair, voltage
J+30 |  |  |  | Iq1 (pu), Reactive Power V-I pair, current
J+31 |  |  |  | Vq2 (pu) (Vq2>Vq1), Reactive Power V-I pair, voltage
J+32 |  |  |  | Iq2 (pu) (Iq2>=Iq1), Reactive Power V-I pair, current
J+33 |  |  |  | Vq3 (pu) (Vq3>Vq2), Reactive Power V-I pair, voltage
J+34 |  |  |  | Iq3 (pu) (Iq3>=Iq2), Reactive Power V-I pair, current
J+35 |  |  |  | Vq4 (pu) (Vq4>Vq3), Reactive Power V-I pair, voltage
J+36 |  |  |  | Iq4 (pu) (Iq4>=Iq3), Reactive Power V-I pair, current
J+37 |  |  |  | Vp1 (pu), Real Power V-I pair, voltage
J+38 |  |  |  | Ip1 (pu), Real Power V-I pair, current
J+39 |  |  |  | Vp2 (pu) (Vp2>Vp1), Real Power V-I pair, voltage
J+40 |  |  |  | Ip2 (pu) (Ip2>=Ip1), Real Power V-I pair, current
J+41 |  |  |  | Vp3 (pu) (Vp3>Vp2), Real Power V-I pair, voltage
J+42 |  |  |  | Ip3 (pu) (Ip3>=Ip2), Real Power V-I pair, current
J+43 |  |  |  | Vp4 (pu) (Vp4>Vp3), Real Power V-I pair, voltage
J+44 |  |  |  | Ip4 (pu) (Ip4>=Ip3), Real Power V-I pair, current
ICONs | # |  | Value | Description
M |  |  |  | Bus number for voltage control; local control if 0
M+1 |  |  |  | PFFLAG: • 1 if power factor control • 0 if Q control (which can be controlled by an external signal)
M+2 |  |  |  | VFLAG: • 1 if Q control • 0 if voltage control
M+3 |  |  |  | QFLAG: • 1 if voltage or Q control • 0 if constant pf or Q control
M+4 |  |  |  | PFLAG: • 1 if active current command has speed dependency • 0 for no dependency
M+5 |  |  |  | PQFLAG, P/Q priority flag for current limit: • 0 for Q priority • 1 for P priority
| STATEs |  | # | Description
| K |  |  | Voltage Measurement filter
| K+1 |  |  | Real power filter
| K+2 |  |  | PI controller for reactive power
| K+3 |  |  | PI controller for voltage error
| K+4 |  |  | First Order lag for reactive current
| K+5 |  |  | First order lag for Pord
| VARs |  | # | Description
| L |  |  | Bus reference voltage (Vref0)
| L+1 |  |  | Storage of current state for state transition (possible values: 0, 1 or 2)
| L+2 |  |  | Power factor reference angle (pfaref), radians
| L+3 |  |  | user defined bias as calculated by the model
| L+4 |  |  | Timer for Thld counter
| L+5 |  |  | Previous value of power reference
| L+6 |  |  | Stored Ipmax value
| L+7 |  |  | Timer for Thld2 counter
| L+8 |  |  | Storage for voltage_dip (used only when Thld2 > 0)
Notes:
1.This model can be used with Type 3 and 4 wind machines. When used for modeling of Type 3 wind machine, the other models to be used along with this model are regca1, repcta1 (optional), wtdta1, wtpta1, wtara1, wttqa1. When used for modeling of Type 4 machines, the other models to be used along with this control model are regca1, wtdta1, and repca1 (optional).
2. When used for modeling Type 3 machines set Pflag (i.e., ICON (M+4)) to 0. Speed dependency will be simulated by the Torque controller (WTTQA1).
3. Thld could be either zero, or less than zero or greater than zero. a. If Thld > 0, then once voltage_dip (voltage_dip is a flag which is set and reset in the model. Voltage_dip is 0 if the Vdip<VT<Vup, else it is 1) becomes 0, Iqinj is held at Iqfrz for Thld seconds. b. If Thld < 0, then once voltage_dip goes to 0, Iqinj remains state (equal to Iqv) for Thld seconds. c. If Thld = 0 , then Iqinj goes back to zero as soon as Voltage_dip becomes 0.
4. pfaref (the power factor angle reference) value is initialized by the model based on ini- tial real and reactive power outputs from the machine.
5. wg is the per unit generator speed and is set in the drive train model.
6. Qref is initialized by the model to a constant or can be connected to an external plant controller model).
7. Pref is initialized by the model to a constant or can be connected to an external plant controller model).
8. Normally Vbias is zero. The user specified Vbias value (which is in CON(J+21)) is used only when the QFlag=1, VFlag=0 and PfFlag=0. For all other combinations of QFlag, VFlag and PfFlag values, the Vbias value is either not required or is calculated and stored in VAR(L+3).
9. ICON(M) contains the remote bus number. If this is 0 or if the remote bus number is not specified then the local bus is used for control.
10. The VDL1 characteristics are defined by 4 pairs of Vq-Iq points (pu voltage versus reac- tive current). Data for the first two pairs (Vq1, Iq1) and (Vq2, Iq2) is mandatory (i.e., these cannot be specified as zero). A maximum of 4 pairs of Vq-Iq points can be speci- fied. The first Vq entry that has a zero value, signals the end of Vq-Iq data. Unused Vq- Iq pairs should be entered as zero. The Vq-Iq values should be such that Vq1 < Vq2 < Vq3 < Vq4, and Iq1 ≤ Iq2 ≤ Iq3 ≤ Iq4.
11. The VDL2 characteristics are defined by 4 pairs of Vp-Ip points (pu voltage versus active current). Data for the first two pairs (Vp1, Ip1) and (Vp2, Ip2) is mandatory (i.e., these cannot be specified as zero). A maximum of 4 pairs of Vp-Ip points can be spec- ified. The first Vp entry that has a zero value, signals the end of Vp-Ip data. Unused Vp- Ip pairs should be entered as zero. The Vp-Ip values should be such that Vp1 < Vp2 < Vp3 < Vp4, and Ip1 ≤ Ip2 ≤ Ip3 ≤ Ip4.
IBUS, 'REECA1', ID, ICON(M) to ICON(M+5), CON(J) to CON(J+44) /
Diagrama de Bloques