## REECB1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
REECB1: Generic Renewable Electrical Control Model | [5 empty] | Generador: | Fecha: | Feb 2019
Electrical Control Model for Large Scale PV
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description
J |  |  |  | Vdip (pu), low voltage threshold to activate reactive current injection logic
J+1 |  |  |  | Vup (pu), Voltage above which reactive current injection logic is activated
J+2 |  |  |  | Trv (s), Voltage filter time constant
J+3 |  |  |  | dbd1 (pu), Voltage error dead band lower threshold (≤0)
J+4 |  |  |  | dbd2 (pu), Voltage error dead band upper threshold (≥0)
J+5 |  |  |  | Kqv (pu), Reactive current injection gain during over and undervoltage conditions
J+6 |  |  |  | Iqh1 (pu), Upper limit on reactive current injection Iqinj
J+7 |  |  |  | Iql1 (pu), Lower limit on reactive current injection Iqinj
J+8 |  |  |  | Vref0 (pu), User defined reference (if 0, model initializes it to initial terminal voltage)
J+9 |  |  |  | Tp (s), Filter time constant for electrical power
J+10 |  |  |  | QMax (pu), limit for reactive power regulator
J+11 |  |  |  | QMin (pu) limit for reactive power regulator
J+12 |  |  |  | VMAX (pu), Max. limit for voltage control
J+13 |  |  |  | VMIN (pu), Min. limit for voltage control
J+14 |  |  |  | Kqp (pu), Reactive power regulator proportional gain
J+15 |  |  |  | Kqi (pu), Reactive power regulator integral gain
J+16 |  |  |  | Kvp (pu), Voltage regulator proportional gain
J+17 |  |  |  | Kvi (pu), Voltage regulator integral gain
J+18 |  |  |  | Tiq (s), Time constant on delay s4
J+19 |  |  |  | dPmax (pu/s) (>0) Power reference max. ramp rate
J+20 |  |  |  | dPmin (pu/s) (<0) Power reference min. ramp rate
J+21 |  |  |  | PMAX (pu), Max. power limit
J+22 |  |  |  | PMIN (pu), Min. power limit
J+23 |  |  |  | Imax (pu), Maximum limit on total converter current
J+24 |  |  |  | Tpord (s), Power filter time constant
ICONs | # |  | Value | Description
M |  |  |  | Bus number for voltage control; local control if 0
M + 1 |  |  |  | PFFLAG (Power factor control flag): • 1 if power factor control • 0 if Q control (which can be controlled by an external signal)
M + 2 |  |  |  | VFLAG: • 1 if Q control • 0 if voltage control
M +3 |  |  |  | QFLAG: • 1 if voltage or Q control • 0 if constant pf or Q control
M +4 |  |  |  | PQFLAG, P/Q priority flag for current limit: • 0 for Q priority • 1 for P priority
| STATEs |  | # | Description
| K |  |  | Voltage Measurement filter
| K+1 |  |  | Real power filter
| K +2 |  |  | PI controller for reactive power
| K+3 |  |  | PI controller for voltage error
| K +4 |  |  | First Order lag for reactive current
| K+5 |  |  | First order lag for Pord
| VARs |  | # | Description
| L |  |  | Bus reference voltage (Vref0)
| L+1 |  |  | Power factor reference angle (pfaref), radians
| L+2 |  |  | Real current command (Ipcmd)
| L+3 |  |  | Reactive current command (Iqcmd)
Notes:
1. pfaref (the power factor angle reference) value is initialized by the model based on ini- tial real and
reactive power outputs from the machine.
2. Qref is initialized by the model to a constant or can be connected to an external plant controller
model).
3. Pref is initialized by the model to a constant or can be connected to an external plant controller
model).
4. ICON(M) contains the remote bus number. If this is 0 or if the remote bus number is not specified
then the local bus is used for control.
5. In using REECB1 to model large scale PV, the other models to be used along with this model are
REGCA1 and REPCA1 (optional)
IBUS, 'REECB1', ID, ICON(M) to ICON(M+4), CON(J) to CON(J+24) /
Diagrama de Bloques