## REECCU1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
REECCU1: Descripción | [5 empty] | Generador: |  |  |  | Fecha: | Noviembre 2025
Library Model
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description |  |  | STATEs | # | Description
J |  |  |  | Vdip (pu), low voltage threshold to activate reactive current injection logic |  |  | K |  | Voltage Measurement filter
J+1 |  |  |  | Vup (pu), Voltage above which reactive current injection logic is activated |  |  | K+1 |  | Real power filter
J+2 |  |  |  | Trv (s), Voltage filter time constant |  |  | K+2 |  | PI controller for reactive power
J+3 |  |  |  | dbd1 (pu), Voltage error dead band lower threshold (≤0) |  |  | K+3 |  | PI controller for voltage error
J+4 |  |  |  | dbd2 (pu), Voltage error dead band upper threshold (≥0) |  |  | K+4 |  | First Order lag for reactive current
J+5 |  |  |  | Kqv (pu), Reactive current injection gain during over and undervoltage conditions |  |  | K+5 |  | First order lag for Pord
J+6 |  |  |  | Iqh1 (pu), Upper limit on reactive current injection Iqinj |  |  | K+6 |  | Energy output from battery
J+7 |  |  |  | Iql1 (pu), Lower limit on reactive current injection Iqinj
J+8 |  |  |  | Vref0 (pu), User defined reference (if 0, model initializes it to initialterminal voltage)
J+9 |  |  |  | Tp (s), Filter time constant for electrical power
J+10 |  |  |  | QMax (pu), limit for reactive power regulator
J+11 |  |  |  | QMin (pu) limit for reactive power regulator |  |  | VARs | # | Description
J+12 |  |  |  | VMAX (pu), Max. limit for voltage control |  |  | L |  | Bus reference voltage (Vref0)
J+13 |  |  |  | VMIN (pu), Min. limit for voltage control |  |  | L+1 |  | Power factor reference angle (pfaref), radians
J+14 |  |  |  | Kqp (pu), Reactive power regulator proportional gain |  |  | L+2 |  | Real current command (Ipcmd)
J+15 |  |  |  | Kqi (pu), Reactive power regulator integral gain |  |  | L+3 |  | Reactive current command (Iqcmd)
J+16 |  |  |  | Kvp (pu), Voltage regulator proportional gain |  |  | L+4 |  | Battery Residual Energy
J+17 |  |  |  | Kvi (pu), Voltage regulator integral gain |  |  | L+5 |  | Auxiliary input signal, Paux
J+18 |  |  |  | Tiq (s), Time constant on delay s4
J+19 |  |  |  | dPmax (pu/s) (>0) Power reference max. ramp rate
J+20 |  |  |  | dPmin (pu/s) (<0) Power reference min. ramp rate
J+21 |  |  |  | PMAX (pu), Max. power limit
J+22 |  |  |  | PMIN (pu), Min. power limit
J+23 |  |  |  | Imax (pu), Maximum limit on total converter current
J+24 |  |  |  | Tpord (s), Power filter time constant
J+25 |  |  |  | Vq1 (pu), Reactive Power V-I pair, voltage
J+26 |  |  |  | Iq1 (pu), Reactive Power V-I pair, current
J+27 |  |  |  | Vq2 (pu) (Vq2>Vq1), Reactive Power V-I pair, voltage
J+28 |  |  |  | Iq2 (pu) (Iq2>Iq1), Reactive Power V-I pair, current
J+29 |  |  |  | Vq3 (pu) (Vq3>Vq2), Reactive Power V-I pair, voltage
J+30 |  |  |  | Iq3 (pu) (Iq3>Iq2), Reactive Power V-I pair, current
J+31 |  |  |  | Vq4 (pu) (Vq4>Vq3), Reactive Power V-I pair, voltage
J+32 |  |  |  | Iq4 (pu) (Iq4>Iq3), Reactive Power V-I pair, current
J+33 |  |  |  | Vp1 (pu), Real Power V-I pair, voltage
J+34 |  |  |  | Ip1 (pu), Real Power V-I pair, current
J+35 |  |  |  | Vp2 (pu) (Vp2>Vp1), Real Power V-I pair, voltage
J+36 |  |  |  | Ip2 (pu) (Ip2>Ip1), Real Power V-I pair, current
J+37 |  |  |  | Vp3 (pu) (Vp3>Vp2), Real Power V-I pair, voltage
J+38 |  |  |  | Ip3 (pu) (Ip3>Ip2), Real Power V-I pair, current
J+39 |  |  |  | Vp4 (pu) (Vp4>Vp3), Real Power V-I pair, voltage
J+40 |  |  |  | Ip4 (pu) (Ip4>Ip3), Real Power V-I pair, current
J+41 |  |  |  | T, battery discharge time (s) (>0)
J+42 |  |  |  | SOCini (pu), Initial state of charge
J+43 |  |  |  | SOCmax (pu), Maximum allowable state of charge
J+44 |  |  |  | SOCmin (pu), Minimum allowable state of charge
ICONs | # |  | Value | Description
M |  |  |  | Bus number for voltage control; local control if 0
M + 1 |  |  |  | PFFLAG (Power factor control flag): 1 if power factor control, 0 if Q control (which can be controlled by an external signal)
M + 2 |  |  |  | VFLAG: 1 if Q control, 0 if voltage control
M +3 |  |  |  | QFLAG: 1 if voltage or Q control, 0 if constant pf or Q control
M +4 |  |  |  | PQFLAG, P/Q priority flag for current limit: 0 for Q priority, 1 for P priority
IBUS, ’USRMDL’, ID, 'REECCU1', 102, 0, 5, 45, 7, 6, ICON(M) to ICON(M+4), CON(J) to CON(J+44) /
Notes:
1. pfaref (the power factor angle reference) value is initialized by the model based on ini- tial real and
reactive power outputs from the machine.
2. Qref is initialized by the model to a constant or can be connected to an external plant controller model).
3. Pref is initialized by the model to a constant or can be connected to an external plant controller model).
4. ICON(M) contains the remote bus number. If this is 0 or if the remote bus number is not specified then
the local bus is used for control.
5. SOCini represents the initial state of charge on the battery and is a user entered value. This is entered in
pu; with 1 pu meaning that the batter is fully charged and 0 means the battery is completely discharged.
6. SOCmax is the maximum allowable state of charge. By definition the maximum value would be 1 pu;
however it may be set to a smaller value (e.g., 0.8 pu) to represent spe- cific manu-facturer requirements
that the battery will remain at or below a certain charging level (e.g., 80 %).
7. SOCmax is the minimum allowable state of charge. By definition the minimum value would be 0 pu;
however it may be set to a larger value (e.g., 0.2 pu) to represent spe- cific manufac-turer requirements
that the battery will remain at or above a certain charging level (e.g., 20 %).
8. Other models to be used with REECC1 are, REGCA1, and REPCA1
9. An auxiliary signal model can be attached to the signal represented as Paux. This can be used for interfacing
with supplemental models like power oscillation damping control.
Diagrama de Bloques