## REECDU1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
REECDU1: Generic Renewable Electrical Control Model | [5 empty] | Generador: |  |  |  | Fecha: | Noviembre 2025
Library Model
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description |  |  | STATEs | # | Description
J |  |  |  | Vdip (pu), low voltage threshold to activate reactive current injection logic |  |  | K |  | Voltage Measurement filter
J+1 |  |  |  | Vup (pu), Voltage above which reactive current injection logic is activated |  |  | K+1 |  | Real power filter
J+2 |  |  |  | Trv (s), Voltage filter time constant |  |  | K+2 |  | PI controller for reactive power
J+3 |  |  |  | dbd1 (pu), Voltage error dead band lower threshold (≤0) |  |  | K+3 |  | PI controller for voltage error
J+4 |  |  |  | dbd2 (pu), Voltage error dead band upper threshold (≥0) |  |  | K+4 |  | First Order lag for reactive current
J+5 |  |  |  | Kqv (pu), Reactive current injection gain during over and undervoltage conditions |  |  | K+5 |  | First order lag for Pord
J+6 |  |  |  | Iqh1 (pu), Upper limit on reactive current injection Iqinj |  |  | K+6 |  | First Order filter in droop compensation path
J+7 |  |  |  | Iql1 (pu), Lower limit on reactive current injection Iqinj
J+8 |  |  |  | Vref0 (pu), User defined reference (if 0, model initializes it to initial terminal voltage)
J+9 |  |  |  | Iqfrz (pu), Value at which Iqcmdbl (value of Iqcmd before limit) is held (frozen) for Thld seconds after a voltage dip is over
J+10 |  |  |  | Thld (s), Time for which Iqcmdbl is frozen after the voltage dip is over
J+11 |  |  |  | Thld2 (s) (≥0), Time for which Ipcmd and Ipmax are frozen after the voltage dip is over |  |  | VARs | # | Description
J+12 |  |  |  | Tp (s), Filter time constant for electrical power |  |  | L |  | Bus reference voltage (Vref0)
J+13 |  |  |  | QMax (pu), Maximum value of the signal Qext or Vext |  |  | L+1 |  | Voltage deadband output
J+14 |  |  |  | QMin (pu) Minimum value of the signal Qext or Vext |  |  | L+2 |  | Power factor reference angle (pfaref), radians
J+15 |  |  |  | VMAX (pu), Maximum limit for voltage control |  |  | L+3 |  | Vbias as calculated by the model
J+16 |  |  |  | VMIN (pu), Minimum limit for voltage control |  |  | L+4 |  | Timer for Thld counter
J+17 |  |  |  | Kqp (pu), Reactive power regulator proportional gain |  |  | L+5 |  | Previous value of power reference
J+18 |  |  |  | Kqi (pu), Reactive power regulator integral gain |  |  | L+6 |  | Input to create step change in Paux
J+19 |  |  |  | Kvp (pu), Voltage regulator proportional gain |  |  | L+7 |  | Timer for Thld2 counter
J+20 |  |  |  | Kvi (pu), Voltage regulator integral gain |  |  | L+8 |  | Storage for voltage_dip flag
J+21 |  |  |  | Vbias (pu), User-defined bias (normally 0) |  |  | L+9 |  | Ipmax
J+22 |  |  |  | Tiq (s), Time constant on delay for block s4 |  |  | L+10 |  | Ipmin
J+23 |  |  |  | dPmax (pu/s) (>0) Power reference maximum ramp rate |  |  | L+11 |  | Iqmax
J+24 |  |  |  | dPmin (pu/s) (<0) Power reference minimum ramp rate |  |  | L+12 |  | Iqmin
J+25 |  |  |  | PMAX (pu), Maximum power limit |  |  | L+13 |  | Ipcmd
J+26 |  |  |  | PMIN (pu), Minimum power limit |  |  | L+14 |  | Iqcmd
J+27 |  |  |  | Imax (pu), Maximum limit on total converter current |  |  | L+15 |  | Input to create step change in Pref
J+28 |  |  |  | Tpord (s), Power filter time constant |  |  | L+16 |  | Input to create step change in Qref
J+29 |  |  |  | Vq1 (pu), VDL table vq-iq pair (voltage) |  |  | L+17 |  | Timer for Tblk
J+30 |  |  |  | Iq1 (pu), VDL table vq-iq pair (current) |  |  | L+18 |  | Ipcmdbl (Ipcmd value before limit)
J+31 |  |  |  | Vq2 (pu), VDL table vq-iq pair (voltage) |  |  | L+19 |  | Iqcmdbl (Iqcmd value before limit)
J+32 |  |  |  | Iq2 (pu), VDL table vq-iq pair (current)
J+33 |  |  |  | Vq3 (pu), VDL table vq-iq pair (voltage)
J+34 |  |  |  | Iq3 (pu), VDL table vq-iq pair (current)
J+35 |  |  |  | Vq4 (pu), VDL table vq-iq pair (voltage)
J+36 |  |  |  | Iq4 (pu), VDL table vq-iq pair (current)
J+37 |  |  |  | Vq5 (pu), VDL table vq-iq pair (voltage)
J+38 |  |  |  | Iq5 (pu), VDL table vq-iq pair (current)
J+39 |  |  |  | Vq6 (pu), VDL table vq-iq pair (voltage)
J+40 |  |  |  | Iq6 (pu), VDL table vq-iq pair (current)
J+41 |  |  |  | Vq7 (pu), VDL table vq-iq pair (voltage)
J+42 |  |  |  | Iq7 (pu), VDL table vq-iq pair (current)
J+43 |  |  |  | Vq8 (pu), VDL table vq-iq pair (voltage)
J+44 |  |  |  | Iq8 (pu), VDL table vq-iq pair (current)
J+45 |  |  |  | Vq9 (pu), VDL table vq-iq pair (voltage)
J+46 |  |  |  | Iq9 (pu), VDL table vq-iq pair (current)
J+47 |  |  |  | Vq10 (pu), VDL table vq-iq pair (voltage)
J+48 |  |  |  | Iq10 (pu), VDL table vq-iq pair (current)
J+49 |  |  |  | Vp1 (pu), VDL table vp-ip pair (voltage)
J+50 |  |  |  | Ip1 (pu), VDL table vp-ip pair (current)
J+51 |  |  |  | Vp2 (pu), VDL table vp-ip pair (voltage)
J+52 |  |  |  | Ip2 (pu), VDL table vp-ip pair (current)
J+53 |  |  |  | Vp3 (pu), VDL table vp-ip pair (voltage)
J+54 |  |  |  | Ip3 (pu), VDL table vp-ip pair (current)
J+55 |  |  |  | Vp4 (pu), VDL table vp-ip pair (voltage)
J+56 |  |  |  | Ip4 (pu), VDL table vp-ip pair (current)
J+57 |  |  |  | Vp5 (pu), VDL table vp-ip pair (voltage)
J+58 |  |  |  | Ip5 (pu), VDL table vp-ip pair (current)
J+59 |  |  |  | Vp6 (pu), VDL table vp-ip pair (voltage)
J+60 |  |  |  | Ip6 (pu), VDL table vp-ip pair (current)
J+61 |  |  |  | Vp7 (pu), VDL table vp-ip pair (voltage)
J+62 |  |  |  | Ip7 (pu), VDL table vp-ip pair (current)
J+63 |  |  |  | Vp8 (pu), VDL table vp-ip pair (voltage)
J+64 |  |  |  | Ip8 (pu), VDL table vp-ip pair (current)
J+65 |  |  |  | Vp9 (pu), VDL table vp-ip pair (voltage)
J+66 |  |  |  | Ip9 (pu), VDL table vp-ip pair (current)
J+67 |  |  |  | Vp10 (pu), VDL table vp-ip pair (voltage)
J+68 |  |  |  | Ip10 (pu), VDL table vp-ip pair (current)
J+69 |  |  |  | rc (pu), Current compensation resistance
J+70 |  |  |  | Xc (pu), Current compensation reactance
J+71 |  |  |  | Tr1 (s), Time constant for reactive current compensation
J+72 |  |  |  | Kc, Reactive current compensation gain
J+73 |  |  |  | Ke, Scaling on Ipmin, (0 for generator, 0 < Ke ≤ 1 for storage)
J+74 |  |  |  | Vblkl (pu), Voltage below which converter will block
J+75 |  |  |  | Vblkh (pu), Voltage above which converter will block
J+76 |  |  |  | Tblk (s), time for which converter will remain blocked after voltage is within the range Vblkl < Vt_filt < Vblkh
ICONs | # |  | Value | Description
M |  |  |  | PFFLAG: 1 if power factor control, 0 if Q control (which can be controlled by an external signal)
M + 1 |  |  |  | VFLAG: 1 if Q control, 0 if voltage control
M + 2 |  |  |  | QFLAG: 1 if voltage or Q control, 0 if constant pf or Q control
M +3 |  |  |  | PFLAG: 1 if active current command has speed dependency, 0 for no dependency
M +4 |  |  |  | PQFLAG, P/Q priority flag for current limit: 0 for Q priority, 1 for P priority
M +5 |  |  |  | VcmpFlag: 1 for current compensation, 0 for reactive droop dompensation
IBUS 'USRMDL' ID 'REECDU1' 102 0 6 77 7 20 ICON(M) to ICON(M+5) CON(J) to CON(J+76) /
Note(s):
Details of this model are given in ‘Memo_RES_Modeling_Updates.pdf' which can be obtained from WECC
website (www.wecc.org).
1. Model Parameters are specified in per unit of machine MVA base.
2. When the voltage Vtfilt is either less than Vdip or greater than Vup, the voltage_dip falg in the model is
set to 1, else it is set to 0. In order to disable voltage dip check logic, set the CONs corresponding to Vdip
and Vup to (say) -1.0 and 99.0 respectively. The voltage_dip flag is used in the model to freeze states
and set the values of Iqcmd and Ipcmd.
3. The term VDL referenced in the CONs table above stands for Voltage-Dependent Limit. The VDL points
represent the voltage-dependent limits on the inverter current. There are 10 pairs of VDLq points (shown
as Vq-Iq pairs) to represent the reactive current limits followed by 10 pairs of VDLp points (shown as Vp-
Ip pairs) to represent the active current limits.
To ignore the VDLp set of points, set all the VDLp data points to zero. Similarly, to ignore the VDLq table,
set all the VDLq data points to zero.
The Vp data points (if specified) should be monotonically increasing (i.e., Vp1<Vp2<Vp3… <Vp10). The
first Vp point can be zero. After this, the first Vp value of zero or if a Vp value is such that it is not
monotonically increasing signifies the end of Vp-Ip curve. Note that Ip values must be greater than or
equal to zero.
The Vq data points (if specified) should be monotonically increasing (i.e., Vp1<Vp2<Vp3… <Vp10). The
first Vq point can be zero. After this, the first Vq value of zero or if a Vq value is such that it is not
monotonically increasing signifies the end of Vq-Iq curve. Note that Iq values can be negative signifying
that both Iqmax and Iqmin are negative (which is used to force inductive current for very high voltage
situations).
4. Imax is used to calculate Ipmax and Iqmax as described below:
If Pqflag is 0 (Q-priority):
Iqmax = min (VDLq, Imax)
If (Iqmax < 0)
Iqmin = Iqmax
else
Iqmin = -Iqmax
end
Ipmax =
Ipmin = - Ke × Ipmax
If Pqflag is 1 (P-priority):
Ipmax = min (VDLp, Imax)
Ipmin = - Ke × Ipmax
Iqmax =
If (Iqmax < 0)
Iqmin = Iqmax
else
Iqmin = -Iqmax
end
Note that if Iqmax is negative, then Iqmin must be equal to Iqmax to force Iqcmd to this limit. This is
used in some cases during extreme high voltage situations to make the inverter absorb reactive power.
5. The explanation for Ke is as follows:
• If Ke = 0, the model mimics a generator, i.e., Ipmin = 0. This means the unit cannot absorb active
power.
• If 0 < Ke ≤ 1, the model mimics a storage device that is capable of also absorbing active current
(charging mode). A value of Ke < 1 implies that the device has a lower capacity for absorbing real
power as compared to its capacity for generating real power.
• Ke cannot be negative or greater than 1
• In case Iqmax is negative, then Iqmin must also be negative and the same value to force Iqcmd to this
limit. Per the WECC REMTF memo (referenced above), this is used in some cases during extreme high
voltages to make the inverter absorb reactive power.
6. Vref0 can be specified as an input parameter.
If initial Vref0 is specified as being ≤ 0.0, model will set this to be equal to the initial terminal voltage Vt.
PSS®E 34.9.5
All material contained in this documentation is proprietary to Siemens Industry Inc., Siemens Power Technologies International
704
Generic Renewable Electrical Control
Models
REECDU1
If Vref0 is specified to be greater than zero, and if Kqv is greater than zero, then upon initialization model
will check if dbd1 < Vref0 – Vt < dbd2. If this condition is not met, the model will set the initial Vref0 to
be equal to Vt to force the Vref0 – Vt to be within the deadbands dbd1 and dbd2.
7. Local current-compensation is simulated using the block . and are the complex
generator terminal voltage and current to which this electrical control model is connected. rc and
xc can both be set to zero to eliminate the modeling of current compensation. Note that rc and xc are
specified in per unit of machine MVA base.
8. Local reactive-droop compensation simulated using the block Vt + Kc×Qelec. Vt is the magnitude of the
machine terminal voltage and Qelec is the generator reactive power. Kc can be set to zero to eliminate
the modeling of reactive-droop compensation.
9. The reactive-current injection arm (whose output is Iqinj) is always active if Kqv is greater than zero. To
completely disable this arm, Kqv can be set to zero and Vdip and Vup can be set to (say) -99 and 99 to
completely turn-off the voltage dip logic.
10. Thld is the time for which Iqcmdbl (value of Iqcmd before limit) is held at its current value (value just
prior to the end of the voltage_dip, i.e., before voltage_dip goes from 1 to 0).
If Thld < 0, then following a voltage dip, Iqcmdbl is held equal to Iqfrz for Thld seconds and is then
released.
Thld can be less than, equal to or greater than zero.
11. Thld2 is the time for which Ipcmd and Ipmax are frozen at the value that existed just prior to the end of
the voltage_dip, i.e., before voltage_dip goes from 1 to 0).
Thld2 must be greater than or equal to zero.
12. Per details as specified in the WECC REMTF memo, the non-windup proportional-integrators corresponding
to STATE(K+2) and STATE(K+3) (shown as s2 and s3 respectively in the block diagram) are linked
as follows: if s3 hits its maximum limit and its derivative (ds3) is positive, then ds3 is set to 0, and furthermore
if the derivative of s2 (i.e., ds2) is also positive, then ds2 is also set to 0 to prevent windup.
However, if ds2 is negative, then ds2 is not set to 0. A similar rule is applied for s3 hitting its lower limit,
but the check is whether ds3 and ds2 are negative.
For the freezing of the states s2, s3, s4 and s5, only the states are frozen, thus in the case of s2 and s3
the proportional gain, if non-zero, still acts during the voltage dip. Finally, for s5, if Tpord is zero then the
time constant and freezing of the state are by-passed, however, the Pmax/Pmin limits are still applied.
13. VAR(L+15) and VAR(L+16) are been provided to allow users to perform step change in Pref & Qref commands.
These are set to zero at model initialization.
14. Although it is possible to model the momentary cessation and the recovery delay by proper parametrization
of the VDL data along with the Thld and Thld2 data, this may not be entirely desirable since
the VDL table parameters are more typically used for modeling the voltage dependence of the inverter
current limits.
To model momentary cessation (inverter blocking), the parameters Vblkl, Vblkh and Tblk are used.
If the filtered voltage (Vtfilt) becomes less than Vblkl or becomes greater than Vblkh, then Iqmax, Iqmin,
Ipmax, and Ipmin are all set to zero thus forcing the Iqcmd and Ipcmd to zero (to emulate inverter
blocking). Once the inverter comes out of blocking mode (i.e., when voltage becomes such that Vblkl
< Vtfilt < Vblkh), the current limits are released only after a delay of Tblk seconds (i.e., Ipmax, Iqmax,
Ipmin and Iqmin are kept at zero for Tblk seconds before they are released).
Diagrama de Bloques