## REGCA1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
REGCA1: Generic Renewable Generator/Converter Model | [5 empty] | Generador: | Fecha: | Feb 2019
Renewable Energy Generator/Converter Model
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description
J |  |  |  | Tg, Converter time constant (s)
J+1 |  |  |  | Rrpwr, Low Voltage Power Logic (LVPL) ramp rate limit (pu/s)
J+2 |  |  |  | Brkpt, LVPL characteristic voltage 2 (pu)
J+3 |  |  |  | Zerox, LVPL characteristic voltage 1 (pu)
J+4 |  |  |  | Lvpl1, LVPL gain (pu)
J+5 |  |  |  | Volim, Voltage limit (pu) for high voltage reactive current management
J+6 |  |  |  | Lvpnt1, High voltage point for low voltage active current management (pu)
J+7 |  |  |  | Lvpnt0, Low voltage point for low voltage active current management (pu)
J+8 |  |  |  | Iolim, Current limit (pu) for high voltage reactive current management (specified as a (-) value)
J+9 |  |  |  | Tfltr, Voltage filter time constant for low voltage active current management (s)
J+10 |  |  |  | Khv, Overvoltage compensation gain used in the high voltage reactive current management
J+11 |  |  |  | Iqrmax, Upper limit on rate of change for reactive current (pu/s)
J+12 |  |  |  | Iqrmin, Lower limit on rate of change for reactive current (pu/s)
J+13 |  |  |  | Accel, acceleration factor (0 < Accel <= 1)
ICONs | # |  | Value | Description
M |  |  |  | Lvplsw (Low Voltage Power Logic) switch (0: LVPL not present, 1:LVPL present)
STATEs | # |  | Description
K |  |  | Converter lag for Ipcmd
K+1 |  |  | Converter lag for Iqcmd
K+2 |  |  | Voltage filter for low voltage active current management
VARs | # |  | Description
L |  |  | Previous terminal voltage
L+1 |  |  | Previous terminal voltage angle
L+2 |  |  | Reactive current overvoltage correction
L+3 |  |  | Initial machine reactive power from power flow
IBUS, 'REGCA1', ID, ICON(M), CON(J) to CON(J+13) /
Notes:
1. This model can be used with Type 3 and 4 wind machines. When used for modeling of Type 3 wind
machine, the other models to be used along with this model are reeca1, repca1 (optional), wtdta1,
wtpta1, wtara1, and wttqa1. When used for modeling of Type 4 machines, the other models to be
used along with this model are reeca1, wtdta1, and repca1 (optional).
Diagrama de Bloques