## REPCA1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
REPCA1: Generic Renewable Plant Control Model | [5 empty] | Generador: | Fecha: | Feb 2019
Generic Renewable Plant Control Model
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description
J |  |  |  | Tfltr, Voltage or reactive power measurement filter time constant (s)
J+1 |  |  |  | Kp, Reactive power PI control proportional gain (pu)
J+2 |  |  |  | Ki, Reactive power PI control integral gain (pu)
J+3 |  |  |  | Tft, Lead time constant (s)
J+4 |  |  |  | Tfv, Lag time constant (s)
J+5 |  |  |  | Vfrz, Voltage below which State s2 is frozen (pu)
J+6 |  |  |  | Rc, Line drop compensation resistance (pu)
J+7 |  |  |  | Xc, Line drop compensation reactance (pu)
J+8 |  |  |  | Kc, Reactive current compensation gain (pu)
J+9 |  |  |  | emax, upper limit on deadband output (pu)
J+10 |  |  |  | emin, lower limit on deadband output (pu)
J+11 |  |  |  | dbd1, lower threshold for reactive power control deadband (<=0)
J+12 |  |  |  | dbd2, upper threshold for reactive power control deadband (>=0)
J+13 |  |  |  | Qmax, Upper limit on output of V/Q control (pu)
J+14 |  |  |  | Qmin, Lower limit on output of V/Q control (pu)
J+15 |  |  |  | Kpg, Proportional gain for power control (pu)
J+16 |  |  |  | Kig, Proportional gain for power control (pu)
J+17 |  |  |  | Tp, Real power measurement filter time constant (s)
J+18 |  |  |  | fdbd1, Deadband for frequency control, lower threshold (<=0)
J+19 |  |  |  | Fdbd2, Deadband for frequency control, upper threshold (>=0)
J+20 |  |  |  | femax, frequency error upper limit (pu)
J+21 |  |  |  | femin, frequency error lower limit (pu)
J+22 |  |  |  | Pmax, upper limit on power reference (pu)
J+23 |  |  |  | Pmin, lower limit on power reference (pu)
J+24 |  |  |  | Tg, Power Controller lag time constant (s)
J+25 |  |  |  | Ddn, droop for over-frequency conditions (pu)
J+26 |  |  |  | Dup, droop for under-frequency conditions (pu)
ICONs | # |  | Value | Description
M |  |  |  | Bus number for voltage control; local control if 0
M +1 |  |  |  | Monitored branch FROM bus number for line drop compensation (if 0 generator power will be used)
M +2 |  |  |  | Monitored branch TO bus number for line drop compensation (if 0 generator power will be used)
M +3 |  |  |  | Branch circuit id for line drop compensation (enter in single quotes) (if 0 generator power will be used)
M +4 |  |  |  | VC Flag (droop flag): • 0: with droop if power factor control • 1: with line drop compensation
M +5 |  |  |  | RefFlag (flag for V or Q control): • 0: Q control • 1: voltage control
M +6 |  |  |  | Fflag (flag to disable frequency control): • 1: enable control • 0: disable
STATEs | # |  | Description
K |  |  | Voltage Measurement filter
K+1 |  |  | Reactive power control filter
K+2 |  |  | PI controller for reactive power
K+3 |  |  | Lead-lag in reactive power path
K+4 |  |  | Real power filter
K+5 |  |  | PI controller for real power
K+6 |  |  | Power controller first order lag
VARs | # |  | Description
L |  |  | Reference for voltage control (Vref)
L+1 |  |  | Reactive power reference (Qref)
L+2 |  |  | Frequency reference (Freq_ref)
L+3 |  |  | Active Power reference (Plant_pref)
L+4 |  |  | Line flow P MW
L+5 |  |  | Line flow Q MVAr
L+6 |  |  | Line flow MVA
L+7 |  |  | Q/V Deadband output
L+8 |  |  | Frequency deadband output
IBUS, 'REPCA1', ID, ICON(M) to ICON(M+6), CON(J) to CON(J+26) /
Notes:
1. This model can be used with Type 3 and 4 wind machines. When used for modeling of Type 3 wind
machine, the model name is REPCTA1, and the other models to be used along with this model are
regca1, reeca1, wtdta1, wtpta1, wtara1, wttqa1. When used for modeling of Type 4 machines, the
model name is REPCA1, and the other models to be used along with this model are regca1, reeca1,
wtdta1.
2. When used with Type 3 wind machine, the output (Pref) of the REPCTA1 model goes as an input Pref
0 into the Torque control model (wttqa1). When used with Type 4 wind ma-chine, the output (Pref)
of the REPCA1 model goes as an input into the electrical control model (reeca1).
3. If ICON(M+1) is zero, then the generator active and reactive powers are used for line-drop compensation
calculation.
Diagrama de Bloques