## REPCTA1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
REPCTA1: Generic Renewable Plant Control Model | [5 empty] | Generador: |  |  |  | Fecha: | Noviembre 2025
Library model
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description |  |  | STATEs | # | Description
J |  |  |  | Tfltr, Voltage or reactive power measurement filter time constant (s) |  |  | K |  | Voltage Measurement filter
J+1 |  |  |  | Kp, Reactive power PI control proportional gain (pu) |  |  | K+1 |  | Reactive power control filter
J+2 |  |  |  | Ki, Reactive power PI control integral gain (pu) |  |  | K+2 |  | PI controller for reactive power
J+3 |  |  |  | Tft, Lead time constant (s) |  |  | K+3 |  | Lead-lag in reactive power path
J+4 |  |  |  | Tfv, Lag time constant (s) |  |  | K+4 |  | Real power filter
J+5 |  |  |  | Vfrz, Voltage below which State s2 is frozen (pu) |  |  | K+5 |  | PI controller for real power
J+6 |  |  |  | Rc, Line drop compensation resistance (pu) |  |  | K+6 |  | Power controller first order lag
J+7 |  |  |  | Xc, Line drop compensation reactance (pu)
J+8 |  |  |  | Kc, Reactive current compensation gain (pu)
J+9 |  |  |  | emax, upper limit on deadband output (pu)
J+10 |  |  |  | emin, lower limit on deadband output (pu)
J+11 |  |  |  | dbd1, lower threshold for reactive power control deadband (<=0) |  |  | VARs | # | Description
J+12 |  |  |  | dbd2, upper threshold for reactive power control deadband (>=0) |  |  | L |  | Reference for voltage control (Vref)
J+13 |  |  |  | Qmax, Upper limit on output of V/Q control (pu) |  |  | L+1 |  | Reactive power reference (Qref)
J+14 |  |  |  | Qmin, Lower limit on output of V/Q control (pu) |  |  | L+2 |  | Frequency reference (Freq_ref)
J+15 |  |  |  | Kpg, Proportional gain for power control (pu) |  |  | L+3 |  | Active Power reference (Plant_pref)
J+16 |  |  |  | Kig, Integral gain for power control (pu) |  |  | L+4 |  | Line flow P MW
J+17 |  |  |  | Tp, Real power measurement filter time constant (s) |  |  | L+5 |  | Line flow Q MVAr
J+18 |  |  |  | fdbd1, Deadband for frequency control, lower threshold (specified as per unit frequency deviation) (<=0) |  |  | L+6 |  | Line flow MVA
J+19 |  |  |  | fdbd2, Deadband for frequency control, upper threshold (specified as per unit frequency deviation) (>=0) |  |  | L+7 |  | Q/V Deadband output
J+20 |  |  |  | femax, frequency error upper limit (pu) |  |  | L+8 |  | Frequency deadband output
J+21 |  |  |  | femin, frequency error lower limit (pu)
J+22 |  |  |  | Pmax, upper limit on power reference (pu)
J+23 |  |  |  | Pmin, lower limit on power reference (pu)
J+24 |  |  |  | Tg, Power Controller lag time constant (s)
J+25 |  |  |  | Ddn, reciprocal of droop for over-frequency conditions (pu)
J+26 |  |  |  | Dup, reciprocal of droop for under-frequency conditions (pu)
ICONs | # |  | Value | Description
M |  |  |  | Bus number for voltage control; local control if 0
M + 1 |  |  |  | Monitored branch FROM bus number for line drop compensation (if 0 generator power will be used)
M + 2 |  |  |  | Monitored branch TO bus number for line drop compensation (if 0 generator power will be used)
M +3 |  |  |  | Branch circuit id for line drop compensation (enter in single quotes) (if 0 generator power will be used)
M +4 |  |  |  | VC Flag (droop flag): 0: with droop if power factor control, 1: with line drop compensation
M +5 |  |  |  | RefFlag (flag for V or Q control): 0: Q control, 1: voltage control
M +6 |  |  |  | Fflag (flag to disable frequency control): 1: enable control, 0: disable
DYR record when used with Type 4 machines: IBUS, 'REPCA1', ID, ICON(M) to ICON(M+6), CON(J) to CON(J+26) /
DYR record when used with Type 3 machines: IBUS, 'REPCTA1', ID, ICON(M) to ICON(M+6), CON(J) to CON(J+26) /
Diagrama de Bloques