## STGV1P
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
STGV1P: Turbine-Governor Model Data Sheets | [5 empty] | Generador: |  |  |  | Fecha: | Julio 2011
Modelo escrito por el Usuario
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
CONs | # |  | Value | Description
J |  |  |  | KREG (p.u.) Power Regulator Droop
J+1 |  |  |  | TREG (sec) Power Regulator time constant
J+2 |  |  |  | DPMAX (p.u.) Power Regulator High Limit
J+3 |  |  |  | DPMIN < 0 (p.u.) Power Regulator Low Limit
J+4 |  |  |  | PDEAD (p.u.) Electric Power Dead Band
J+5 |  |  |  | TF (sec) Electric Power Filter time constant
J+6 |  |  |  | KP (p.u.) Power Controller Gain
J+7 |  |  |  | Ti > 0 (sec) Power Controller time constant
J+8 |  |  |  | KDROOP, 1/p.u. Regulation
J+9 |  |  |  | U0 (p.u. per sec) Opening valve rate limit
J+10 |  |  |  | UC < 0 (p.u. per sec) Closing valve rate limit
J+11 |  |  |  | TG > 0 (sec) HP valve servomotor time constant
J+12 |  |  |  | GMAX (p.u.) Maximum valve position
J+13 |  |  |  | GMIN (p.u.) Minimum valve position
J+14 |  |  |  | TSCH (sec) Stream chest delay
J+15 |  |  |  | TRH (sec) Reheater delay
J+16 |  |  |  | TIP (sec) Delay due to IP turbine section
J+17 |  |  |  | TLP (sec) Delay due to LP turbine section
J+18 |  |  |  | KHP (p.u.) HP fraction
J+19 |  |  |  | KIP (p.u.) IP fraction
J+20 |  |  |  | KLP (p.u.) LP fraction
J+21 |  |  |  | TRATE, Steam Turbine Rating (MW)
STATEs | # |  | Description |  |  |  | VARs | # | Description
K |  |  | Speed deviation filter |  |  |  | L |  | Electric Power reference
K+1 |  |  | Electric power filter
K+2 |  |  | PI power controller |  |  |  | IBUS, ‘USRMDL’, ID, ’STGV1P’, 5, 0, 0, 22, 8, 1,
K+3 |  |  | Valve position |  |  |  | CON(J) to CON(J+21) /
K+4 |  |  | HP turbine dynamics
K+5 |  |  | Reheater dynamics
K+6 |  |  | IP turbine dynamics
K+7 |  |  | LP turbine dynamics
Diagrama de Bloques
STGV1P
SPEED
PMECH
PELEC