## WT4EM_SENV
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
WT4EM_SENV: Electrical model for renewable machine | [8 empty] | Fecha: | Octubre 2021
Modelo definido por el usuario: SENVION 3.6M114 NES
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs |  |  |  |  | L
CONs | # |  | Value | Description
J |  |  |  | Trv - Filter time constant for voltage measurements [s]
J+1 |  |  |  | Tp - Filter time constant for power measurement [s]
J+2 |  |  |  | Vdip - Undervoltage condition trigger voltage [pu]
J+3 |  |  |  | Vup - Overvoltage condition trigger voltage [pu]
J+4 |  |  |  | Qmin - Reactive power limit minimum [pu]
J+5 |  |  |  | Qmax - Reactive power limit maximum [pu]
J+6 |  |  |  | Kqp - Proportional gain Qctrl [pu]
J+7 |  |  |  | Kqi - Integral gain Qctrl [pu]
J+8 |  |  |  | Vmax - Voltage control maximum [pu]
J+9 |  |  |  | Vmin - Voltage control minimum [pu]
J+10 |  |  |  | Kvp - Proportional gain Vctrl [pu]
J+11 |  |  |  | Kvi - Integral gain Vctrl [pu]
J+12 |  |  |  | Tiq - Time constant on lag delay [s] (Tiq>0)
J+13 |  |  |  | db1 - Voltage deadband for overvoltage iq injection [pu]
J+14 |  |  |  | db2 - Voltage deadband for undervoltage iq injection [pu]
J+15 |  |  |  | Kqv - Gain for reactive current injection during fault [pu]
J+16 |  |  |  | Iql1 - Minimum limit of reactive current injection [pu]
J+17 |  |  |  | Iqh1 - Maximum limit of reactive current injection [pu]
J+18 |  |  |  | Thld - Reactive current injection delay after voltage dip [s]
J+19 |  |  |  | dPmax - Ramp rate on power reference [pu/s]
J+20 |  |  |  | dPmin - Ramp rate on power reference [pu/s]
J+21 |  |  |  | Pmax - Maximum power reference [pu]
J+22 |  |  |  | Pmin - Minimum power reference [pu]
J+23 |  |  |  | Tpord - Time constant Pctrl [s]
J+24 |  |  |  | Ipmin_dip - Minimun Ipcmd during voltage dip [pu]
J+25 |  |  |  | Imax - Maximum converter current limit [pu]
J+26 |  |  |  | Vq1 - Reactive Power V-I pair, voltage [pu]
J+27 |  |  |  | Iq1 - Reactive Power V-I pair, current [pu]
J+28 |  |  |  | Vq2 - (Vq2>Vq1), Reactive Power V-I pair, voltage [pu]
J+29 |  |  |  | Iq2 - (Iq2>Iq1), Reactive Power V-I pair, current [pu]
J+30 |  |  |  | Vq3 - (Vq3>Vq2), Reactive Power V-I pair, voltage [pu]
J+31 |  |  |  | Iq3 - (Iq3>Iq2), Reactive Power V-I pair, current [pu]
J+32 |  |  |  | Vq4 - (Vq4>Vq3), Reactive Power V-I pair, voltage [pu]
J+33 |  |  |  | Iq4 - (Iq4>Iq3), Reactive Power V-I pair, current [pu]
J+34 |  |  |  | Vp1 - Real Power V-I pair, voltage [pu]
J+35 |  |  |  | Ip1 - Real Power V-I pair, current [pu]
J+36 |  |  |  | Vp2 - (Vp2>Vp1), Real Power V-I pair, voltage [pu]
J+37 |  |  |  | Ip2 - (Ip2>Ip1), Real Power V-I pair, current [pu]
J+38 |  |  |  | Vp3 - (Vp3>Vp2), Real Power V-I pair, voltage [pu]
J+39 |  |  |  | Ip3 - (Ip3>Ip2), Real Power V-I pair, current [pu]
J+40 |  |  |  | Vp4 - (Vp4>Vp3), Real Power V-I pair, voltage [pu]
J+41 |  |  |  | Ip4 - (Ip4>Ip3), Real Power V-I pair, current [pu]
J+42 |  |  |  | Iq_frz - Value at which injection is held after voltage dip [pu]
J+43 |  |  |  | Tp_rmp - Time ramp recuperation of Pe after Vdip
ICONs | # |  | Value | Description
M |  |  |  | Ctrl - Local or remote (PPC) control (local control if 0)
M+1 |  |  |  | PQflag - P/Q priority flag for current limit (0-Qpriority / 1-Ppriority)
M+2 |  |  |  | Qflag - Reactive Power Flag Ctrl (0-Constant PF or Qctrl / 1-V or Qctrl)
M+3 |  |  |  | Vflag - Voltage Flag Control (0-Vctrl / 1-Qctrl)
M+4 |  |  |  | PFflag - Power Factor Control Flag (1-Qctrl / 0-PFctrl)
M+5 |  |  |  | Pflag - Active Power Flag Ctrl (0-No dependency / 1-SPD dependency)
STATEs | # |  | Description |  |  | VARs | # | Description
K |  |  | PT1 V meas |  |  | L |  | QV inj ref
K+1 |  |  | PT1 P meas |  |  | L+1 |  | Pfref
K+2 |  |  | Piaw of Qctrl |  |  | L+2 |  | Vbias
K+3 |  |  | Piaw of Vctrl |  |  | L+3 |  | Qref
K+4 |  |  | PT1 of Constant Qctrl |  |  | L+4 |  | Pref
K+5 |  |  | PT1aw of Pctrl |  |  | L+5 |  | PickDrop_THLD
K+6 |  |  | CurrLimitLogic_Int1 |  |  | L+6 |  | PickDrop_THLD_Time
K+7 |  |  | CurrLimitLogic_Int2 |  |  | L+7 |  | P_Ratelimiter
K+8 |  |  | IpcmdLimitDuringDip |  |  | L+8 |  | PD_VD_1
K+9 |  |  | IpcmdBeforeDip |  |  | L+9 |  | PD_VD_1_Time
[6 empty] | L+10 |  | PD_VD_2
[6 empty] | L+11 |  | PD_VD_2_Time
[6 empty] | L+12 |  | VD_Flipflop
[6 empty] | L+13 |  | IpcmdFaultFlipFlop
[6 empty] | L+14 |  | IpcmdFaultPickDrop
[6 empty] | L+15 |  | IpcmdFaultPickDropTime
[6 empty] | L+16 |  | IqcmdInjFault
IBUS, 'USRMDL', ID, WT4EM_SENV, 102, 0, 6, 44, 10, 17, ICON(M), CON(J) to CON(J+43)/
Diagrama de Bloques
WT4EM_SENV
WQCMND
WPCMND
WIPCMD
WIQCMD