The main purpose of this report is to present a digital model of the master control functions of a multi HVDC transmission systems. The master control coordinates the operation of several HVDC transmission blocks and also includes regulators common for the whole transmission system.

The dynamic master control model is designed to handle up to 5 parallel blocks of two terminal DC transmission line models.

The report describes the functions of the dynamic models and gives instructions how to set up the master control model and the HVDC Back-to-Back transmission model. The input data and applicable instructions are presented how to solve the load flow, add dynamic HVDC models, to run the dynamic simulation and how to run the system in dynamic simulations. These procedures are arranged for the simulation program PSS/E version 26.2 or later from Power Technologies, Inc.

The load flow model of the dc transmission is built up by the standard components available in PSS/E. The dynamic models are special user models designed to represent the ABB design of an HVDC transmission system. The model MCTRL5 introduces the dynamic functions of the common master control functions for the whole HVDC transmission system. The model CDCAB2 introducing the dynamic behavior to the DC standard unit in PSS/E ‘Two-terminal DC transmission line’. The model POWDEC models the frequency dependency of the active power transmission.

The control functions implemented in the master control model are active power control, reactive power control and multi block damping controller.

- The models, which are treated here, are limited to fundamental frequency ac quantities, describing by phasors, and mean values of dc quantities.

- CONTENT

1. HVDC TRANSMISSION SYSTEM	3

1.1	Introduction	3

1.2	Overview	4

1.3	Basic data of test case	4

2	Load Flow Model in PSS/E program	5

2.1	Description	5

2.2	Load Flow Model	6

3	Dynamic Model	7

3.1	Introduction	7

3.2	User model MCTRL5	7

3.2.1	Functional description	7

3.2.2	Operation	9

3.3	User model CDCAB2	9

3.3.1	Description CDCAB2	9

3.3.2	Operation	9

3.4	User model POWDEC	10

3.4.1	Description	10

3.4.2	Operation	10

4	Operation Instruction of the Test Cases	10

4.1	Introduction	10

4.2	Double block operation	11

4.2.1	Load flow	11

4.2.2	Snap shot and compile	12

4.2.3	Dynamic simulation	13

4.3	Multi block operation	15

4.3.1	Load flow	15

4.3.2	Snap shot and compile	15

4.3.3	Dynamic simulation	15

5	DATA SHEET	17

5.1	Dynamic Model of Master Control MCTRL5.	17

5.2	Dynamic Model CDCAB2, Data Sheet	23

6	References	28

6.1	Files	28

6.2	Reference Reports	28

7	QUICK START PROCEDURE FOR RUNNING ON PC	29

# 1. HVDC TRANSMISSION SYSTEM

## Introduction

The main purpose of this report is to present a maser control model which contains common master functions to coordinate the operation of several two terminal HVDC transmission blocks. The HVDC transmission blocks are operating in parallel transmitting active power between the two ac networks. It is assumed that all the blocks are connected to the same ac bus.

The report also presents instructions how to set up the load flow, solve the load flow, take a snap shot, add dynamic models and finally  how to run the dynamic simulation.

The test cases presented in this report include the basic design data of the Garabi HVDC Interconnection transmission system and all the PSS/E commands necessary to setup the standard load flow elements modeled in the digital simulation program PSS/E from Power Technologies, Inc, U.S. The cases have been tested and verified on the PC computer platform with PSS/E ver. 26.2.

All the control functions of the dynamic models are based on the control logic developed by ABB Power Systems AB for application in their HVDC Transmission systems.

The dynamic behavior of the dc transmission is modeled by introducing the two user models MCTRL5 and CDCAB2. The model POWDEC ican also be added to introduce the frequency dependent power control function.

The dynamic model, MCTRL5, coordinates the power between multi block of HVDC transmission provided with fundamental parameters that describe the system. The dynamic models includes following functions

- Active power control

- Reactive power control

- Damping controller of parallel HVDC transmissions

Additionally, the MCTRL5 model accommodates the following actions by the user,

- Power ramping of the whole transmission

- Power ramping on biblock transmission

- Power ramping on block transmission

- Biblock compensation at power limitation

The dynamic model, CDCAB2, simulates the dynamic behavior of a two terminal HVDC transmission. The model includes the following functions,

- Basic equations of the rectifier converters

- Basic equations of the inverter converter

- Master control of the two terminal transmission

- Converter control

The dynamic model, POWDEC, recognizes the following actions,

- Power order reduction at frequency deviations

## Overview

The ac system model is set up to obtain two test cases where the HVDC dynamic models can be tested in a simple network. The ac systems are represented by infinite sources with short circuit impedances and one ac transmission line added on the power receiving side.

When this basic system has been installed and is running correctly the simple ac networks can be replaced with more detailed networks.

The technical solutions for the converter stations are chosen to present the basic HVDC transmission system. The presented cases are designed as modular HVDC/CCC concept from ABB Power Systems.

The load flow model of the dc transmission is built up by the standard components available in PSS/E from version.26.2. The dynamic models are special user models designed to represent the ABB design of an HVDC transmission system. The model MCTRL5 introduces the dynamic functions of the common master control functions for the whole HVDC transmission system. The model CDCAB2 simulates the two converters and also includes the control functions of each two terminal DC link. The model POWDEC models the frequency dependency of the active power transmission.

General assembly of the power system models and its associated controls are presented in following paragraphs. The technique of bringing a system model to a steady state operation condition, saving its dynamic data into a snapshot file and running the dynamic simulation is also discussed.

The two test cases show a double block system operating with two parallel HVDC blocks while the second case present a multi block transmission system with five parallel HVDC blocks.

## Basic data of test case

The presented test cases are based on the two terminal HVDC back-to-back transmission blocks. Each block consists of two converters, one rectifier and one inverter. The Garabi blocks have a rated transmission power of 550 MW operating between two ac busses in an ac system. One converter is controlling the dc current and the other is in voltage control operating with a constant extinction angle.

Each HVDC transmission block is introduced with following base data

Nominal power			550 MW

Nominal dc voltage		140 kV

Nominal dc current		3930 A

AC Filter			85 MW

Ac line reactors are added in the converter stations to reduce the ac voltages, due to the long ac transmissions lines.

To coordinate and identify the HVDC blocks, each block has been given a unique number. It is assumed that the identity of the block corresponds to the actual identity number used in the Garabi station, i.e. block 1 has the identity 1 and so on.

# Load Flow Model in PSS/E program

## Description

The PSS/E program is composed basically of three packages: Power Flow, Dynamics and Plotting. This paragraph deals with the setup of a load flow model in PSS/E

The system model is built by means of basic standard elements interconnected at ac nodes. This paragraph provides additional instruction on the appropriate representation of a two-terminal DC transmission line in the PSS/E power flow program. Representation in this form is required for successfully result of the load flow calculation and initialization of the dynamics models described in paragraph 3.

The data for building the system is given in the raw data file, flow_btb.raw.

The setup of the HVDC transmission in the PSS/E program has been tested in version 26.2 of the PSS/E program on the PC computer platform.

In Garabi II a new arrangement of the line reactors are introduced. The following scheme is used, where Nr_Block, is the number of active blocks in the HVDC transmission.

The reactive load is controlled in the following way,

At low power transmission

Argentina side					150 MVAr

Brazil side	120 + 85 + 85 		total 	290 MVAr

At high power transmission the switchable reactors are disconnected.

Argentina side					150 MVAr

Brazil side					120 MVAr

Reactive power generation

Each transmission block has one filter bank with the reactve power generation of,

Argentina side			Nr_Block * 85 + 9.15 MVAr

Brazil side			Nr_Block * 85 + 22.1 MVAr

The reactive power 9.15 and 22.1 is added due to the PLC filters.

## Load Flow Model

The basic configuration of one HVDC/CCC back-to-back transmission block is shown in the following figure.

The system model is build by means of standard elements in PSS/E load flow program as shown in the figure below.

The two terminal DC transmission line model is setup by two serie connected 6-pulse converters configured as shown in the figure below.

In the test cases the number of parallel HVDC/CCC blocks are added to represent two or five blocks operation.

Operating with five parallel blocks require duplicated ac transmission lines to handle the increased power transmission.

# Dynamic Model

## Introduction

A special PSS/E user models have been developed to represent the common functions of a complex  system of several HVDC transmission blocks.

The data sheet for the models are included in paragraph 5. The data sheets contain actual constant parameters for the test case and the parameters determine the dynamic performance of the dc transmission

## User model MCTRL5

### Functional description

The MCTRL5 model controls the power flow of up to 5 of HVDC two terminal transmission blocks.

The dynamic model, MCTRL5, controls the power orders to the active HVDC blocks. The model is provided with fundamental parameters in the input data that defines the HVDC transmission system. The dynamic models includes following main functions

- Active power control

- Reactive power control

- Damping controller between parallel HVDC transmission blocks

#### Active power control

The active power control functions coordinates the power order to the HVDC transmission blocks. During the initiation the actual power orders are calculated to each blocks. Depending of the operation mode, the power can be set individually for each block or on biblock level or the total power for the whole transmission.

The power limit of each block is introduced and can be set individually for each block. A loss of power in one block is compensated by the other block if it is not in limitation.

The input settings of the ICON-constants define the active blocks and also the control modes.

Power orders are introduced in MW. If the HVDC converters are operating current control mode, the actual dc power is calculated by using the nominal dc voltage of 140 kV.

A rate of change limiter is introduced to avoid unrealistic fast order changes. One increase and one decrease constants define the actual rate of change.

The active power controller has three control modes. These modes are,

- Control mode 1	Individual block control

The power order or Current order is initiated from the load flow solution and the order can be changed from the Edit function in the PSS/E menu.

- Control mode 2	Biblock control

Each biblock is controlled individually. Biblock 1 from VAR(L+2) and Biblock 2 from VAR(L+3). The remaining block can be controlled from VAR(L+4). A change in power order will be distributed to both blocks in the biblock configuration. If the power order to one block is limited the other block in the same biblock will compensate the missing power.

If an individual power order in one biblock must be changed the corresponding ICON-constant must be reset and the common control mode of the biblock is disabled and the order can be set manually.

- Control mode 3	Master control

A common power order determines the total power of the whole DC transmission

The total power is set manually in VAR(L+1) and the power order is distributed to all blocks in the same relation used in the load flow solution. A change in power order is thus distributed to all the active blocks

#### Reactive power control

The reactive power is controlled by the ac voltage regulator. One regulator is introduced for each ac side. The regulator is activated as soon as the actual ac voltage exceeds the reference value set by the operator.

The ac voltage regulator is designed as a PI-regulator where the actual parameters are set in the dynamic input data. The output of the regulator increases the gamma reference of the inverter converter and thus increases the reactive power consumption of the converter.

The function is activated by the constants ICON(M+11) (rectifier side) and ICON(M+12) (inverter side).

#### Damping controller between parallel HVDC blocks

The controller is activated as soon as the rectifier current controller goes to its min limit and the rectifier current control is lost. A pi-regulator gives a contribution to the inverter control to reduce the dc voltage by increasing the gamma min reference.

The reference value of the controller can be set manually in the input data file CON(J+12). By setting the value equal to zero, the reference value is automatically set, equal to the actual input value from the HVDC blocks, during the initiation in mode 1. In this way the controller is adjusted to the actual load flow solution.

### Operation

The control functions can be activated or deactivated by corresponding parameters in the ICON vector. Depending on the actual operating mode, the transmitted power can thus be controlled at block level, biblock level or system level.

An overview of the parameters can be seen in the data sheet, see paragraph 5.1.

## User model CDCAB2

### Description CDCAB2

The user model CDCAB2 is a detailed model of the two terminal HVDC transmission. A general description of this dynamic HVDC model is presented in the report 1JNL100029-389, Dynamic HVDC Model in PSS/E program version 26.2.

This report deals with HVDC transmission systems, where up to five of these transmission blocks are working in parallel.

The user model CDCAB2 has been updated to include the communication with the master control model. The corresponding files have been named cfc_model_036.f.

This indicates that the file has been updated ‘036’, meaning year 2000 week 36.

The following files defines the model,

cfc_model_036.f		source file

data_btb_036.f			data file

cfc_constants_036.ins		declaration file

To make the model user friendly the parameter list of the data sheet has been limited to 44 constants. The remaining parameters (about 150) are specified in a separate data file (data_btb_036.f). These parameters are internally stored in a common memory.

This data file is common for all the dynamic HVDC models in of type, CDCAB2, in the system. On the contrary, all the constants specified in the dynamic data file (dyn_btb.dyr) can be set individually for each dc transmission.

The input data can be verified by reading the printout from the initiation stage. The activity DOCU produces a tabulated list of the model references in the dynamic setup. The storage locations used by the model in the various dynamic arrays are also listed

The selections, FILE, LIST, Dynamic Models and Data (DOCU) and Select bus number generate the parameter list.

### Operation

The dynamic model CDCAB2 includes a master control function, which only controls the transmitted power of the converter block. The model MCTRL5 is adding the common control features of the whole transmission system.

The master control of each block provides all the functions common for the two converters and includes Active Power Control, Frequency Control and Damping Control.

Operation and control of a single block are obtained by resetting the master control functions, which releases the individual control variables.

## User model POWDEC

### Description

This user model can also be added into the simulation to study the dynamic behavior of the HVDC system at frequency deviation in the sending ac system. The active power of the transmission is reduced according to a special scheme specified according to regulations of the ac system. The source file has been updated to give the user control how the power reduction should be carried out.

### Operation

The ICON(M+44) of the POWDEC model is used to identify the HVDC block to be controlled. A new switch has introduced so the ICON-constant also can be used to point out which power order should be controlled, system of biblock level.

If ICON(I+44) is set equal to 1, only the HVDC block with identity 1 is controlled. By setting the ICON-constant equal to the position in the VAR-vector of the system or biblock power order all the active blocks controlled from this power order will be included in the power reduction.

For example, if all the HVDC blocks should be controlled, the ICON-constant should point to the system power order of the master control mode VAR(L+1).

C  ADD HVDC Interface 991116, 20000912

C

If (ICON(I+44).LT.100) Then

Setval(ICON(I+44)) = Setval(ICON(I+44)) * FACT

write (19,*) 'Setval_out =',Setval(ICON(I+44)), FACT, Time

Else

VAR(ICON(I+44)) = VAR(ICON(I+44)) * FACT

write (19,*) 'VAR(',ICON(I+44),') =',VAR(ICON(I+44)), FACT, Time

Endif

C

These lines have been implemented in the new model version, source file powdec_036.f

# Operation Instruction of the Test Cases

## Introduction

This paragraph presents the data and response files used for set up and running the dynamic simulations for two test cases. The two test cases represent the Garabi transmission operating in two different transmission modes. The first test case is a double block transmission where the 1100 MW is transmitted via two parallel blocks. This corresponds to the Garabi 1 configuration.

The second test case is a setup of the maximum operation mode with a transmission of 2750 MW via five HVDC blocks.

Appendix 1 presents a fast procedure to start up the test cases by using the response files which includes the basic commands required to solve the load flow and to run the dynamic simulation.

This paragraph will give more details of each step in the procedure.

## Double block operation

### Load flow

The douible block test case is set up with a power transmission of 1100 MW and two HVDC/CCC converter blocks in operation

Example of raw data file of the test case,

File: flow_btb.raw

0   100   / Garabi 1100 MW,nom power, two blocks

<Garabi system: CCCgarabi1/flow_btb.raw>

<1100 MW power transfer, reduced network>

1,'Arg_sw    ',500,3,0.0,0.0,1,1,1.0,   0.1

2,'Ita_sw    ',525,3,0.0,0.0,1,1,1.0,   0.2

10,'Garabi_a ',500,1,0.0,0.0,1,1,1.0,  -8.3

20,'Garabi_b ',525,1,0.0,0.0,1,1,1.0,  16.4

30,'Ita      ',525,1,0.0,0.0,1,1,1.0,   7.5

0  / Line reactor

0 /* Infinite Sources

1 1 +1100  176 9999 -9999 1.0100  0 1000  0.0033  0.003330  0.0  0.0 1.0 1 100 9999 -9999

2 1 -1100 -144 9999 -9999 1.0050  0 1000  0.0033  0.003330  0.0  0.0 1.0 1 100 9999 -9999

0 /* Branches

1  10 1  0.00133   0.0147   1.3320   0.0  0.0  0.0,,,   0.0  0.0  0.0  0.0 1

20  30 1  0.00308   0.04167  4.9613   0.0  0.0  0.0,,,   0.0  0.0  0.0  0.0 1

30  2  1  0.00      0.0147   0.0      0.0  0.0  0.0,,,   0.0  0.0  0.0  0.0 1

0

0

0 /* HVDC Current control CCC_conv

1 2   0.4    3930    140    0.0     0.4   0.10    R    0.0

10 2 -5.70 -5.70  0.0001  1.118  500  0.10360  0.977 1.11  0.98  .0000001 0  0  0 1  3.7305

20 2 21.70 21.70  0.0001  1.366  525  0.09866  1.035 1.11  0.90  .0000001 0  0  0 1  6.3418

2 2   0.4    3930    140    0.0     0.4   0.10    R    0.0

10 2 -5.70 -5.70  0.0001  1.118  500  0.10360  0.977 1.11  0.98  .0000001 0  0  0 1  3.7305

20 2 21.70 21.70  0.0001  1.366  525  0.09866  1.035 1.11  0.90  .0000001 0  0  0 1  6.3418

0 / Switched shunts, reactors and filters

10  0  1.0  1.0  0  86.65  1  86.65

20  0  1.0  1.0  0  -57.9  1  -57.9

30  0  1.0  1.0  0  -150.  1  -150.

0

0

0

0

0

0

0

0

The load flow can be solved by the following steps.

- Manually command steps,

- READ, ALL, 		Raw data file

- CHNG, 		change the iteration steps 20 -> 200

- FDNS, OPT, 		run decoupled Newton Raphson

- FNSL,OPT		run full Newton Raphson

- BAT_CONL, 		converge loads

- CONG,			converge generators

- SAVE 			the case in file flow_btb

### Snap shot and compile

Before a dynamic simulation can be performed, three steps have to be executed, creating snap shop, compiling the dynamic models and finally link the object files into a executable file (Dsusr.dll-file).

A snap shot is created by following response file, snap_btb.idv

MENU,OFF /* ver.26.2.2, output snap_btb.idv

LOFL

CASE

flow_btb.sav

ORDR

FACT

RTRN

DYRE

dyn_btb.dyr

conec.flx

conet.flx

,,,

compile

SNAP

snap_btb.snp

,,,,

ECHO

@END

A bat-file is created (PC-platform) with the name compile.bat. This file includes all the commands and compiler parameters to start the flecs-compiler and the Fortran-compiler.

The command “compile” compiles the file conec.flx and conet.flx.

Next steps are to compile the source files of the models

The source files of the model CDCAB2 are Fortran files and the Flecs compiler should not be used. It is enough just to run the Fortran compiler.

The command “comp_036” will compile the CDCAB2 model

The master control MCTRL5 and the POWDEC models are compiled with both Flecs and Fortran compiler.

The command “comp_mctrl5” will compile the MCTRL5 model and

In the same way “comp_powdec” will compile the POWDEC model.

All the object files must be linked together to create the DLL-file. This is done by the PSS/E file cload4, as

The command “cload4 cfc_model_036.obj data_btb.obj  mctrl5.obj”

Will create the Dsusr.dll-file used to start up the dynamic simulation.

Example of bat-file;  comp_mctrl5

@ECHO OFF

FLECS32 "mctrl5.flx" -L NO -F PSS003.FOR -EXPAND -W 100 -S * "C:\Program Files\PTI\PSSE26\PSSLIB" -F77

DF /4L132 /4Ya /4Nd /nologo /fltconsistency /fpscomp:logicals /c /4Nportlib /Fo"mctrl5.OBJ" /D"DLLI" /MD PSS003.FOR /I"C:\Program Files\PTI\PSSE26\PSSLIB"

DEL PSS003.FOR

REM

ECHO If no errors, execute "HVDCL-CLOAD4"

### Dynamic simulation

The input data can be verified by checking the printout from a valid load flow case and dynamic data in the dynamics working memory. The output is in the form of a Dynamic Data File and is activated by the selections, FILE, OUTPUT, Write dynamic data in source format (DYDA).

Note that an integration time step of <¼ cycle or less should be used when PSS/E simulation cases include a HVDC with typical time constants as listed.

The following response-file will start the simulation in following steps,

- Setup the snap_shot, flow_btb.snp and activate the saved case, flow_btb.sav.

- Set the integration time step to <¼ of the cycle time, <5 ms.

- The plot signals are added

- Set plot file, start.out

- Run the system

Note: The plot channels are selected according to the position of the signal in the STATE-vector and VAR-vector according to the data sheets in paragraph 6. The data sheet includes the starting position obtained in the two test cases.

The user can now continue the dynamic simulation by activating the control function available in the models or perform changes in the ac system.

For instant, the active power of the dc transmission can be changed by alter the active power main order, VAR(202), see data sheet.

The plot signals introduced during the start procedure are now available for plotting by using the normal features in PSS/E.

The dynamic date is introduced by the following,

File:	dyn_btb.dyr

1, 'GENCLS', 1, 0.0, 0.0 /  Update 000831

2, 'GENCLS', 1, 0.0, 0.0 /

10 'USRMDL' 1 'MCTRL5' 8 0 15 40 8 100

1    1 1 0    1 1 0   0 0 0   0   0 0 0 0

2750 1100 1100 550 0 0 550 550 550 550 550

0.05 0.0 5.0 1.0 2.0 1.0 0.1 1.0 8.0  0

0.01 0.0 5.0 0.0 2.0 1.0 0.1 0.5 10.0

1.05 1.0 0.1 0.1 5.0

1.05 1.0 0.1 0.1 5.0/

1  'USRMDL'  0 'CDCAB2' 7 1

10 44 30 100

1 0 0 0 0 0 0 0 3 2

4.02

140.0  3.930

50.00  0  60.0  0  0  0

0 0 0 0 0 0 0 0

100

0 0 0 0 0 0

0.005 0.06  0.8 0.2 0.1 2.0 0.3

0.005 0.055 0.8 0.2 0.1 2.0 0.3

80.0 0.0005 40.0 0.0004

0 0/

2  'USRMDL'  0 'CDCAB2' 7 1

10 44 30 100

1 0 0 0 0 0 0 0 3 2

4.02

140.0  3.930

50.00  0  60.0  0  0  0

0 0 0 0 0 0 0 0

100

0 0 0 0 0 0

0.005 0.06  0.8 0.2 0.1 2.0 0.3

0.005 0.055 0.8 0.2 0.1 2.0 0.3

80.0 0.0005 40.0 0.0004

0 0/

/

With the input data shown above the power orders are organized according to the following figure.

A power order change can thus be initiated by editing the variable VAR(L+1) and in this test case position VAR(202).

If the operation mode is changed to Biblock control by resetting ICON(M+1), the power order is controlled by variable VAR(L+2) to biblock 1.

If also the Biblock control is reset ICON(M+2)=0, the power order is controlled by Editing the DC line in PSS/E menu.

## Multi block operation

### Load flow

Test case with active power transmission of 2750 MW and five HVDC/CCC converter blocks in operation. Garabi 1 operating with two blocks at 1100 MW and Garabi 2 operating with two blocks at 1100 MW and a fifth block operating at 550 MW.

### Snap shot and compile

Before a dynamic simulation can be performed, three steps have to be executed, creating snap shot, compiling the dynamic models and finally start up the case.

The procedure is described in paragraph 4.2.2

### Dynamic simulation

The following input file introduces dynamic data of the five HVDC blocks,

File:	dyn_btb_5.dyr

1, 'GENCLS', 1, 0.0, 0.0 /  Update 000831

2, 'GENCLS', 1, 0.0, 0.0 /

10 'USRMDL' 1 'MCTRL5' 8 0 15 40 8 100

1    1 1 1    1 1 0   1 1 0   1   0 0 0 0

2750 1100 1100 550 0 0 550 550 550 550 550

0.05 0.0 5.0 1.0 2.0 1.0 0.1 1.0 8.0  0

0.01 0.0 5.0 0.0 2.0 1.0 0.1 0.5 10.0

1.05 1.0 0.1 0.1 5.0

1.05 1.0 0.1 0.1 5.0/

1  'USRMDL'  0 'CDCAB2' 7 1

10 44 30 100

1 0 0 0 0 0 0 0 3 2

4.02

140.0  3.930

50.00  0  60.0  0  0  0

0 0 0 0 0 0 0 0

100

0 0 0 0 0 0

0.005 0.06  0.8 0.2 0.1 2.0 0.3

0.005 0.055 0.8 0.2 0.1 2.0 0.3

80.0 0.0005 40.0 0.0004

0 0/

2  'USRMDL'  0 'CDCAB2' 7 1

and so on to block 5

5  'USRMDL'  0 'CDCAB2' 7 1

10 44 30 100

1 0 0 0 0 0 0 0 3 2

4.02

140.0  3.930

50.00  0  60.0  0  0  0

0 0 0 0 0 0 0 0

100

0 0 0 0 0 0

0.005 0.06  0.8 0.2 0.1 2.0 0.3

0.005 0.055 0.8 0.2 0.1 2.0 0.3

80.0 0.0005 40.0 0.0004

0 0/

/

With the input data shown above the power orders are organized according to the following figure.

A power order change can thus be initiated by editing the variable VAR(L+1) and in this test case variable VAR(502) will determine the total power of the dc transmission. The distribution of the power order is done with the same ratio as specified in the load flow, as long as no power limitation is exceeded.

# DATA SHEET

## Dynamic Model of Master Control MCTRL5.

PTI POWER SYSTEM SIMULATOR

MASTER CONTROL

(HVDC CCC Transmission with 5 back-to-back transmission blocks)

CALL  MCTRL5(M, J, K, L) from CONEC

This is HVDC MC model, Id = 12345678

using ICONs starting at			#__________ M,

and CONs  starting at			#___________J,

and STATEs starting at			#___________K,

and VARs   starting at			#___________L.

Dynamic HVDC Master Control Model

BusId ‘USRMDL’  IC IT NI NC NS NV Data_List/

(BusId ‘USRMDL’ 8  0   15   40   8   100  ................./ )

where,

IC	equal to 8	Other model

(placed before return in CONEC)

IT	equal to 0	Not a current injection model

NI	equal to 15	number of ICON vectors

NC	equal to 40	number of CON vectors

NS	equal to 8	number of STATE vectors

NV	equal to 100	number of VAR vectors

Data_List: ICONS, CONS input data for the dc model itself, see data sheet below.

(The actual values of the constants are included in the data sheets)

Comments:

The model assumes that the block number corresponds to the blocks in the real system. For example, Block 1 and Block 2 correspond to block number 1 respective block number 2 and thus correspond to the two HVDC blocks which belongs to the Garabi 1 system.

The position numbers of the vectors have been added in the data sheet for the two described test cases.

CONSTANTS	MCNTRL5

| ICONs | # | Value | Name | Description |
| --- | --- | --- | --- | --- |
| M | (21,51) | 1 |  | Power direction Argentina -> Brazil |
| M+1 |  | 1 |  | Garabi, total active power control |
| M+2 |  | 1 |  | Garabi 1, Biblock active |
| M+3 |  | 1 |  | Garabi 2, Biblock active |
| M+4 |  | 1 |  | Block 1 active |
| M+5 |  | 1 |  | Block 2 active |
| M+6 |  | 0 |  | Power compensation Block 1 and 2 active |
| M+7 |  | 1 |  | Block 3 active |
| M+8 |  | 1 |  | Block 4 active |
| M+9 |  | 0 |  | Power compensation Block 3 and 4 active |
| M+10 |  | 1 |  | Block 5 active |
| M+11 |  | 0 |  | AC Voltage regulator Argentina active |
| M+12 |  | 0 |  | AC Voltage regulator Brazil active |
| M+13 |  | 0 |  | Internal logic |
| M+14 |  | 0 |  | Internal logic |

CONSTANTS		MCTRL5

| CONs | # | Value | NAME | DESCRIPTION |
| --- | --- | --- | --- | --- |
| J | (93,225) | 2750 |  | Garabi Max power limit MW |
| J+1 |  | 1100 |  | Garabi 1 Max power limit |
| J+2 |  | 1100 |  | Garabi 2 Max power limit |
| J+3 |  | 550 |  | Garabi 3 Max power limit |
| J+4 |  |  |  |  |
| J+5 |  |  |  |  |
|  |  |  | Max active power limitation |  |
| J+6 |  | 550 |  | Block 1 Max power limit |
| J+7 |  | 550 |  | Block 2 Max power limit |
| J+8 |  | 550 |  | Block 3 Max power limit |
| J+9 |  | 550 |  | Block 4 Max power limit |
| J+10 |  | 550 |  | Block 5 Max power limit |
|  |  |  | Alpha Controller |  |
| J+11 |  | 0.05 |  | Alpha control, input filter time const |
| J+12 |  | 3.5 |  | Alpha control, reference deg |
| J+13 |  | 5.0 |  | Alpha control, diff limit deg |
| J+14 |  | 1.0 |  | Alpha control, deadband deg |
| J+15 |  | 2.0 |  | Alpha control, gain 1 |
| J+16 |  | 1.0 |  | Alpha control, gain 2 |
| J+17 |  | 0.1 |  | Alpha control, p_gain |
| J+18 |  | 1.0 |  | Alpha control, i_time_const |
| J+19 |  | 8.0 |  | Alpha control, output limit deg |
| J+20 |  |  |  |  |
|  |  |  | Gamma controller |  |
| J+21 |  | 0.01 |  | Gamma control, input filter time const |
| J+22 |  | 0.0 |  | Gamma control, reference deg |
| J+23 |  | 5.0 |  | Gamma control, diff limit deg |
| J+24 |  | 0.0 |  | Gamma control, deadband deg |
| J+25 |  | 2.0 |  | Gamma control, gain 1 |
| J+26 |  | 1.0 |  | Gamma control, gain 2 |
| J+27 |  | 0.1 |  | Gamma control, p_gain |
| J+28 |  | 0.5 |  | Gamma control, i_time_const |
| J+29 |  | 10.0 |  | Gamma control, output limit deg |
|  |  |  | AC Voltage regulator |  |
| J+30 |  | 1.05 |  | AC voltage regulator, Argentina, Volt.Ref |
| J+31 |  | 1.0 |  | AC voltage regulator, Argentina, gain |
| J+32 |  | 0.1 |  | AC voltage regulator, Argentina, prop.gain |
| J+33 |  | 0.1 |  | AC voltage regulator, Argentina, time integrator |
| J+34 |  | 5.0 |  | AC voltage regulator, Argentina, Limit |
|  |  |  | AC Voltage regulator |  |
| J+35 |  | 1.05 |  | AC voltage regulator, Brazil, Volt.Ref |
| J+36 |  | 1.0 |  | AC voltage regulator, Brazil, gain |
| J+37 |  | 0.1 |  | AC voltage regulator, Brazil, prop gain |
| J+38 |  | 0.1 |  | AC voltage regulator, Brazil, time integrator |
| J+39 |  | 5.0 |  | AC voltage regulator, Brazil, limit |

STATEs	MCTRL5

| STATEs | # | Name | DESCRIPTION |
| --- | --- | --- | --- |
| K | (65,155) | P_ret_pu |  |
| K+1 |  |  | Alpha control, input filter |
| K+2 |  |  | Alpha control, integrator |
| K+3 |  |  | Gamma control, input filter |
| K+4 |  |  | Gamma control, integrator |
| K+5 |  |  | AC Voltage Regulator, Argentina |
| K+6 |  |  | AC Voltage Regulator, Brazil |
| K+7 |  |  | Spare |

VARIABLES:		MCTRL5

| VARs | # | NAME | DESCRIPTION |
| --- | --- | --- | --- |
| L | (201,501) |  | Master control id |
|  |  | Power Order |  |
| L+1 |  |  | Garabi Total Power Order MW |
| L+2 |  |  | Garabi 1 Power Order MW |
| L+3 |  |  | Garabi 2 Power Order MW |
| L+4 |  |  | Garabi 3 Power Order MW |
| L+5 |  |  | Spare |
|  |  | Loss of active power |  |
| L+6 |  |  | Power loss in Block 1 |
| L+7 |  |  | Power loss in Block 2 |
| L+8 |  |  | Power loss in Block 3 |
| L+9 |  |  | Power loss in Block 4 |
| L+10 |  |  | Power loss in Block 5 |
| L+11 |  |  | Power Order Block 1 |
| L+12 |  |  | Power Order Block 2 |
| L+13 |  |  | Power Order Block 3 |
| L+14 |  |  | Power Order Block 4 |
| L+15 |  |  | Power Order Block 5 |
| L+16 |  |  | Spare |
| L+17 |  |  | Spare |
| L+18 |  |  | Spare |
| L+19 |  |  | Spare |
| L+20 |  |  | Spare |
|  |  | Alpha diff inputs |  |
| L+21 |  |  | Alpha Int_diff Block 1 |
| L+22 |  |  | Alpha Int_diff Block 2 |
| L+23 |  |  | Alpha Int_diff Block 3 |
| L+24 |  |  | Alpha Int_diff Block 4 |
| L+25 |  |  | Alpha Int_diff Block 5 |
|  |  | Gamma diff inputs |  |
| L+26 |  |  | Gamma Int_diff Block 1 |
| L+27 |  |  | Gamma Int_diff Block 2 |
| L+28 |  |  | Gamma Int_diff Block 3 |
| L+29 |  |  | Gamma Int_diff Block 4 |
| L+30 |  |  | Gamma Int_diff Block 5 |
|  |  | Delta gamma output |  |
| L+31 |  |  | Dgmin to Block 1 |
| L+32 |  |  | Dgmin to Block 2 |
| L+33 |  |  | Dgmin to Block 3 |
| L+34 |  |  | Dgmin to Block 4 |
| L+35 |  |  | Dgmin to Block 5 |
|  |  | Delta alpha output |  |
| L+36 |  |  | Dalpha min to Block 1 |
| L+37 |  |  | Dalpha min to Block 2 |
| L+38 |  |  | Dalpha min to Block 3 |
| L+39 |  |  | Dalpha min to Block 4 |
| L+40 |  |  | Dalpha min to Block 5 |
|  |  | RPC outputs Arg. |  |
| L+41 |  |  | Da_rpc to Block 1, Argentina |
| L+42 |  |  | Da_rpc to Block 2 |
| L+43 |  |  | Da_rpc to Block 3 |
| L+44 |  |  | Da_rpc to Block 4 |
| L+45 |  |  | Da_rpc to Block 5 |
|  |  | RPC outputs Brazil |  |
| L+46 |  |  | Da_rpc to Block 1, Brazil |
| L+47 |  |  | Da_rpc to Block 2 |
| L+48 |  |  | Da_rpc to Block 3 |
| L+49 |  |  | Da_rpc to Block 4 |
| L+50 |  |  | Da_rpc to Block 5 |
|  |  | Alpha controller |  |
| L+51 |  |  | Acont_in |
| L+52 |  |  | Acont_diff |
| L+53 |  |  | Acont_swc_g |
|  |  | Gamma controller |  |
| L+54 |  |  | Gcont_in |
| L+55 |  |  | Gcont_diff |
|  |  | Voltage regulator Arg |  |
| L+56 |  |  | Uac regulator Argentina, Dvolt input |
| L+57 |  |  | Uac regulator Argentina, Dvolt diff |
|  |  | Voltage regulator Bra |  |
| L+58 |  |  | Uac regulator Brazil, Dvolt input |
| L+59 |  |  | Uac regulator Brazil, Dvolt diff |
| L+60 |  |  |  |
| L+61 |  |  | Active power ratio of Garabi 1 |
| L+62 |  |  | Active power ratio of Garabi 2 |
| L+63 |  |  | Active power ratio of Block 5 (Garabi 3) |
| L+64 |  |  | Active power ratio of Block 1 and Block 2 |
| L+65 |  |  | Active power ratio of Block 3 and Block 4 |
| L+66 |  |  |  |
| L+67 |  |  |  |
| L+68 |  |  |  |
| L+69 |  |  |  |

## Dynamic Model CDCAB2, Data Sheet

- PTI POWER SYSTEM SIMULATOR

- CDCAB2	(HVDC Transmission)

- CALL  CDCAB2(7,1,10,44,30,100) from CONEC

CALL  TDCAB2(7,1,10,44,30,100) from CONET

This is HVDC model, Id		#_____1_____ I,

using ICONs starting at			#_____1_____ M,

and CONs  starting at			#_____5______J,

and STATEs starting at			#_____5______K,

and VARs   starting at			#_____1______L.

- CONSTANTS

| ICONs | # | Value | Description |
| --- | --- | --- | --- |
| M | (1) | 1 | Current direction, current from rect=1, inv=0 |
| M+1 |  | 0 | Block, internal program variable |
| M+2 |  | 0 | Bypass rectifier, internal program variable |
| M+3 |  | 0 | Bypass inverter, internal program variable |
| M+4 |  | 0 | Frequency Control, disable=0 rectifier enable=1, inverter enabl = 2 |
| M+5 |  | 0 | Damping Controller, disable=0 rectifier enable=1,inverter enabl = 2 |
| M+6 |  | 0 | Internal program variable |
| M+7 |  | 0 | Internal program variable |
| M+8 |  | 3 | Internal program variable, CCC_Indication Rect=1,Inv=2,Rect+Inv=3 |
| M+9 |  | 2 | Internal program variable, Transmission Type Line/Cable=1, Back-to-Back=2 |

- CONSTANTS

| CONs |  |  | # |  |  | Value |  |  | NAME | DESCRIPTION |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| J | (5) |  |  | 4.02 |  |  | Iomax_Master |  |  |  | Max Limit in transmitted dc current, kA |  |
| J+1 |  |  |  | 140 |  |  | UdN |  |  |  | Nominal DC Voltage in kV |  |
| J+2 |  |  |  |  | 3.93 |  |  | IdN |  |  | Nominal DC Current in kA |  |
| J+3 |  |  |  |  | 50 |  |  | Freq_Nom_r |  |  | Frequency at Rectifier, Hz |  |
| J+4 |  |  |  |  | 0 |  |  | CCC_ind_r |  |  | CCC indication Rectifier, CCC conv. CCC=1 |  |
| J+5 |  |  |  |  | 60 |  |  | Freq_Nom_i |  |  | Frequency at Inverter, Hz |  |
| J+6 |  |  |  |  | 0 |  |  | CCC_ind_i |  |  | CCC indication Inverter, CCC conv. CCC=1 |  |
| J+7 |  |  |  |  | 0 |  |  | Alpha_r0 |  |  | Delay angle init value rectifier (from Matlab) |  |
| J+8 |  |  |  |  | 0 |  |  | Alpha_i0 |  |  | Delay angle init value inverter (from Matlab) |  |
|  |  |  |  |  |  |  |  |  |  |  | #### Line/Cable Model |  |
| J+9 |  |  |  |  | 0 |  |  | LS_r |  |  | Rectifier smoothing reactor inductance (mH) |  |
| J+10 |  |  |  |  | 0 |  |  | RS_r |  |  | Rectifier smoothing reactor resistance (Ohm)) |  |
| J+11 |  |  |  |  | 0 |  |  | L_r |  |  | Rectifier line/cable inductance (mH) |  |
| J+12 |  |  |  |  | 0 |  |  | CC |  |  | Linie/Cable capacitance (uF) |  |
| J+13 |  |  |  |  | 0 |  |  | RC |  |  | Linie/Cable serie capacitance (Ohm) |  |
| J+14 |  |  |  |  | 0 |  |  | LS_i |  |  | Inverter smoothing reactor inductance (mH) |  |
| J+15 |  |  |  |  | 0 |  |  | RS_i |  |  | Inverter smoothing reactor resistance (Ohm)) |  |
| J+16 |  |  |  |  | 0 |  |  | L_i |  |  | Inverter line/cable inductance (mH) |  |
|  |  |  |  |  |  |  |  |  |  |  | #### Back-to-Back Model |  |
| J+17 |  |  |  |  | 200 |  |  | L_S |  |  | Smoothing reactor inductance (mH) |  |
|  |  |  |  |  |  |  |  |  |  |  | #### Rectifier Converter |  |
| J+18 |  |  |  |  | 0 |  |  | dx_r |  |  | Commutation inductance,Transformer inductance |  |
| J+19 |  |  |  |  | 0 |  |  | dr_r |  |  | Commutation resistance,Transformer resistance |  |
| J+20 |  |  |  |  | 0 |  |  | dxc_r |  |  | Commutation capacitance |  |
|  |  |  |  |  |  |  |  |  |  |  | #### Inverter Converter |  |
| J+21 |  |  |  |  | 0 |  |  | dx_i |  |  | Commutation inductance,Transformer inductance |  |
| J+22 |  |  |  |  | 0 |  |  | dr_i |  |  | Commutation resistance,Transformer resistance |  |
| J+23 |  |  |  |  | 0 |  |  | dxc_i |  |  | Commutation capacitance, inverter |  |
|  |  |  |  |  |  |  |  |  |  |  | #### VDCOL Parameters, see Figure 1 |  |
| J+24 |  |  |  |  | 0.005 |  |  | T_Down_r |  |  | Time constant for decreasing dc voltage |  |
| J+25 |  |  |  |  | 0.06 |  |  | T_Up_r |  |  | Time constant for increasing dc voltage |  |
| J+26 |  |  |  |  | 0.8 |  |  | Udbr_r |  |  | Voltage breakpoint for activating VDCOL limit |  |
| J+27 |  |  |  |  | 0.2 |  |  | Iomaxm_r |  |  | Maximum of lower VDCOL current limit |  |
| J+28 |  |  |  |  | 0.1 |  |  | Iomin_r |  |  | Minimum of lower VDCOL current limit |  |
| J+29 |  |  |  |  | 2.0 |  |  | Imax_r |  |  | Maximum Current limit of VDCOL |  |
| J+30 |  |  |  |  | 0.3 |  |  | Udlow_r |  |  | Low breakpoint in dc voltage |  |
| J+31 |  |  |  |  | 0.002 |  |  | T_Down_i |  |  | Time constant for decreasing dc voltage |  |
| J+32 |  |  |  |  | 0.055 |  |  | T_Up_i |  |  | Time constant for increasing dc voltage |  |
| J+33 |  |  |  |  | 0.8 |  |  | Udbr_i |  |  | Voltage breakpoint for activating VDCOL limit |  |
| J+34 |  |  |  |  | 0.2 |  |  | Iomaxm_i |  |  | Maximum of lower VDCOL current limit |  |
| J+35 |  |  |  |  | 0.1 |  |  | Iomin_i |  |  | Minimum of lower VDCOL current limit |  |
| J+36 |  |  |  |  | 2.0 |  |  | Imax_i |  |  | Maximum Current limit of VDCOL |  |
| J+37 |  |  |  |  | 0.3 |  |  | Udlow_i |  |  | Lower breakpoint in dc voltage |  |
|  |  |  |  |  |  |  |  |  |  |  | CCA Parameters |  |
| J+38 |  |  |  |  | 80 |  |  | Kp_r |  |  | CCA Rectifier,Proportional gain (deg/pu) |  |
| J+39 |  |  |  |  | 0.0005 |  |  | Ti_r |  |  | CCA Rectifier,Integrator gain (deg/pu/sec) |  |
| J+40 |  |  |  |  | 40 |  |  | Kp_i |  |  | CCA Inverter,Proportional gain (deg/pu) |  |
| J+41 |  |  |  |  | 0.0004 |  |  | Ti_i |  |  | CCA InverterIntegrator gain (deg/pu/sec) |  |
|  |  |  |  |  |  |  |  |  |  |  | #### Inverter control |  |
| J+42 |  |  |  |  | 0 |  |  | Gamp_ref_i |  |  | Inverter Gamma_prim reference (deg) |  |
| J+43 |  |  |  |  | 0 |  |  |  |  |  | Spare Not used |  |

- Note: The symbol  indicates that the actual constant, if set to zero, is picked up from the load flow, otherwise the specified value are used.

- STATE

| STATEs | # | DESCRIPTION |
| --- | --- | --- |
| K | (5) | DC Current, rectifier |
| K+1 |  | DC Current measurement, rectifier |
| K+2 |  | DC Voltage measurement, rectifier |
| K+3 |  | DC Current, inverter |
| K+4 |  | DC Current measurement, inverter |
| K+5 |  | DC Voltage measurement, inverter |
| K+6 |  | Cable voltage, not used in Back-to-Back |
| K+7 |  | VDCOL dc voltage measuring, rectifier |
| K+8 |  | VDCOL dc voltage measuring, inverter |
| K+9 |  | CCA, integrator part, rectifier |
| K+10 |  | CCA, integrator part, inverter |
| K+11 |  | Alpha in rectifier |
| K+12 |  | Alpha in inverter |
| K+13 |  | Inverter current margin |
| K+14 |  | Amin, rate of change |
| K+15 |  |  |
| K+16 |  | Amax, rate of change |
| K+17 |  | Amax current controller |
| K+18 |  | Udio filter in Amax calculation |
| K+19 |  | Not used |
| K+20 |  | Commutation voltage |
| K+21 |  | Frequency measuring in rectifier |
| K+22 |  | Frequency measuring in rectifier |
| K+23 |  | Damping Controller filter 1 |
| K+24 |  | Damping Controller filter 2 |
| K+25 |  | Master control, dc voltage measuring |
| K+26 |  | Alpha filtering, rectifier |
| K+27 |  | Alpha filtering, inverter |
| K+28 |  | Not used |
| K+29 |  | Not used |

- VARIABLES:

| VARs | # | Value | NAME | DESCRIPTION |
| --- | --- | --- | --- | --- |
| L | (1) |  | Pac_r | Active power in rectifier |
| L+1 |  |  | Qac_r | Reactive power in rectifier |
| L+2 |  |  | Pac_i | Active power in inverter |
| L+3 |  |  | Qac_i | Reactive power in inverter |
| L+4 |  |  | Ioo | MC; DC current order |
| L+5 |  |  | Iorder_r | VDCOL, limited dc current order, rectifier |
| L+6 |  |  | Iorder_i | VDCOL, limited dc current order, inverter |
| L+7 |  |  | I_error_r | CCA, current control error, rectifier |
| L+8 |  |  | Aprop_r | CCA, proportional part, rectifier |
| L+9 |  |  | Alfa_order_r | CCA, alpha order, rectifier |
| L+10 |  |  | Amin_cca_r | Alpha minimum limit, rectifier |
| L+11 |  |  | Amax_cca_r | Alpha maximum limit, rectifier |
| L+12 |  |  | I_error_i | CCA, current control error, inverterr |
| L+13 |  |  | Aprop_i | CCA, proportional part, inverter |
| L+14 |  |  | Alfa_order_i | CCA, current control error, inverter |
| L+15 |  |  | Amin_cca_i | Alpha minimum limit, inverter |
| L+16 |  |  | Amax_cca_i | Alpha maximum limit, inverter |
| L+17 |  |  | Alpha_r | CFC, Alpha rectifier |
| L+18 |  |  | Alpha_i | CFC Alpha inverter |
| L+19 |  |  | dang_r | Phase shift correction |
| L+20 |  |  | dang_i | Phase shift correction |
| L+21 |  |  | Us_kv_r | Converter voltage, rectifier |
| L+22 |  |  | Us_kv_i | Converter voltage, rectifier |
| L+23 |  |  | Udc_r | DC voltage, rectifier |
| L+24 |  |  | Udc_i | DC voltage, inverte |
| L+25 |  |  | Id_r | DC current, rectifier |
| L+26 |  |  | Id_i | DC current, inverter |
| L+27 |  |  | Alfa_r | Alpha, rectifier |
| L+28 |  |  | Alfap_r | Alphaprim, rectifier |
| L+29 |  |  | Alfa_i | Alpha, inverter |
| L+30 |  |  | Gama_i | Gamma angle, inverter |
| L+31 |  |  | Gamap_i | Gamma prim angle, inverter |
| L+32 |  |  | abs(Iac_r) | Injected ac current, rectifier |
| L+33 |  |  | abs(Iac_i) | Injected ac current, inverter |
| L+34 |  |  | Us_r | DC voltage, rectifier |
| L+35 |  |  | Us_i | DC voltage, inverter |
| L+36 |  |  | Delt_Po_Freq | FC, Frequency modulation |
| L+37 |  |  | Delt_Po_Stab | DC, Damping Control modulation |
| L+38 |  |  | Inv_Io_Margin | Inverter current order margin |
| L+39-99 |  |  | Test | Storage of internal program variables |

# References

## Files

Load flow

Raw data file				flow_btb.raw

Dynamic data

Dyr data file	2 blocks		dyn_btb.dyr

Dyr data file	5 blocks		dyn_btb_5.dyr

Model files:

Master control model MCTRL5		mctrl5.flx

Converter control model CDCAB2	cfc_model_036.f

Data of BtB converter block 		data_btb_036.f

Declaration file				cfc_constants_036.f

Response files:

Solve load flow case			solf_lf.idv

Create snapshot				snap.idv

Start up of dynamic case		start_btb.idv

Bat files

Compile conec and conet		compile.bat

Compile model mctrl5			comp_mctrl5.bat

Compile model powdec			comp_powdec.bat

Link all files				link_036.bat

## Reference Reports

[1]	Dynamic HVDC Model in PSS/E

Program version 26.2

1JNL100029-389

[2]	Capacitor Commutated Converter, CCC

Control Principles.	1JNL100004-959

[3]	PSS/E Program Application Guide

Model CDCAB1,

ABB Detailed DC line model, CDCAB1

[4]	PSS/E Program Operation Manual

III.4.3 Non-Standard Models,

ABB DC line model, CDCAB1

Appendix 1, page:1

# QUICK START PROCEDURE FOR RUNNING ON PC

The following is a quick guide to get started using the provided response files (xxxx.idv).  A listing of the idv files is provided in section 4.

- Step 1. Run solv_lf.idv

1. Open the pss/e load flow program: select IO Control and then Set dialog input device, choose and execute solv_lf.idv.

2. Exit pss/e load flow.

This will generate a solved load flow saved case, flow_btb.sav, using the raw data file flow_btb.raw.

- Step 2. Run snap.idv

1. Open the pss/e dynamic program: select IO Control and then Set dialog input device, choose and execute snap.idv.

2. Exit pss/e dynamic program.

This will create a snap file, snap.snp, that will be used for subsequent dynamic runs.

- Step 3. Compile and Link

1. Get in DOS and the appropriate directory where the files for this case is located, execute the following commands in sequence:

compile

comp_036

comp_mctrl5

link_036

2. Exit DOS.

3. Create a “short-cut” to start the pss/e dynamic program and modify the path so that the correct dsusr.dll file from the appropriate directory will be used.

- Appendix 1, page:2

- Step 4. Run strt_btb.idv

1. Start the pss/e dynamic simulation using the “short-cut” created in Step 3 above.

2. Select IO Control and then Set dialog input device, choose and execute start_btb.idv. .

This will initialize and set the case up ready for disturbance simulation. Quantities to be saved for plotting are entered by the execution of start_btb.idv.

Note that the time step size is specified and set to 0.0001 sec by start_btb.idv, and the output for plotting will be stored in the file start.out.

The case is now ready for dynamic simulation.

To speed up the simulation it is convenient to plot and write every 10:th or 50:th step. This allows the simulation to be fairly accurate while the time consuming output is limited.

- Step 5. Run simulation

The power order can be increased and decreased by using the normal procedure in PSS/E.

The results can be plotted by running the pss/e plot program.