## Table 1
Chemical | PVDF rating | PFA/PTFE rating | EPDM rating | Temperature limits | Common Misapplication Flag | Source
Ultrapure Water (UPW) | Excellent (Purad UHP PVDF) | A-Excellent (PTFE-backed diaphragm seals) | A-Excellent (PTFE-backed EPDM) | 130°F for Blue-White pumps; 400°F for Fil-Trek UPW housings | No | 1
Sodium Hydroxide (NaOH) / Caustic | Excellent (Used in C-1500N pump head/adapters) | A-Excellent (PTFE-coated diaphragm) | Not in source | Up to 130°F | Yes - Do not use C-1500N for UHP wafer-process chemical delivery; it is for facilities/wastewater neutralization only. | 1
Concentrated hydrochloric acid | Excellent (Inferred based on recommended use for wetted body) | A-Excellent (Wetted surfaces specified for this service) | Not in source | -80°F to 400°F | Yes: Avoid stainless steel wetted components as chloride ions cause pitting corrosion. | 2
Semiconductor ultra-high-purity acid | Excellent (Inferred based on recommended use for wetted body) | A-Excellent (Specified for this service) | Not in source | -80°F to 400°F | No | 2
Ultrapure Water (UPW/HUPW) | A-Excellent | A-Excellent | Not in source | -4°F to 284°F | No | 3
High-purity Acid Distribution | A-Excellent | A-Excellent | Not in source | -4°F to 284°F | No | 3
Hydrofluoric acid | D-Severe Effect/Fail | A-Excellent (Inferred) | Not in source | Hot (specific values not in source) | Yes - PVDF valves (like Asahi T342) are often misapplied to hot acid lines where PFA/PTFE is required. | 4
Sulfuric acid | D-Severe Effect/Fail | A-Excellent (Inferred) | Not in source | Hot (specific values not in source) | Yes - PVDF valves are often misapplied to hot aggressive chemicals like sulfuric acid leading to chemical attack. | 4
Ultra Pure Water (UPW) | A-Excellent | A-Excellent | Not in source | 68°F (20°C) for stated pressure ratings | No | 5, 6
Hot caustic loops | Not in source | A-Excellent (Specified for this service) | Not in source | -80°F to 400°F | No | 2
Hydrofluoric acid (HF) | Not in source | A-Excellent (Specified for this service) | Not in source | -80°F to 400°F | No | 2
Pharmaceutical API process chemicals | Not in source | A-Excellent (Specified for this service) | Not in source | -80°F to 400°F | No | 2
UHP PFA fluid paths | Not in source | A-Excellent | Not in source | -320°F to 500°F | No | 3
Aggressive Chemicals (Lined Equipment) | Not in source | A-Excellent | Not in source | Up to 400°F | No | 3
Hydrofluoric Acid (HF) | Not in source | A-Excellent (Dymatrix PFA/PTFE line recommended) | Not in source | Not in source | Yes - T-342 Diaphragm Valve (PVDF/PP) is not automatically appropriate for aggressive HF service; PFA/PTFE Dymatrix products are recommended instead. | 1
Sulfuric Acid (H2SO4) | Not in source | A-Excellent (Dymatrix PFA/PTFE line recommended) | Not in source | Not in source | Yes - Keeping leaked acid isolated from water is critical to avoid violent exothermic reactions; ensure SAFE-Tank resin/fitting compatibility. | 1
Hydrochloric Acid (HCl) | Not in source | A-Excellent (Dymatrix PFA/PTFE line recommended) | Not in source | Not in source | Yes - Specific contaminant identity (HCl vs HF) changes required resin/packing for scrubbers. | 1
Hydrogen Peroxide (H2O2) | Not in source | A-Excellent (Dymatrix PFA/PTFE line recommended) | Not in source | Not in source | Yes - T-342/T-343 valve series not automatically appropriate for H2O2 just because it is inside a fab; require specific material evaluation. | 1
CMP Slurry | Not in source | Excellent (Falconics PFA flow controllers) | Not in source | Not in source | Yes - Slurry handling has high risk of check-valve shear/particle agglomeration; standard mag-drive pumps may fail without specific bearing selection (SSiC). | 1
Ultrapure water | A-Excellent (Inferred) | Not in source | Not in source | Not in source | No | 4
Sodium hydroxide (43%) | Not in source | A-Excellent (PTFE-coated diaphragm) | Not in source | Not in source | Yes - Equipment like the C1500N pump may use PVC suction tubing which leaches plasticizers despite being rated for caustic. | 4
Hydrofluoric Acid (HF) | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Sulfuric Acid | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Nitric Acid | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Hydrochloric Acid (HCl) | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Hydrogen Peroxide (H2O2) | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Sodium Hydroxide (NaOH) | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Potassium Hydroxide (KOH) | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Ammonium Hydroxide | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Phosphoric Acid | Not in source | Compatible (High) | Not in source | Not in source | No | 7
TMAH | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Isopropyl Alcohol (IPA) | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Acetic Acid | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Buffered Oxide Etch (BOE) | Not in source | Compatible (High) | Not in source | Not in source | No | 7
SC-1 / SC-2 Mixtures | Not in source | Compatible (High) | Not in source | Not in source | No | 7
CMP Slurry | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Calcium Chloride | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Ferric Chloride | Not in source | Compatible (High) | Not in source | Not in source | No | 7
Alum | Not in source | Compatible (High) | Not in source | Not in source | No | 7
General Corrosive Media (Mag-Drive Pump application) | Not in source | A-Excellent (Lining) | Not in source | Not in source | Yes - Dry run of PFA-lined pump caused SSiC bearing failure and casing damage. | 8
Hydrofluoric Acid (HF) | Not in source | Not in source | Not in source | Not in source | Yes. LibertyCES should be positioned as an equipment supplier (pumps, tanks, valves), not a chemical supplier. | 3
Sulfuric Acid | Not in source | Not in source | Not in source | Not in source | Yes. Requires double-wall tanks (SAFE-Tank) when secondary containment is absent. | 3
Hydrochloric Acid (HCl) | Not in source | Not in source | Not in source | Not in source | No | 3
Hydrogen Peroxide (H2O2) | Not in source | Not in source | Not in source | Not in source | No | 3
Caustic (NaOH) | Not in source | Not in source | Not in source | Not in source | No | 3
CMP Slurry | Not in source | Not in source | Not in source | Not in source | Yes. Slurry abrades moving parts and settles in dead legs. | 3
50% Sulfuric Acid | Not in source | Not in source | Not in source | Not in source | No | 9
45% Potassium Hydroxide | Not in source | Not in source | Not in source | Not in source | No | 9
Sodium Hypochlorite | Not in source | Not in source | Not in source | Not in source | Yes - susceptible to gas binding, suction problems, and material incompatibility issues. | 9
Magnetic-drive pump fluids (General) | Not in source | Not in source | Not in source | Not in source | Yes - assuming sealless means failure-proof; often missing dry-run protection for internal bearings. | 9
Sodium Hydroxide (43%) | Not in source | Not in source | Not in source | Not in source | No | 10, 11
Hydrofluoric Acid (HF) | Not in source | Not in source | Not in source | Not in source | No | 12, 13

## Source References
Index | Reference
1 | LIBERTYCES-FLOOD-SPRINT-MASTER-REFERENCE.md
2 | Mag Drive Pump Dry Run Failure — SSiC Bearing Damage ¦ LibertyCES
3 | LIBERTYCES-SEMICONDUCTOR-MANUFACTURER-OPPORTUNITY-MAP.md
4 | The Liberty Specs™ Podcast — Episodes, Transcripts & Engineering Breakdowns ¦ LibertyCES
5 | asahi-purad-uhp-pvdf-piping-system-engineering-diagram-libertyces.png
6 | asahi-purad-uhp-pvdf-piping-system-engineering-diagram-vertical-libertyces.png
7 | LIBERTYCES-SEMICONDUCTOR-KEYWORD-UNIVERSE.md
8 | ssic-bearing-fragments-pfa-lined-casing-dry-run-teardown-libertyces.png
9 | Module 2 — James Interview Specification Method
10 | blue-white-chem-feed-c1500n-diaphragm-pump-neutralization-skid-install-libertyces.webp
11 | blue-white-chem-feed-c1500n-diaphragm-pump-neutralization-skid-wide-angle-libertyces.webp
12 | finish-thompson-db-series-mag-drive-pump-hf-supply-semiconductor-facility-vertical-libertyces.png
13 | finish-thompson-db-series-mag-drive-pump-hf-supply-semiconductor-facility-vertical-libertyces.png