## Fillable TEMPLATE
SITE ID | LOCATIONAL IDENTIFIER | LEAD GOOSENECK CURRENTLY PRESENT? | CURRENT STREET SIDE SERVICE LINE MATERIAL | WAS STREET SIDE SERVICE LINE MATERIAL EVER PREVIOUSLY LEAD? | STREET SIDE SERVICE LINE SIZE | STREET SIDE SERVICE LINE INSTALL DATE | CURRENT PROPERTY SIDE SERVICE LINE MATERIAL | PROPERTY SIDE SERVICE LINE SIZE | PROPERTY SIDE SERVICE LINE INSTALL DATE | BUILDING TYPE | POINT-OF-ENTRY OR POINT-OF-USE TREATMENT PRESENT? | BUILDING PLUMBING MATERIAL 1 | BUILDING PLUMBING MATERIAL 2 | BUILDING PLUMBING MATERIAL INSTALL DATE | COMMENTS | BASIS OF STREET SIDE MATERIAL CLASSIFICATION | WAS STREET SIDE MATERIAL FIELD VERIFIED? | DATE OF STREET SIDE FIELD VERIFICATION, IF APPLICABLE | METHOD OF STREET SIDE FIELD VERIFICATION, IF APPLICABLE | BASIS OF PROPERTY SIDE MATERIAL CLASSIFICATION | WAS PROPERTY SIDE MATERIAL FIELD VERIFIED? | DATE OF PROPERTY SIDE FIELD VERIFICATION, IF APPLICABLE | METHOD OF PROPERTY SIDE FIELD VERIFICATION, IF APPLICABLE | NOTES ON BASIS OF MATERIAL CLASSIFICATION
103-0000-00 | 621 NORTH BIRON DRIVE (WOOD ROOM) | N | C | N |  | 1957 | C | 1" |  | NONRES | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/05/2024 | Visual insp during install or repair
104-0000-00 | 600 NORTH BIRON DRIVE (RECOVERY) | N | C | N |  | 2023 | C | 2" |  | NONRES | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 03/01/203 | Visual insp during install or repair
105-0000-00 | 621 NORTH BIRON DRIVE (WW NO. 26) | N | DI | N |  | 1957 | DI | 6" |  | NONRES | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 06/05/2024 | Visual insp during install or repair
106-0000-00 | 621 NORTH BIRON DRIVE (WAREHOUSE) (HIGH) | N | DI | N |  | 1957 | DI | 4" |  | NONRES | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/13/2024 | Visual insp during install or repair
106-0000-00 | 621 NORTH BIRON DRIVE (WAREHOUSE) (LOW) | N | DI | N |  | 1957 | DI | 4" |  | NONRES | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/13/2024 | Visual insp during install or repair
107-0000-00 | 621 NORTH BIRON DRIVE (MAIN MILL) | N | DI | N |  | 1957 | DI | 6" |  | NONRES | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 06/05/2024 | Visual insp during install or repair
110-0000-00 | 621 NORTH BIRON DRIVE (OFFICE) | N | C | N |  | 1957 | C | 1 1/2" |  | NONRES | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 01/28/2020 | Visual insp during install or repair
112-0000-00 | 300 NORTH BIRON DRIVE (SPARHAWK) | N | C | N |  | 1957 | C | 2" |  | NONRES | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 10/05/2023 | Visual insp at meter | Meter was removed and water shut off
119-0000-00 | 711 CENTER STREET | N | C | N |  | 1957 | G | 5/8" |  | SF | N | O |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/24/2024 | Cross-connection survey
120-0000-00 | 731 CENTER STREET | N | C | N |  | 1957 | G | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 08/14/2024 | Cross-connection survey
122-0000-00 | 741 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 08/26/2024 | Cross-connection survey
123-0000-00 | 751 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 07/03/2024 | Cross-connection survey
125-0000-00 | 811 CENTER STREET | N | C | N |  | 1957 | DI | 5/8" |  | SF | N | O |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/10/2024 | Cross-connection survey
127-0000-00 | 830 NORTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/31/2023 | Cross-connection survey
128-0000-00 | 821 CENTER STREET | N | C | N |  | 1957 | DI | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/29/2024 | Cross-connection survey
129-0000-00 | 831 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 09/13/2024 | Cross-connection survey
132-0000-00 | 851 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 08/15/2024 | Cross-connection survey
134-0000-00 | 861 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 06/18/2024 | Cross-connection survey
135-0000-00 | 911 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 08/01/2024 | Cross-connection survey
136-0000-00 | 941 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 03/16/2011 | Cross-connection survey
137-0000-00 | 951 CENTER STREET | N | C | N |  | 1957 | DI | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/16/2024 | Cross-connection survey
139-0000-00 | 971 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/20/2024 | Cross-connection survey
140-0000-00 | 981 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/10/2024 | Cross-connection survey
141-0000-00 | 1020 NORTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 06/05/2024 | Cross-connection survey
142-0000-00 | 1020 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 04/05/2023 | Cross-connection survey
143-0000-00 | 1060 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 04/05/2023 | Cross-connection survey
144-0000-00 | 1060 CENTER STREET (SHOP) | N | C | N |  |  | C | 5/8" |  | NONRES | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/15/2023 | Visual insp during install or repair
144-1000-00 | 1060 CENTER STREET (WAREHOUSE) | N | C | N |  | 2025 | C | 1" |  | NONRES | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 5/13/2025 | Cross-connection survey
145-0000-00 | 980 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 04/15/2024 | Cross-connection survey
146-0000-00 | 981 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/05/2023 | Cross-connection survey
147-0000-00 | 971 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 02/15/2023 | Cross-connection survey
148-0000-00 | 970 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 05/15/2023 | Cross-connection survey
149-0000-00 | 960 CENTER STREET | N | C | N |  | 1957 | P | 5/8" |  | SF | N | O | C |  |  | Installation record | N |  |  | Field inspection only | Y | 08/14/2024 | Cross-connection survey
150-0000-00 | 951 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 06/18/2024 | Cross-connection survey
151-0000-00 | 950 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 07/16/2024 | Cross-connection survey
152-0000-00 | 940 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/09/2023 | Cross-connection survey
153-0000-00 | 930 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 07/01/2024 | Cross-connection survey
153-0000-00 | 930 CENTER STREET (DEDUCT) | N | C | N |  |  | C | 1" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 07/01/2024 | Cross-connection survey
154-0000-00 | 941 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 07/16/2024 | Cross-connection survey
155-0000-00 | 920 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/17/2023 | Cross-connection survey
156-0000-00 | 931 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 08/02/2023 | Cross-connection survey
157-0000-00 | 911 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 09/30/2020 | Cross-connection survey
158-0000-00 | 910 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/15/2024 | Cross-connection survey
158-0000-00 | 910 CENTER STREET (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/15/2024 | Cross-connection survey
159-0000-00 | 860 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 06/26/2023 | Cross-connection survey
160-0000-00 | 861 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 03/28/2023 | Cross-connection survey
160-0000-00 | 861 WILLIAMS STREET (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 03/28/202 | Cross-connection survey
161-0000-00 | 850 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/31/2023 | Cross-connection survey
162-0000-00 | 841 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/03/2024 | Cross-connection survey
163-0000-00 | 831 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 07/15/2024 | Cross-connection survey
164-0000-00 | 830 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 10/06/2023 | Cross-connection survey
165-0000-00 | 810 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/03/2023 | Cross-connection survey
165-0000-00 | 810 CENTER STREET (DEDUCT) | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 04/04/2025 | Cross-connection survey
166-0000-00 | 821 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/07/2024 | Cross-connection survey
167-0000-00 | 760 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | L | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/12/2023 | Cross-connection survey
168-0000-00 | 761 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/17/2024 | Cross-connection survey
169-0000-00 | 741 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 06/26/2023 | Cross-connection survey
170-0000-00 | 750 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/27/2023 | Cross-connection survey
170-0000-00 | 750 CENTER STREET (DEDUCT) | N | C | N |  | 2024 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Installed after lead ban | Y | 10/04/2024 | Cross-connection survey
171-0000-00 | 740 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/23/2023 | Cross-connection survey
172-0000-00 | 720 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/15/2024 | Cross-connection survey
173-0000-00 | 731 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/29/2023 | Cross-connection survey
174-0000-00 | 721 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 08/14/2024 | Cross-connection survey
175-0000-00 | 710 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/25/2024 | Cross-connection survey
176-0000-00 | 670 CENTER STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 03/29/2023 | Cross-connection survey
177-0000-00 | 671 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 01/29/2024 | Cross-connection survey
178-0000-00 | 661 WILLIAMS STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/03/2024 | Cross-connection survey
180-0000-00 | 630 CENTER STREET | N | C | N |  | 1957 | C | 1" |  | NONRES | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 03/27/2023 | Visual insp during install or repair
183-0000-00 | 550 CENTER STREET | N | C | N |  | 1956 | C | 1" |  | SCH/DC | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 09/25/2024 | Visual insp during install or repair
183-0000-00 | 550 CENTER STREET (HIGH FLOW) | N | C | N |  | 1956 | C | 2" |  | SCH/DC | N | C | O |  |  | Field inspection only | N |  |  | Field inspection only | Y | 09/25/2024 | Visual insp during install or repair
183-0000-00 | 550 CENTER STREET (LOW FLOW) | N | C | N |  | 1956 | C | 2" |  | SCH/DC | N | C | O |  |  | Field inspection only | N |  |  | Field inspection only | Y | 09/25/2024 | Visual insp during install or repair
186-0000-00 | 140 BEAVER STREET | N | C | N |  | 1956 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/16/2024 | Cross-connection survey
187-0000-00 | 411 CENTER STREET | N | C | N |  | 1956 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 07/10/2024 | Cross-connection survey
188-0000-00 | 460 NORTH BIRON DRIVE (OLD C.U.) | N | C | N |  | 1956 | C | 1" |  | NONRES | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 09/26/2024 | Visual insp during install or repair
192-0000-00 | 281 SOUTH BIRON DRIVE (MILL HOME) | N | C | N |  | 1957 | C | 5/8" |  | SF | N | O |  |  |  | Installation record | N |  |  | Field inspection only | Y | 08/15/2024 | Cross-connection survey
193-0000-00 | 121 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 04/27/2023 | Cross-connection survey
194-0000-00 | 131 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/30/2023 | Cross-connection survey
195-0000-00 | 130 CRANBERRY STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 07/08/2024 | Cross-connection survey
196-0000-00 | 140 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/202/2024 | Cross-connection survey
197-0000-00 | 150 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/07/2024 | Cross-connection survey
197-0000-00 | 150 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/07/2024 | Cross-connection survey
198-0000-00 | 141 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 08/31/2023 | Cross-connection survey
199-0000-00 | 151 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 07/18/2024 | Cross-connection survey
200-0000-00 | 161 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/31/2023 | Cross-connection survey
201-0000-00 | 171 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/15/2023 | Cross-connection survey
201-0000-00 | 171 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C |  |  |  | Field inspection only | N |  |  | Field inspection only | Y | 05/15/2023 | Cross-connection survey
202-0000-00 | 221 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 02/22/2024 | Cross-connection survey
202-0000-00 | 221 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 02/13/2024 | Cross-connection survey
203-0000-00 | 231 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 04/06/2023 | Cross-connection survey
204-0000-00 | 241 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 06/14/2023 | Cross-connection survey
204-0000-00 | 241 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 06/14/2023 | Cross-connection survey
205-0000-00 | 251 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 04/05/2023 | Cross-connection survey
205-0000-00 | 251 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 04/05/2023 | Cross-connection survey
206-0000-00 | 271 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 06/18/2024 | Cross-connection survey
206-0000-00 | 271 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 06/18/2024 | Cross-connection survey
207-0000-00 | 260 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/06/2024 | Cross-connection survey
207-0000-00 | 260 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/06/2024 | Cross-connection survey
208-0000-00 | 250 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/03/2024 | Cross-connection survey
208-0000-00 | 250 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/03/2024 | Cross-connection survey
209-0000-00 | 240 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/06/2024 | Cross-connection survey
209-0000-00 | 240 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/06/2024 | Cross-connection survey
210-0000-00 | 230 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/08/2024 | Cross-connection survey
210-0000-00 | 230 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 1" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/08/2024 | Cross-connection survey
211-0000-00 | 220 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/02/2024 | Cross-connection survey
211-0000-00 | 220 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/02/2024 | Cross-connection survey
212-0000-00 | 170 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 03/30/2023 | Cross-connection survey
213-0000-00 | 171 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 07/24/2024 | Cross-connection survey
214-0000-00 | 221 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 06/05/2023 | Cross-connection survey
215-0000-00 | 231 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | CLS | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/21/2024 | Cross-connection survey
216-0000-00 | 241 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 06/01/2023 | Cross-connection survey
217-0000-00 | 251 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 07/31/2023 | Cross-connection survey
218-0000-00 | 261 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 08/14/2023 | Cross-connection survey
219-0000-00 | 320 BLUEBIRD LANE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 02/15/2024 | Cross-connection survey
220-0000-00 | 270 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/06/2024 | Cross-connection survey
220-0000-00 | 270 KAHOUN ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/06/2024 | Cross-connection survey
221-0000-00 | 260 KAHOUN ROAD | N | C | N |  | 1957 | C | 1" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 06/14/2023 | Cross-connection survey
221-0000-00 | 260 KAHOUN ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 06/14/2023 | Cross-connection survey
222-0000-00 | 240 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 09/13/2023 | Cross-connection survey
223-0000-00 | 220 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 08/05/2023 | Cross-connection survey
223-0000-00 | 220 KAHOUN ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 08/05/2024 | Cross-connection survey
224-0000-00 | 421 CARDINAL STREET | N | C | N |  | 1957 | P | 5/8" |  | SF | N | O | C |  |  | Installation record | N |  |  | Field inspection only | Y | 08/15/2024 | Cross-connection survey
225-0000-00 | 431 CARDINAL STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/12/2023 | Cross-connection survey
226-0000-00 | 450 CARDINAL STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/13/2024 | Cross-connection survey
227-0000-00 | 441 CARDINAL STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/22/2024 | Cross-connection survey
228-0000-00 | 451 CARDINAL STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 09/27/2023 | Cross-connection survey
229-0000-00 | 551 CARDINAL STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 04/22/2024 | Cross-connection survey
230-0000-00 | 550 CARDINAL STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 04/25/2023 | Cross-connection survey
231-0000-00 | 574 CARDINAL STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/11/2023 | Cross-connection survey
232-0000-00 | 565 CARDINAL STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 05/01/2023 | Cross-connection survey
233-0000-00 | 575 CARDINAL STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 09/07/2023 | Cross-connection survey
234-0000-00 | 585 CARDINAL STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 03/07/2024 | Cross-connection survey
235-0000-00 | 721 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 05/07/2024 | Cross-connection survey
236-0000-00 | 651 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/13/2024 | Cross-connection survey
237-0000-00 | 640 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/15/2024 | Cross-connection survey
238-0000-00 | 620 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/25/2023 | Cross-connection survey
239-0000-00 | 541 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/02/2024 | Cross-connection survey
240-0000-00 | 610 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 07/10/2024 | Cross-connection survey
241-0000-00 | 530 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/01/2023 | Cross-connection survey
242-0000-00 | 531 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/27/2023 | Cross-connection survey
245-0000-00 | 510 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/17/2023 | Cross-connection survey
246-0000-00 | 460 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/21/2023 | Cross-connection survey
247-0000-00 | 461 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 07/16/204 | Cross-connection survey
248-0000-00 | 453 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/29/2023 | Cross-connection survey
249-0000-00 | 421 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 05/16/2024 | Cross-connection survey
250-0000-00 | 411 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/07/2024 | Cross-connection survey
251-0000-00 | 410 ORIOLE LANE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 07/02/2024 | Cross-connection survey
252-0000-00 | 150 KAHOUN ROAD | N | C | N |  | 1957 | P | 5/8" |  | SF | N | O |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 05/05/2024 | Cross-connection survey
253-0000-00 | 410 CARDINAL STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/05/2023 | Cross-connection survey
254-0000-00 | 151 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 04/15/2024 | Cross-connection survey
255-0000-00 | 141 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Previous eval | N |  |  | Field inspection only | Y | 08/16/2024 | Cross-connection survey
256-0000-00 | 131 KAHOUN ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Previous eval | N |  |  | Field inspection only | Y | 03/13/2023 | Cross-connection survey
257-0000-00 | 371 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/29/2024 | Cross-connection survey
258-0000-00 | 120 CRANBERRY ROAD | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 07/10/2024 | Cross-connection survey
258-0000-00 | 120 CRANBERRY ROAD (DEDUCT) | N | C | N |  |  | C | 5/8" |  | SF | N | C | O |  |  | Previous eval | N |  |  | Field inspection only | Y | 07/10/2024 | Cross-connection survey
260-0000-00 | 1661 SOUTH BIRON DRIVE | N | DI | N | 6" | 1995 | DI | 6" |  | NONRES | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 10/01/2024 | Cross-connection survey | 2" meter
262-0000-00 | 1571 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C |  |  |  | SL repair/replace record | N |  |  | Field inspection only | Y | 09/15/2023 | Cross-connection survey
263-0000-00 | 1551 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C |  |  |  | SL repair/replace record | N |  |  | Field inspection only | Y | 04/26/2024 | Cross-connection survey
264-0000-00 | 1531 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C |  |  |  | SL repair/replace record | N |  |  | Field inspection only | Y | 05/30/2023 | Cross-connection survey
265-0000-00 | 1511 SOUTH BIRON DRIVE | N | P | N |  | 2015 | P | 5/8" |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | Field inspection only | Y | 04/24/2023 | Cross-connection survey
267-0000-00 | 1461 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C | O |  |  | SL repair/replace record | N |  |  | Field inspection only | Y | 06/20/2024 | Cross-connection survey
268-0000-00 | 1451 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C | O |  |  | SL repair/replace record | N |  |  | Field inspection only | Y | 08/01/2024 | Cross-connection survey
269-0000-00 | 1431 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/21/2024 | Cross-connection survey
270-0000-00 | 1411 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/10/2024 | Cross-connection survey
271-0000-00 | 1371 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 10/04/2023 | Cross-connection survey
272-0000-00 | 1361 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | CLS | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/21/2024 | Cross-connection survey
273-0000-00 | 1351 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/11/2023 | Cross-connection survey
274-0000-00 | 1341 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/29/2023 | Cross-connection survey
275-0000-00 | 1331 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/18/2024 | Cross-connection survey
276-0000-00 | 1241 SOUTH BIRON DRIVE | N | C | N |  | 2015 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/24/2023 | Cross-connection survey
277-0000-00 | 1231 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/30/2024 | Cross-connection survey
278-0000-00 | 1191 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/25/2023 | Cross-connection survey
279-0000-00 | 1252 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/02/2024 | Cross-connection survey
280-0000-00 | 1212 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/12/2023 | Cross-connection survey
281-0000-00 | 1192 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 10/03/2023 | Cross-connection survey
282-0000-00 | 1152 SOUTH BIRON DRIVE | N | C | N |  | 1957 | P | 5/8" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/16/2024 | Cross-connection survey
283-0000-00 | 1171 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/28/2024 | Cross-connection survey
284-0000-00 | 1151 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/12/2023 | Cross-connection survey
285-0000-00 | 1141 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/14/2023 | Cross-connection survey
286-0000-00 | 1131 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/03/2023 | Cross-connection survey
287-0000-00 | 1072 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/01/2023 | Cross-connection survey
288-0000-00 | 1122 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/02/2024 | Cross-connection survey
289-0000-00 | 1042 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/10/2023 | Cross-connection survey
290-0000-00 | 1061 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 10/12/2023 | Cross-connection survey
291-0000-00 | 1041 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/06/2024 | Cross-connection survey
292-0000-00 | 1030 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/04/2023 | Cross-connection survey
293-0000-00 | 1022 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/14/2024 | Cross-connection survey
294-0000-00 | 1010 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/25/2023 | Cross-connection survey
295-0000-00 | 1021 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/11/2023 | Cross-connection survey
296-0000-00 | 951 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/17/2024 | Cross-connection survey
297-0000-00 | 931 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/15/2023 | Cross-connection survey
298-0000-00 | 940 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/02/2024 | Cross-connection survey
299-0000-00 | 930 SOUTH BIRON DRIVE | N | C | N |  | 1957 | P | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/16/2024 | Cross-connection survey
300-0000-00 | 920 SOUTH BIRON DRIVE | N | C | N |  | 2008 | C | 5/8" |  | SF | N | C | O |  |  | SL repair/replace record | N | 02/01/2008 |  | Field inspection only | Y | 05/22/2024 | Cross-connection survey
301-0000-00 | 911 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/14/2024 | Cross-connection survey
302-0000-00 | 841 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/02/2023 | Cross-connection survey
303-0000-00 | 291 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/12/2023 | Cross-connection survey
304-0000-00 | 300 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 03/15/2024 | Cross-connection survey
305-0000-00 | 290 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 1" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 03/14/2024 | Cross-connection survey
306-0000-00 | 280 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/27/2023 | Cross-connection survey
307-0000-00 | 270 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 03/07/2024 | Cross-connection survey
308-0000-00 | 250 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/07/2023 | Cross-connection survey
309-0000-00 | 271 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/16/2024 | Cross-connection survey
310-0000-00 | 251 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/06/2023 | Cross-connection survey
311-0000-00 | 241 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/06/2023 | Cross-connection survey
312-0000-00 | 231 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 09/25/2023 | Cross-connection survey
313-0000-00 | 240 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/02/2023 | Cross-connection survey
314-0000-00 | 220 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/30/2023 | Cross-connection survey
315-0000-00 | 210 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 04/26/2024 | Cross-connection survey
316-0000-00 | 211 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 01/03/2024 | Cross-connection survey
317-0000-00 | 190 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | CLS |  |  | Installation record | N |  |  | Field inspection only | Y | 03/08/2024 | Cross-connection survey
318-0000-00 | 170 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 02/13/2024 | Cross-connection survey
319-0000-00 | 150 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/28/2024 | Cross-connection survey
320-0000-00 | 130 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 09/11/2023 | Cross-connection survey
321-0000-00 | 131 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 03/05/2024 | Cross-connection survey
322-0000-00 | 100 SHORE ACRES | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/21/2023 | Cross-connection survey
323-0000-00 | 121 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 04/26/2024 | Cross-connection survey
324-0000-00 | 110 SHORE ACRES DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/19/2024 | Cross-connection survey
325-0000-00 | 716 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/16/2024 | Cross-connection survey
326-0000-00 | 741 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/20/2024 | Cross-connection survey
327-0000-00 | 761 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 09/25/2023 | Cross-connection survey
328-0000-00 | 781 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/10/2024 | Cross-connection survey
329-0000-00 | 770 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 03/24/2023 | Cross-connection survey
330-0000-00 | 810 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/17/2024 | Cross-connection survey
331-0000-00 | 821 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/02/2023 | Cross-connection survey
332-0000-00 | 811 SOUTH BIRON DRIVE | N | C | N |  | 1957 | C | 5/8" |  | SF | N | O |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/11/2023 | Cross-connection survey
333-0000-00 | 671 JOHNSON PARKWAY | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 07/16/2024 | Cross-connection survey
334-0000-00 | 631 JOHNSON PARKWAY | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/01/2023 | Cross-connection survey
335-0000-00 | 611 JOHNSON PARKWAY | N | C | N |  | 1961 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/18/2024 | Cross-connection survey
336-0000-00 | 281 VAN SLATE STREET | N | C | N |  | 1961 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/18/2024 | Cross-connection survey
337-0000-00 | 620 JOHNSON PARKWAY | N | C | N |  | 1961 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/15/2023 | Cross-connection survey
338-0000-00 | 680 JOHNSON PARKWAY | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 04/01/2024 | Cross-connection survey
339-0000-00 | 121 EAGLE ROAD | N | C | N |  | 1994 | C | 5/8" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/24/2024 | Visual insp during install or repair
339-0000-00 | 121 EAGLE ROAD | N | C | N |  | 1994 | C | 1" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/27/2024 | Cross-connection survey
341-0000-00 | 150 EAGLE ROAD | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/25/2024 | Cross-connection survey
342-0000-00 | 180 EAGLE STREET | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/14/2023 | Cross-connection survey
343-0000-00 | 120 BUFFALO STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | O | C |  |  | SL repair/replace record | Y | 5/23/2024 |  | Field inspection only | Y | 06/26/2024 | Cross-connection survey
344-0000-00 | 131 BUFFALO STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 03/14/2024 | Cross-connection survey
345-0000-00 | 140 BUFFALO STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/10/2024 | Cross-connection survey
346-0000-00 | 140 BUFFALO STREET (NURSERY) | N | C | N |  | 1957 | C | 5/8" |  | NONRES | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/10/2024 | Visual insp during install or repair
347-0000-00 | 151 BUFFALO STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/18/2023 | Cross-connection survey
348-0000-00 | 161 BUFFALO STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 07/18/2024 | Cross-connection survey
349-0000-00 | 160 BUFFALO STREET | N | C | N |  | 1957 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 06/06/2023 | Cross-connection survey
350-0000-00 | 170 DEER STREET | N | C | N |  | 1960 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/23/2023 | Cross-connection survey
351-0000-00 | 160 DEER STREET | N | C | N |  | 1960 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 05/20/2024 | Cross-connection survey
352-0000-00 | 161 DEER STREET | N | C | N |  | 1960 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 06/07/2023 | Cross-connection survey
353-0000-00 | 151 DEER STREET | N | C | N |  | 1960 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/01/2023 | Cross-connection survey
354-0000-00 | 150 DEER STREET | N | C | N |  | 1960 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 06/12/2023 | Cross-connection survey
355-0000-00 | 140 DEER STREET | N | C | N |  | 1960 | C | 5/8" |  | SF | N | C | O |  |  | Installation record | N |  |  | Field inspection only | Y | 05/02/2024 | Cross-connection survey
356-0000-00 | 131 DEER STREET | N | C | N |  | 1960 | C | 5/8" |  | SF | N | C |  |  |  | Installation record | N |  |  | Field inspection only | Y | 07/10/2024 | Cross-connection survey
357-0000-00 | 240 EAGLE ROAD | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C | CLS |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/09/2024 | Cross-connection survey
358-0000-00 | 2910 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/17/2024 | Cross-connection survey
359-0000-00 | 2905 32ND STREET NORTH | N | C | N |  | 1990 | C | 1" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/28/2023 | Cross-connection survey
360-0000-00 | 2834 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/11/2023 | Cross-connection survey
361-0000-00 | 2821 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/12/2023 | Cross-connection survey
362-0000-00 | 2814 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/07/2024 | Cross-connection survey
363-0000-00 | 2824 32ND STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/11/2023 | Cross-connection survey
364-0000-00 | 2811 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/01/2023 | Cross-connection survey
365-0000-00 | 2720 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/24/2024 | Cross-connection survey
366-0000-00 | 2721 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/31/2023 | Cross-connection survey
367-0000-00 | 2710 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/24/2024 | Cross-connection survey
368-0000-00 | 2711 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | CLS |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/20/2024 | Cross-connection survey
369-0000-00 | 2621 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/24/2023 | Cross-connection survey
370-0000-00 | 2620 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/22/2024 | Cross-connection survey
371-0000-00 | 2610 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/23/2024 | Cross-connection survey
372-0000-00 | 2611 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/08/2023 | Cross-connection survey
373-0000-00 | 2570 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/14/2024 | Cross-connection survey
374-0000-00 | 2550 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/28/2024 | Cross-connection survey
375-0000-00 | 2540 32ND STREET NORTH | N | P | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/26/2024 | Cross-connection survey
376-0000-00 | 2535 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/14/2024 | Cross-connection survey
377-0000-00 | 2530 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/22/2024 | Cross-connection survey
378-0000-00 | 2520 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | CLS |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/15/2024 | Cross-connection survey
379-0000-00 | 2510 32ND STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | CLS |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/03/2024 | Cross-connection survey
380-0000-00 | 3211 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/25/2024 | Visual insp during install or repair
381-0000-00 | 3241 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/26/2024 | Visual insp during install or repair
382-0000-00 | 3311 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/26/2024 | Visual insp during install or repair
383-0000-00 | 3321 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/08/2023 | Cross-connection survey
384-0000-00 | 3311 A PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/07/2023 | Cross-connection survey
385-0000-00 | 3311 B&C PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | MF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/20/2024 | Cross-connection survey
386-0000-00 | 3310 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/09/2024 | Cross-connection survey
387-0000-00 | 3240 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/28/2023 | Cross-connection survey
388-0000-00 | 3230 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/29/2023 | Cross-connection survey
389-0000-00 | 3210 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/04/2024 | Cross-connection survey
390-0000-00 | 2160 32ND STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/20/2024 | Cross-connection survey
391-0000-00 | 3150 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/08/2023 | Cross-connection survey
392-0000-00 | 2151 32ND STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/30/2024 | Cross-connection survey
393-0000-00 | 2131 32ND STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/19/2024 | Cross-connection survey
394-0000-00 | 2121 32ND STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/26/2023 | Cross-connection survey
395-0000-00 | 2111 32ND STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/28/2024 | Cross-connection survey
396-0000-00 | 2041 32ND STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/01/2024 | Cross-connection survey
397-0000-00 | 2031 32ND STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/26/2024 | Cross-connection survey
398-0000-00 | 2021 32ND STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/20/2024 | Cross-connection survey
399-0000-00 | 1910 32ND STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/27/2024 | Visual insp during install or repair
400-0000-00 | 1930 32ND STREET NORTH | N | C | N |  | 1992 | C | 5/8" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/26/2024 | Visual insp during install or repair
401-0000-00 | 1911 32ND STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 11/14/2020 | Cross-connection survey
402-1000-00 | 1909 32ND STREET NORTH | N | P | N |  | 1994 | P | 1 1/2" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/22/2024 | Visual insp during install or repair
402-2000-00 | 1909 32ND STREET NORTH | N | P | N |  | 1994 | P | 1 1/2" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/22/2024 | Visual insp during install or repair
402-3000-00 | 1909 32ND STREET NORTH | N | P | N |  | 1994 | P | 2" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/22/2024 | Visual insp during install or repair
402-4000-00 | 1909 32ND STREET NORTH | N | P | N |  | 1994 | P | 2" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/22/2024 | Visual insp during install or repair
403-0000-00 | 3110 WOLOSEK AVENUE | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/15/2024 | Cross-connection survey
404-0000-00 | 2012 31ST STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/01/2024 | Cross-connection survey
405-0000-00 | 2012 31ST STREET NORTH (SHED) | N | C | N |  | 1994 | C | 5/8" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/01/2024 | Visual insp during install or repair
406-0000-00 | 1911 31ST STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/01/2024 | Cross-connection survey
407-0000-00 | 2041 31ST STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/22/2024 | Cross-connection survey
408-0000-00 | 2111 31ST STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/15/2024 | Cross-connection survey
409-0000-00 | 2110 31ST STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/13/2023 | Cross-connection survey
410-0000-00 | 2120 31ST STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/22/2024 | Cross-connection survey
411-0000-00 | 2131 31ST STREET NORTH | N | C | N |  | 1994 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/06/2023 | Cross-connection survey
412-0000-00 | 3030 PLOVER ROAD (GAS STATION) | N | C | N | 2" | 1992 | C | 1" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/27/2024 | Visual insp during install or repair
413-0000-00 | 3030 PLOVER ROAD (IRRIGATION) | N | C | N |  | 1992 | C | 1" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/27/2024 | Visual insp during install or repair
414-0000-00 | 3030 PLOVER ROAD (CAR WASH) | N | C | N | 2" | 1992 | C | 2" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/27/2024 | Visual insp during install or repair
415-0000-00 | 2930 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/29/2024 | Visual insp during install or repair
416-0000-00 | 2910 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/29/2024 | Cross-connection survey | Meter removed, water shut off
417-0000-00 | 2900 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/29/2024 | Cross-connection survey
418-0000-00 | 2840 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/29/2024 | Cross-connection survey | Meter removed, water shut off
419-0000-00 | 2830 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/26/2024 | Visual insp during install or repair
420-0000-00 | 2820 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/26/2011 | Visual insp during install or repair
421-0000-00 | 2710 PLOVER ROAD (HOUSE) | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 10/09/2024 | Cross-connection survey
422-0000-00 | 2710 PLOVER ROAD (HOTEL) | N | C | N |  | 1992 | C | 1" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/06/2024 | Visual insp at meter | Meter removed, water shut off
425-0000-00 | 2511 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/15/2024 | Cross-connection survey
426-0000-00 | 2551 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/01/2024 | Cross-connection survey
427-0000-00 | 2611 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/14/2023 | Cross-connection survey
428-0000-00 | 2831 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/27/2023 | Cross-connection survey
429-0000-00 | 2841 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/26/2024 | Visual insp during install or repair
430-0000-00 | 2911 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/30/2024 | Cross-connection survey
431-0000-00 | 2941 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/05/2024 | Cross-connection survey
432-0000-00 | 3011 PLOVER ROAD | N | C | N |  | 1992 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/14/2024 | Cross-connection survey
433-0000-00 | 3031 PLOVER ROAD | N | C | N |  | 1992 | C | 1" |  | NONRES | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/26/2024 | Visual insp during install or repair
434-0000-00 | 2320 30TH STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/01/2024 | Cross-connection survey
435-0000-00 | 2510 30TH STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/01/2024 | Cross-connection survey
436-0000-00 | 2421 30TH STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/10/2023 | Cross-connection survey
437-0000-00 | 2431 30TH STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/12/2023 | Cross-connection survey
438-0000-00 | 2520 30TH STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/05/2023 | Cross-connection survey
439-0000-00 | 3010 FOREST LANE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/17/2023 | Cross-connection survey
440-0000-00 | 2531 30TH STREET NORTH | N | C | Y |  | 1990 | C | 5/8" |  | SF | N | CLS | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/11/2024 | Cross-connection survey
441-0000-00 | 2930 FOREST LANE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/09/2023 | Cross-connection survey
442-0000-00 | 2920 FOREST LANE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/10/2024 | Cross-connection survey
443-0000-00 | 2910 FOREST LANE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/07/2024 | Cross-connection survey
444-0000-00 | 2911 FOREST LANE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/26/2024 | Cross-connection survey
445-0000-00 | 2931 FOREST LANE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/06/2023 | Cross-connection survey
446-0000-00 | 2941 FOREST LANE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/22/2024 | Cross-connection survey
447-0000-00 | 3021 FOREST LANE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/11/2023 | Cross-connection survey
448-0000-00 | 3031 FOREST LANE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/27/2023 | Cross-connection survey
449-0000-00 | 2535 31ST STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/13/2024 | Cross-connection survey
450-0000-00 | 2526 31ST STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/24/2024 | Cross-connection survey
451-0000-00 | 2525 31ST STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/01/2024 | Cross-connection survey
452-0000-00 | 3010 LARSON AVENUE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/25/2024 | Cross-connection survey
453-0000-00 | 3020 LARSON AVENUE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/17/2024 | Cross-connection survey
454-0000-00 | 2515 31ST STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | CLS |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 0/22/2024 | Cross-connection survey
455-0000-00 | 2331 31ST STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/15/2024 | Cross-connection survey
456-0000-00 | 2311 31ST STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/25/2024 | Cross-connection survey
457-0000-00 | 3151 PLOVER ROAD (Meter for billing) | N | P | N |  | 1992 | C | 3" |  | MF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/17/2024 | Cross-connection survey
458-0000-00 | 3121 LARSON AVENUE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/09/2024 | Cross-connection survey
459-0000-00 | 3111 FOREST LANE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/26/2024 | Cross-connection survey
460-0000-00 | 3121 FOREST LANE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/24/2023 | Cross-connection survey
461-0000-00 | 3120 WILDWOOD DRIVE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | CLS |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/24/2024 | Cross-connection survey
462-0000-00 | 3121 WILDWOOD DRIVE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/31/2023 | Cross-connection survey
463-0000-00 | 3110 WILDWOOD DRIVE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | CLS |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/01/2024 | Cross-connection survey
464-0000-00 | 3111 WILDWOOD DRIVE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 10/23/2023 | Cross-connection survey
465-0000-00 | 3030 WILDWOOD DRIVE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/02/2024 | Cross-connection survey
466-0000-00 | 3031 WILDWOOD DRIVE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/29/2023 | Cross-connection survey
467-0000-00 | 3021 WILDWOOD DRIVE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/16/2024 | Cross-connection survey
468-0000-00 | 3020 WILDWOOD DRIVE | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/15/2023 | Cross-connection survey
469-0000-00 | 2610 30TH STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/27/2023 | Cross-connection survey
470-0000-00 | 2620 30TH STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/27/2023 | Cross-connection survey
471-0000-00 | 2711 30TH STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/08/2024 | Cross-connection survey
472-0000-00 | 2710 30TH STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/10/2023 | Cross-connection survey
473-0000-00 | 2720 30TH STREET NORTH | N | P | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/04/2024 | Cross-connection survey
474-0000-00 | 2811 30TH STREET NORTH | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/11/2023 | Cross-connection survey
475-0000-00 | 3011 TANGLEWOOD TRAIL | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/26/2024 | Cross-connection survey
476-0000-00 | 3020 TANGLEWOOD TRAIL | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/21/2023 | Cross-connection survey
477-0000-00 | 3031 TANGLEWOOD TRAIL | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | CLS |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/05/2024 | Cross-connection survey
478-0000-00 | 3030 TANGLEWOOD TRAIL | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/12/2023 | Cross-connection survey
479-0000-00 | 3111 TANGLEWOOD TRAIL | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/31/2023 | Cross-connection survey
480-0000-00 | 3110 TANGLEWOOD TRAIL | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | CLS |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/23/2024 | Cross-connection survey
481-0000-00 | 3120 TANGLEWOOD TRAIL | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/28/2023 | Cross-connection survey
482-0000-00 | 3121 TANGLEWOOD TRAIL | N | C | N |  | 1990 | C | 5/8" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/10/2023 | Cross-connection survey
484-0000-00 | 740 SOUTH BIRON DRIVE | N | C | N |  | 2013 | C | 5/8" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/17/2024 | Visual insp during install or repair
485-0000-00 | 451 KAHOUN ROAD | N | DI | N |  | 1990 | C | 3" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/16/2024 | Visual insp at meter
489-0000-00 | 2136 32ND STREET NORTH | N | P | N |  | 1994 | P | 5/8" |  | NONRES | N | O |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/14/2024 | Visual insp during install or repair
490-0000-00 | 7351 INTERGRITY WAY | N | DI | N | 4" | 2015 | DI | 1" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/27/2023 | Visual insp during install or repair
490-0000-00 | 7351 INTERGRITY WAY (DEDUCT) | N | C | N |  | 2015 | DI | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/27/2023 | Visual insp during install or repair
491-0000-00 | 7375 INTERGIRTY WAY | N | DI | N | 4" | 2015 | DI | 1" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/27/2023 | Visual insp during install or repair
491-0000-00 | 7375 INTERGIRTY WAY (DEDUCT) | N | C | N |  | 2015 | DI | 5/8" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/27/2023 | Visual insp during install or repair
493-0000-00 | 1256 ANCHOR LANDING DRIVE | N | P | N |  | 2019 | P | 1 1/2" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/05/2020 | Visual insp during install or repair
494-0000-00 | 2923 NORTH BIRON DRIVE | N | C | N |  | 2019 | C | 1 1/2" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/18/2020 | Visual insp during install or repair
495-0000-00 | 1259 ANCHOR LANDING DRIVE | N | C | N |  | 2019 | C | 1 1/2" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/08/2020 | Visual insp during install or repair
496-0000-00 | 7474 INTERGRITY WAY | N | DI | N | 6" | 2015 | DI | 1" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/30/2021 | Visual insp during install or repair
496-0000-00 | 7474 INTERGRITY WAY | N | DI | N |  | 2015 | DI | 1" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/30/2021 | Visual insp during install or repair
496-0000-00 | 7474 INTERGRITY WAY | N | DI | N |  | 2023 | DI | 1" |  | NONRES | N | O | C |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/19/2024 | Visual insp during install or repair
497-0000-00 | 2815 PLOVER ROAD | N | P | N |  | 1992 | P | 1" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/26/2022 | Visual insp during install or repair
498-0000-00 | 1249 ANCHOR LANDING DRIVE | N | P | N |  | 2019 | P | 1" |  | NONRES | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/17/2022 | Visual insp during install or repair
600-0000-00 | 2711 SUNSET POINT DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/27/2020 | Cross-connection survey
602-0000-00 | 2561 SUNSET POINT DRIVE (MAIN HOUSE) | N | C | N |  | 2019 | C | 1" |  | SF | N | C | CLS |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/15/2021 | Cross-connection survey
602-0000-00 | 2561 SUNSET POINT DRIVE (GARAGE) | N | C | N |  | 2019 | C | 1" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/06/2020 | Cross-connection survey
603-0000-00 | 2551 SUNSET POINT DRIVE | N | C | N |  | 2019 | P | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/17/2020 | Cross-connection survey
604-0000-00 | 3122 WATERVIEW SRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/30/2020 | Cross-connection survey
605-0000-00 | 2631 SUNSET POINT DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/14/2025 | Cross-connection survey
606-0000-00 | 2641 SUNSET POINT DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/13/2020 | Cross-connection survey
607-0000-00 | 2300 NORTH BIRON DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/18/2020 | Cross-connection survey
608-0000-00 | 2270 NORTH BIRON DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/20/2020 | Cross-connection survey
609-0000-00 | 2341 NORTH BIRON DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/29/2020 | Cross-connection survey
610-0000-00 | 961 HUFFMAN ROAD | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/29/2020 | Cross-connection survey
611-0000-00 | 2330 NORTH BIRON DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/01/2020 | Cross-connection survey
612-0000-00 | 2351 NORTH BIRON DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/01/2020 | Cross-connection survey
613-0000-00 | 991 HUFFMAN ROAD | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/13/2020 | Cross-connection survey
614-0000-00 | 2260 NORTH BIRON DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/03/2020 | Cross-connection survey
615-0000-00 | 2250 NORTH BIRON DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/03/2020 | Cross-connection survey
616-0000-00 | 931 HUFFMAN ROAD | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/12/2020 | Cross-connection survey
617-0000-00 | 2170 NORTH BIRON DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 10/08/2020 | Cross-connection survey
618-0000-00 | 1311 BRIDGEVIEW DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/11/2021 | Cross-connection survey
619-0000-00 | 1129 BRIDGEWATER DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/02/2021 | Cross-connection survey
619-0000-00 | 1129 BRIDGEWATER DRIVE (DEDUCT) | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/18/2022 | Cross-connection survey
620-0000-00 | 1131 BRIDGEWATER DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/15/2021 | Cross-connection survey
620-0000-00 | 1131 BRIDGEWATER DRIVE (DEDUCT) | N | P | N |  | 2019 | P | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/02/2022 | Cross-connection survey
621-0000-00 | 2461 SUNSET POINT DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 05/27/2022 | Cross-connection survey
622-0000-00 | 3101 WATERVIEW DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 09/30/2021 | Cross-connection survey
622-0000-00 | 3101 WATERVIEW DRIVE (DEDUCT) | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/02/2022 | Cross-connection survey
623-0000-00 | 2531 SUNSET POINT DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 10/04/2021 | Cross-connection survey
624-0000-00 | 2451 SUNSET POINT DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 10/20/2021 | Cross-connection survey
625-0000-00 | 1243 BRIDGEVIEW DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 11/09/2021 | Cross-connection survey
626-0000-00 | 1339 BRIDGEVIEW DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 12/07/2021 | Cross-connection survey
627-0000-00 | 3081 WATERVIEW DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 12/22/2021 | Cross-connection survey
627-0000-00 | 3081 WATERVIEW DRIVE (DEDUCT) | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 10/06/2022 | Cross-connection survey
628-0000-00 | 1168 BRIDGEWATER DRIVE | N | P | N |  | 2019 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 03/31/2022 | Cross-connection survey
628-0000-00 | 1168 BRIDGEWATER DRIVE (DEDUCT) | N | P | N |  | 2019 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/18/2022 | Cross-connection survey
629-0000-00 | 1184 BRIDGEWATER DRIVE | N | P | N |  | 2019 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 06/08/2022 | Cross-connection survey
629-0000-00 | 1184 BRIDGEWATER DRIVE (DEDUCT) | N | P | N |  | 2019 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/02/2022 | Cross-connection survey
630-0000-00 | 3102 WATERVIEW DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 08/19/2022 | Cross-connection survey
631-0000-00 | 3065 WATERVIEW DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 12/08/2022 | Cross-connection survey
631-0000-00 | 3065 WATERVIEW DRIVE (DEDUCT) | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 07/06/2023 | Cross-connection survey
632-0000-00 | 3155 WATERVIEW DRIVE | N | P | N |  | 2019 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/11/2023 | Cross-connection survey
632-0000-00 | 3155 WATERVIEW DRIVE (DEDUCT) | N | P | N |  | 2019 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 01/11/2023 | Cross-connection survey
633-0000-00 | 2240 NORTH BIRON DRIVE | N | C | N |  | 2019 | C | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/27/2023 | Cross-connection survey
634-0000-00 | 2431 NORTH BIRON DRIVE | [14 empty] | Installed after lead ban |  |  |  | Other - describe in notes |  |  |  | No property side lateral or meter installed yet
635-0000-00 | 2714 NORTH BIRON DRIVE | N | C | N |  | 2023 | P | 1" |  | SF | N | C |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 12/22/2023 | Cross-connection survey
635-0000-00 | 2714 NORTH BIRON DRIVE (DEDUCT) | N | C | N |  | 2023 | P | 1" |  | SF | N | C | O |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 04/30/2024 | Cross-connection survey
636-0000-00 | 2460 NORTH BIRON DRIVE | N | P | N |  | 2024 | P | 1" |  | SF | N | C | O |  |  | Installed after lead ban | Y | 10/02/2024 |  | Field inspection only | Y | 10/02/2024 | Cross-connection survey
637-0000-00 | 1075 RED HAWK COURT | N | P | N |  | 2024 | P | 1" |  | SF | N | C | O |  |  | Installed after lead ban | Y | 4/25/2024 |  | Field inspection only | Y | 09/05/2024 | Cross-connection survey
637-0000-00 | 1075 RED HAWK COURT (DEDUCT) | N | P | N |  | 2024 | P | 1" |  | SF | N | C | O |  |  | Installed after lead ban | Y | 4/25/2024 |  | Field inspection only | Y | 04/25/2024 | Cross-connection survey
638-0000-00 | 1101 HUFFMAN ROAD | N | P | N |  | 2024 | P | 1" |  | SF | N | C | O |  |  | Installed after lead ban | Y | 9/17/2024 |  | Field inspection only | Y | 01/27/2025 | Cross-connection survey
639-0000-00 | 1032 RED HAWK COURT | N | P | N |  | 2024 | P | 1" |  | SF | N | C | O |  |  | Installed after lead ban | Y | 5/15/2024 |  | Field inspection only | Y | 12/09/2024 | Cross-connection survey
639-0000-00 | 1032 RED HAWK COURT (DEDUCT) | N | P | N |  | 2024 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | N | 5/15/2024 |  | Field inspection only | N | 10/10/2025 | Cross-connection survey
640-0000-00 | 4021 NORTH 72ND STREET | N | P | N |  | 2024 | P | 1" |  | NONRES | N | C | O |  |  | Installed after lead ban | Y | 11/01/2024 |  | Field inspection only | Y | 5/07/2025 | Cross-connection survey
641-0000-00 | 3249 WATERVIEW DRIVE | N | P | N |  | 2024 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | Y | 10/03/204 |  | Field inspection only | Y | 02/21/2025 | Cross-connection survey
641-0000-00 | 3249 WATERVIEW DRIVE (DEDUCT) | N | P | N |  | 2024 | P | 1" |  | OTH | N | O |  |  |  | Installed after lead ban | Y | 10/03/2024 |  | Field inspection only | Y | 02/21/2025 | Cross-connection survey
642-0000-00 | 3251 WATERVIEW DRIVE | N | P | N |  | 2024 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | Y | 10/03/2024 |  | Field inspection only | Y | 02/21/2025 | Cross-connection survey
642-0000-00 | 3251 WATERVIEW DRIVE (DEDUCT) | N | P | N |  | 2024 | P | 1" |  | OTH | N | O |  |  |  | Installed after lead ban | Y | 10/03/2024 |  | Field inspection only | Y | 02/21/2025 | Cross-connection survey
643-0000-00 | 2541 SUNSET POINT DRIVE | N | P | N |  | 2019 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | Y | 11/28/2024 |  | Field inspection only | Y | 05/26/2025 | Cross-connection survey
644-0000-00 | HUFFMAN ROAD | N | P | N |  | 2019 |  |  |  | SF | [5 empty] | Installed after lead ban | N | [6 empty] | No property side lateral or meter installed yet
645-0000-00 | 937 HUFFMAN ROAD | N | P | N |  | 2019 | P | 1" |  | SF | [5 empty] | Installed after lead ban | N | 7/31/2025 |  | SL repair/replace record | Y | 2/13/2026 | Cross-connection survey
646-0000-00 | 3253 WATERVIEW DRIVE | N | P | N |  | 2024 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | SL repair/replace record | N | 09/25/2025 | Cross-connection survey
647-0000-00 | 3255 WATERVIEW DRIVE | N | P | N |  | 2024 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | SL repair/replace record | N | 09/25/2025 | Cross-connection survey
648-0000-00 | 1238 BRIDGEVIEW DRIVE | N | P | N |  | 2019 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/06/2025 | Cross-connection survey
649-0000-00 | 3200 WATERVIEW DRIVE | N | P | N |  | 2019 | P | 1" |  | SF | N | O |  |  |  | Installed after lead ban | N |  |  | Field inspection only | Y | 02/06/2025 | Cross-connection survey
| 3151 PLOVER ROAD (HOUSE) | N | P | N |  | 2015 | P |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT A) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  | Vacant Lot | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT B) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT C) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 1) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 2) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  | Vacant Lot | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 3) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 4) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 5) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  | Vacant Lot | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 6) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 7) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 8) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  | Vacant Lot | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 9) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 10) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 11) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 12) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 13) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 14) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 15) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
| 3151 PLOVER ROAD (LOT 16) | N | P | N |  | 2015 | G |  |  | SF | N | O |  |  |  | SL repair/replace record | N |  |  | SL repair/replace record | N |  |  | Inventory done by project manager of property
Note on B1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Required field for all service connections. Every connection must have a unique identifier.
Note on D1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Required field for all service connections.
Note on E1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Required field for all service connections.
Note on H1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Required field for all service connections.
Note on Q1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Required field for all service connections.
Note on U1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Required field for all service connections.

## Field Descriptions
Click here to open USEPA 2022 Guidance for Developing and Maintaining a Service Line Inventory
Note: Field names that are shadednavy are required for every service connection. Field names shaded blue are recommended, optional, or only required under certain conditions. See field descriptions for more information.
| Column | Description
A | SITE ID | PWS that do not wish to report site addresses to the department in column B can use this column to “link” their materials inventory table to a separate service address table for their own use. This column is optional, however, it strongly recommended that PWS enter the site ID for locations that are lead and copper monitoring sites in this column.
B | LOCATION IDENTIFIER | The location identifier can be the site address, however if there is more than one service connection at a given address, it must include additional detail. If the PWS does not wish to report addresses to the department it can be a block, intersection or landmark. This column is required per sub-subparagraph §141.84 (a)(8)(i) of the LCRR which requires that a location identifier be associated with each service line.
| Column | Description | Answer options |  | Answer Option Descriptions
C | GOOSENECK CURRENTLY PRESENT? | Is there a gooseneck, lead connector or pigtail present? PWS are required to track this information, if known. However, PWS are not required to conduct investigations to determine if a gooseneck is present. | Y | YES - WITH CERTAINTY
|  |  | N | NO - WITH CERTAINTY
|  |  | UNK | NOT KNOWN WITH CERTAINTY
D | CURRENT STREET SIDE SERVICE LINE MATERIAL | Service line pipe material, from the water main to curb stop. | L | CONFIRMED LEAD
|  |  | C | CONFIRMED COPPER
|  |  | G | CONFIRMED GALVANIZED
|  |  | P | CONFIRMED PLASTIC
|  |  | DI | CONFIRMED DUCTILE IRON
|  |  | CI-L | CONFIRMED LINED CAST IRON
|  |  | CI-U | CONFIRMED UNLINED CAST IRON
|  |  | UNK-LG | UNKNOWN - MAY CONTAIN LEAD OR GALVANIZED
|  |  | UNK-NOLG | UNKNOWN - DEFINITELY DOES NOT CONTAIN LEAD OR GALVANIZED
E | WAS STREET SIDE SERVICE LINE MATERIAL EVER PREVIOUSLY LEAD? | Was the service line ever previously lead? | Y | YES – SERVICE LINE WAS PREVIOUSLY LEAD
|  |  | N | NO – KNOWS WITH CERTAINTY THAT SERVICE LINE MATERIAL WAS NEVER PREVIOUSLY LEAD
|  |  | UNK | NOT KNOWN WITH CERTAINTY IF MATERIAL WAS EVER PREVIOUSLY LEAD
| Column | Description
F | STREET SIDE SERVICE LINE SIZE | Service line pipe diameter in inches, from the water main to curb stop. This information is useful as a screening tool as most lead service lines are 2 inches or less in diameter. Furthermore, PWSs are required to report service line size to the PSC for their annual report. This column may also be used by PWS that wish to track information required by both agencies in a single document. Column F is optional.
G | STREET SIDE SERVICE LINE INSTALL DATE | The four-digit year that the utility-side service was installed (i.e. 1974). If the exact year is not known, enter the decade (i.e. enter 1970 for any year in the 1970s) Althought this information is not required, it can be used as a screening tool to determine if the service line was installed before or after the lead ban (1986). Column G is optional.
H | CURRENT PROPERTY SIDE SERVICE LINE MATERIAL | Service line pipe material, from the curb stop to water meter. See Row D for answer options.
I | PROPERTY SIDE SERVICE LINE SIZE1 | Service line pipe diameter, in inches, from the curb stop to water meter. This information is useful as a screening tool as most lead service lines are 2 inches or less in diameter. Furthermore, PWS are required to report service line size to the PSC for their annual report. This column may also be used by PWS that wish to track information required by both agencies in a single document. Column I is optional.
J | PROPERTY SIDE SERVICE LINE INSTALL DATE | If the exact year is not known, enter the decade (i.e. enter 1970 for any year in in the 1970s). This information it can be used as a screening tool to determine if the service line was installed before or after the lead ban (1986). Column J is optional.
| Column | Description | Answer options |  | Answer Option Descriptions
K | BUILDING TYPE | The type of structure that is served water by the service connection. At a minimum, the PWS must identify the connection either SF, MF or NONRES. | SF | SINGLE-FAMILY RESIDENTIAL
|  |  | MF | MULTI-FAMILY RESIDENTIAL
|  |  | SCH/CC | SCHOOL OR CHILD CARE
This category may be used by the PWSs to track locations that must be monitored under §141.92.
|  |  | RES/CC | RESIDENTIAL & IN-HOME CHILD CARE
This category may be used by the PWSs to track locations that must be monitored under §141.92.
|  |  | NONRES | NONRESIDENTIAL ONLY, NO SCHOOL OR CHILD CARE.
|  |  | MIX | MIXED RESIDENTIAL & NONRESIDENTIAL, NO SCHOOL OR CHILD CARE.
|  |  | O | OTHER
L | POINT-OF-ENTRY OR POINT-OF-USE TREATMENT PRESENT? | Is the cold-water kitchen tap treated by point-of-entry or point-of-use softening, filter or other treatment? Column L is optional. | Y | YES - the sample tap is treated by a point of use or point of entry softener or filter
|  |  | N | NO - the sample tap is not treated by a point of use or point of entry softener or filter
|  |  | UNK | Presence or absence of POU and POE is UNKNOWN
M | BUILDING PLUMBING MATERIAL 1 | The type of plumbing materials inside the structure that water is deliver to. If there is more than one known plumbing material type, select the second material type in column N. Columns M and N are optional. | CLS | Copper with lead solder
|  |  | C | Copper, no lead solder
N | BUILDING PLUMBING MATERIAL 2 |  | O | Other material that is not copper, or copper with lead solder
|  |  | UNK | Unknown
| Column | Description
O | BUILDING PLUMBING MATERIAL INSTALL DATE | The four-digit year that the interior premise plumbing was installed. If the exact year is not known, you may enter the decade if the decade is not the 1980s. If the decade is the 1980s, you may enter one of the following: 1983-1984, <1983 or >1984. Column O is optional.
P | COMMENTS | Use this column information to enter any other information that the PWS finds helpful to them or any information they wish to share with the department. Column P is optional.
| Column | Description | Answer options |  | Answer Option Descriptions (Chapter 4 of EPA inventory guidance )
Q | BASIS OF STREET SIDE MATERIAL CLASSIFICATION | Use the drop-down menu to select the method used for materials classification. If the method you used is not one of the options, select other and describe the basis for classification in Column Y- Notes on materials classification. | Previous eval |  | Previous Materials Evaluation
|  |  | Installation record |  | Installation record (e.g., tap card)
|  |  | Installed after lead ban |  | Installation date after lead ban (1986)
|  |  | Diameter > 2 inches |  | Service line diameter is > 2 inches
|  |  | SL repair/replace record |  | Service line repair or replacement record
|  |  | Water sampling only |  | Water sampling only with no records
|  |  | Field inspection only |  | Field inspection only with no records
|  |  | Other - describe in notes |  | Other - if other is selected describe the basis for material classification in the Notes Column Y.
| Column | Description
R | WAS STREET SIDE MATERIAL FIELD VERIFIED? | Was the street side material field verified? Select "Y" for "Yes" or "N" for "No".
S | DATE OF STREET SIDE FIELD VERIFICATION, IF APPLICABLE | If you selected "Yes" in column R, enter the date (DD/MM/YYYY) or four-digit year that the material was field verified. This field is only required if "Yes" was selected in Column R.
| Column | Description | Answer options |  | Answer Option Descriptions (Chapter 5 of EPA inventory guidance)
T | METHOD OF STREET SIDE FIELD VERIFICATION, IF APPLICABLE | If PWS selected "Yes" in column R, select the method used for field verification. If the method you used is not one of the options, select other and describe the basis for classification in Column Y. This field is only required if "Yes" was selected in Column R. | Customer self id |  | Customer self-identification
|  |  | CCTV - internal |  | CCTV investigation at curb stop - internal
|  |  | CCTV - external |  | CCTV investigation at curb stop - external
|  |  | Mech excav |  | Mechanical excavation at one location
|  |  | Visual insp at meter |  | Visual inspection at the meter pit
|  |  | Visual insp during install or repair |  | Visual inspection during construction or repair
|  |  | Cross connection survey |  | Cross Connection survey
|  |  | Other |  | Other - describe in Notes Column Y
| Column | Description
U | BASIS OF PROPERTY SIDE MATERIAL CLASSIFICATION | Use the drop-down menu to select the method used for materials classification. If the method you used is not one of the options, select other and describe the basis for classification in Column Y. See Column Q for a description of and an explanation of answer options.
V | WAS PROPERTY SIDE MATERIAL FIELD VERIFIED? | Was the street side material field verified? Select "Y" for "Yes" or "N" for "No".
W | DATE OF PROPERTY SIDE FIELD VERIFICATION, IF APPLICABLE | If PWS selected "Yes" in column R, select the method used for field verification. If the method you used is not one of the options, select other and describe the basis for classification in Column Y. This field is only required if "Yes" was selected in Column V.
X | METHOD OF PROPERTY SIDE FIELD VERIFICATION, IF APPLICABLE | If you selected "Yes" in column V, select the method used for field verification. See column T for an explanation of answer options. This field is only required if "Yes" was selected in Column V.
Y | NOTES MATERIAL CLASSIFICATION | If PWS selected "other" in Columns Q, T, U or X, describe the basis for classification or field verification here. This field is only required if "other" was selected in column Q, T, U and/or X.

## FAQs
Why do Public Water Systems (PWSs) need to provide this information?
Under Section §141.84 of the Lead and Copper Rule Revision (LCRR), all community Public Water Systems (PWS) “must develop an inventory to identify the materials of service lines connected to the public water distribution system. The inventory must include all service lines connected to the public water distribution system regardless of ownership status.”
What specifically does the LCRR materials inventory require (columns D, E and H)?
Subparagraph §141.84 (a) (4) of the LCRR states that “each service line, or portion of the service line where ownership is split, must be categorized” as belonging to one of the following groups: lead; non-lead; lead status unknown; or galvanized requiring replacement. The information provided in columns D, E and H of the materials spreadsheet will enable the department to correctly assign every service line or portion thereof to one of these four categories.
What is the Site ID (column A)? Is this required?
The PWS can use this column to identify the site ID of lead and copper monitoring sites. For all other locations, the site ID is optional. PWSs that do not wish to report site addresses to the department in column B may want to use this column to “link” their materials inventory table to a separate service address table for their own use.
What is a locational identifier (column B)?
Sub-subparagraph §141.84 (a)(8)(i) of the LCRR requires a location identifier associated with each service line. The locational identifier can be the site address, or it can be a block, intersection or landmark.
The LCRR defines some categories of materials, such as ‘lead status’ and ‘galvanized downstream of lead’ differently in different sections of the rule. Thus, the spreadsheet is intended to be a simple and easy way for municipal PWSs to collect and report the information required now and in the future. The DNR will use the materials inventory data collected by the water system to categorize each of their service connections appropriately under each section of the LCRR.
Gooseneck, pigtail or lead connector present? (Column C)
Building Type (Column K)
Point-of-Use or Point-of-Entry Treatment Present? (Column L)
Building plumbing materials and plumbing install date (Columns M, N and O)
Property side service line material (Column H)
Property side service line size (Column I)
Property side service line install date (Column J)
Current street side service line material (Column D)
Was street side service line ever previously lead? (Column E)
Street side service line size (Column F)
Street side service line install date (Column G)
Materials Inventory Template For Drinking Water Systems Under The Lead And Copper Rule Revisions
Why do PWSs need to indicate whether a gooseneck is present (column C)?
Paragraph §141.86 (a) of the LCRR directs every public water system to “identify a pool of targeted sampling sites based on the service line inventory.” However, the materials information needed to categorize service lines in accordance with §141.84 alone is insufficient to identify these targeted sampling sites. Specifically, as per LCRR sub-paragraph §141.86 (a) (5), Tier 3 sampling sites include both single-family structures served by galvanized lines located downstream of a lead service line (i.e. confirmed galvanized requiring replacement) or downstream of a lead gooseneck, pigtail or connector.
Why do PWSs need to indicate whether a service line that is not currently lead was ever previously lead (column E)?
The materials history of the upstream utility service line is needed to correctly categorize customer-side galvanized service lines as either non-lead or galvanized requiring replacement under the LCRR. Sub-subparagraph §141.84 (a)(4)(ii) of the LCRR requires that public water systems identify locations where a galvanized service line “is or was at any time downstream of a lead service line” or “lead status unknown” service line as “galvanized requiring replacement”. If a water system knows with certainty that the utility side of a service line is not now, and never has previously been lead, then the downstream customer-side galvanized service line is identified as “non-lead”. If a PWS does not know this with certainty, the material is categorized as “galvanized requiring replacement.” However, as per paragraph §141.86 (a), galvanized service lines currently or formerly downstream of a lead gooseneck, pigtail, or connector are not identified as galvanized requiring replacement.
Are PWSs required to track the interior premise plumbing materials and install date at every service location in their system (columns M, N and O)?
This information is only required for service locations that are potential compliance sampling sites. If the PWS has at least as many Tier 1, Tier 2 and/or Tier 3 sampling sites as their required number of monitoring sites, then they are not required to track this information at this time. However, the PWS will be required to collect this information in the future, once all of their lead service lines and galvanized lines requiring replacement are removed. It is recommended that PWS collect this information on an ongoing basis whenever they are inside structures, as part of their normal operations.
Are PWSs required to track whether there is a point-of-entry (POE) or point-of-use (POU) treatment device at every service location (column L)?
This information is only required for service connections that are potential monitoring sites. Sub-paragraph §141.86 (1) of the LCRR states that “Sampling sites may not include sites with installed point-of-entry (POE) treatment devices and taps used at sampling sites may not have point-of-use (POU) devices designed to remove inorganic contaminants…” However, the department recommends that PWSs collect this information concurrently with premise plumbing materials at a given residence, so that PWSs don”t need to revisit residences that become potential monitoring sites once their lead and galvanized lines are removed.
Are PWSs required to use the DNR template?
No, PWSs are not required to use the DNR template for their materials inventory. However, PWSs that track their drinking water distribution system materials using a different method should provide all of the information requested in the template.
Do Municipal PWSs have to report this information to the DNR and PSC both?
Due to differences in the frequency and timing of reporting and the type of information reported, municipal public water systems will continue to report service line information annually to the Public Service Commission (W-22 and W-29) for the foreseeable future. However, the DNR and PSC are in discussions about how they can collaborate to minimize the amount of similar reporting to multiple agencies after the LCRR compliance date.
Materials Inventory Template For Drinking Water Systems Under The Lead And Copper Rule Revisions

## ANSWER LIST (hidden)
[7 empty] | Previous eval | Customer self id
Y | B | SF | L | L | 3/8" | Y | Installation record | CCTV - internal
N | K | MF | C | C | 1/2" | N | Installed after lead ban | CCTV - external
| A | SCH/DC | G | CLS | 5/8" | UNK | Diameter > 2 inches | Mech excav
|  | RES/CC | P | O | 3/4" |  | SL repair/replace record | Visual insp at meter
|  | NONRES | DI | UNK | 1" |  | Water sampling only | Visual insp during install or repair
|  | MIX | CI-L |  | 1 1/4" |  | Field inspection only | Cross-connection survey
|  | OTH | CI-U |  | 1 1/2" |  | Other - describe in notes | Other - describe in notes
|  |  | UNK-LG |  | 1 3/4"
|  |  | UNK-NOLG |  | 2"
3"
4"
6"
8"
10"
12"
14"
16"
OTH