Contributors

| John Pearson | ISO-NE |
| --- | --- |
| Brad Marszalkowski | ISO-NE |
| David Forrest | EPRI Consultant |
| Ryan Quint | NERC |
| David Conroy | Joint Utilities of New York-CMP |
| Herb Schrayshuen | Power Advisors on behalf of NextEra |
| James Grant | NYISO |
| Brian Robinson | Utility Services |
| Dan Kopin | Utility Services |
| Michael Jones | National Grid (RSC Co-Vice Chair) |
| Quintin Lee | Eversource (RSC Co-Vice Chair) |
| Benjamin Loebick | United Illuminating |
| Guy V. Zito | NPCC (RSC Chair) |

NPCC also thanks the Regional Standards Committee and the state and provincial regulatory authorities who provided guidance and information during the development of this document.

Revision History

| Version | Date | Action | Change Tracking (New, Errata or Revisions) |
| --- | --- | --- | --- |
| 1 | 8/19/19 | Effective Date | New |
| 2 | X/XX/XX | RSC and Subgroup developed revisions | Revisions, add AGIR and various enhancements and clarifications and Appendices |

Contents

Executive Summary	4

Introduction and Objective	5

NPCC DER Impact Reporting	7

DER BPS Impact Considerations	7

NPCC Interconnection Guidance	8

Voltage Response	10

Frequency Support	11

Reconnection to the Utility System	12

Inverters	12

Certification per UL 1741 SA as grid support utility interactive inverters	13

Minimum Protective Functions	14

Metering	15

Power Quality	17

Power Factor	17

Islanding	17

Automatic Underfrequency Load Shedding (UFLS) Programs	17

Effective Grounding for DER	18

Resource Adequacy	18

Energy Storage Systems for DER	19

System control and Data Acquisition (SCADA) and Communications	20

DER Recommendations	20

Appendix A, NPCC DER Impact Reporting Form and Process	22

Appendix B, NPCC Areas- Comparisons	24

Appendix C – SPIDER Working Group Reliability Guidelines & Activities	25

Appendix D, NPCC Reliability Principles	28

Appendix E, State and Provincial AGIR Information	31

New York State	31

New England, by State	31

Province of Quebec (some references are only available in French)	34

Province of Ontario	37

Province of New Brunswick	38

Appendix F, ISO New England	39

Appendix G, State Renewable and Green Energy Requirements	41

# Executive Summary

The Northeast Power Coordinating Council, Inc. (NPCC) is responsible for promoting and enhancing the reliability of the International, interconnected Bulk Power System in Northeastern North America.

Development of this document was initiated by the NPCC Board of Directors to provide Regional guidance and information for voluntary use by NPCC Members and stakeholders. The guidance provided herein identifies potential reliability risks to the BPS, recommendations to mitigate them, and also identifies opportunities to leverage the operational characteristics of DER to enhance reliability and resilience of the NPCC Bulk Power System (BPS).  Helpful links to other resources are provided throughout the document.

As Distributed Energy Resources (DER) installed on the distribution system, continue to replace traditional industry generation resources the resource fuel mix and operational characteristics of the system will change.  DER will necessitate changes to how the system is planned and operated.  The North American Electric Reliability Corporation (NERC) Reliability Standards are not applicable to equipment on the distribution systems unless such equipment has a direct impact on the “reliable operation” of the BPS, such as Automatic Underfrequency Load Shedding (UFLS). However, as penetration of DER increases, planning and operating assessments used to assure reliable operation of the BPS will need to accurately represent how DER interacts with the BPS.

NPCC recognizes that national efforts are underway at the NERC level to define DER and address some aspects related to planning and modeling.  Appendix C outlines some specific reliability activities related to DER which are either developed, or in the process of being developed, by the NERC System Planning Impacts Working Group (SPIDER), along with links to some of their documents. NPCC and its members have been engaged in efforts at the national level and are leading efforts to address outstanding issues within the scope of those groups and provide expertise.  With the understanding of what efforts are underway nationally, NPCC can coordinate and fill a vital role in identifying additional areas where the Region may provide information and services to promote reliable deployment of DER.  Specifically, in the area of coordination with State and Provincial Government Regulatory Authorities, and distribution utilities.  Also, opportunities exist in the areas of obtaining data, models, testing and verification, observability, protection systems and other operational characteristics of DER and their effect on the distribution systems.

NPCC has also been conducting DER Forums, the purpose of which is to promulgate DER related information, educate, and inform.  NPCC’s Regional Standards Committee (RSC) and Reliability Coordinating Committee (RCC) have also developed a joint process and a form to report DER related impacts, analyze and determine a way to address any issues.  The Form and process may be found in Appendix A and on the NPCC website.

NPCC, is not creating new Criteria or Standards through this guidance document. The intent is purely informational and as NERC’s SPIDER, and other groups develop their respective guidance documents it will be revised to achieve continued alignment and avoid duplication.

This guidance document contains DER Recommendations, and information provided by NPCC’s Members, NERC, the industry, the US National Labs, the Electric Power Research Institute and information from NPCC Staff. Also, it is important to note that specific distribution utility requirements within NPCC at the local level will supersede any suggested approaches in this document.

# Introduction and Objective

A consistent defined term for what type generating resources are included in DER is not broadly accepted by the industry. Also, DER is not currently a term that is defined by NERC.

For the purpose of this NPCC guidance, DER refers to:

Any non-BPS connected real or reactive power resources (generating units, multiple generating units at a single location, distributed generation installations, battery storage, systems etc.) located within the boundary of any distribution utility’s service territory, irrespective of capacity, allowing individual small DER to be captured if they are not aggregated. Some DER technologies are more intermittent in their production characteristics than resources which operate based on a controllable fuel input.

Initially, in the first version of this guidance document, NPCC specified a threshold for inclusion of DER in any Regional Guidance would not include individual rooftop solar or wind turbines or other localized DER net metering installations, however the aggregate effect of these types of DER can have a significant change in the power system and if not properly understood can impact the reliable operation of the BPS, as we have seen in California subsequent to their Rule 21. NPCC is now observing aggregation of DER beginning to enter capacity wholesale markets within the NPCC Region.  This document will continually be modified as emerging issues related to DER’s deployment, interconnection, planning and operations are identified and technology improves.

This document identifies opportunities for DER related process improvement and address potential reliability risks, promote good utility interconnection practices necessary for reliability, and promulgate information on how DER can enhance reliable operation of the Transmission Distribution interface by providing essential reliability services.  In addition, during the development of this document, a review of existing DER related documents was performed and NPCC is working with the NY Interconnection Technical Working Group as well as the Joint Utilities group of NY to align processes where possible.

National standards are established to address DER impact on system reliability.  IEEE Std 1547-2018 brings significant potential benefits to the BPS by requiring that DER provide essential reliability services to ensure stability, reliability, and security.  State and Provincial requirements for DER interconnection should also require compliance with IEEE 1547 through inclusion in those interconnection agreements.

As DER continues to penetrate the electric system at the “grid edge” or distribution system, and replace conventional transmission grid connected resources, there is an increasing reliability related need to understand and influence the effect of these DER resources on the BPS.  It is important to understand how DER is interconnected, planned, operated and how they interact with the transmission system.

Reliably and securely integrating DER into the electric system requires a comprehensive multi-pronged approach utilizing perspectives from different areas.  DER design, modeling, planning, and relay coordination require consideration of jurisdictional issues.  The importance of Members working with their respective national, state, and provincial regulatory authorities to help them understand the consequences of and formulation of effective DER interconnection requirements is critical. While there may be some broad universal guidelines, the details of effective DER interconnection requirements should be reconciled with the nature of the system within which the interconnection is taking place.  Appendix B of this document provides a comparison of NPCC’s Area requirements, at the time of the Version 1 writing, to help identify opportunities for guidance.

Many, if not most, of the contemporary DER is theoretically capable of bringing several enhancements to reliability, provided that there are sufficient design specifications and interconnection requirements to implement the enhancements.  Inverter based DER may use fast, programmable response to provide benefits to reliability if properly configured with coordination with the host utility.  Coordination must consider effects both on the distribution system and the BPS. The sections below address DER impact on the BPS including aspects of:

- Interconnection guidance

- Voltage response

- Frequency support

- Reconnecting to the utility following faults

- Under frequency load shedding

While DER presents opportunities to enhance reliability, they also introduce challenges at the transmission/distribution interface if not deployed correctly.  Interoperability with the transmission system is not solely determined at the point of interconnection. Visibility and a level of controllability of DER is essential for transmission operators to maintain situational awareness for reliable operation of the BPS, and for short-term forecasting.   Additionally, characteristics of DER such as capacity, intermittent production, location, protection settings, and other parameters must be known for long-term operational performance forecasting and system planning to ensure BPS reliability is maintained.

Presently there are limited study tools in general use to perform fully integrated studies of transmission and distribution which would allow both systems to be modeled and studied (in steady state and dynamically) together, although work is underway in this regard.  EPRI has an open sourced co-simulation tool under test.  In the shorter term, visibility of the variability of DER capacity could dramatically affect the quality of state estimator information and methods of improving data and forecasting need to be explored.

In recognition of both the benefits and challenges associated with DER, the approach taken with this second version of the NPCC DER guidance document is to collect interconnection related information within the NPCC Region as well as in other areas of the NERC Electric Reliability Organization (ERO) Enterprise.  There are some specific situations where opportunity exists to ensure better coordination across the NPCC Region.  The intent of this document is to identify any emerging reliablity issues and opportunities for further work, and provide general guidance and information where possible, offer consistent guidance with North America wide technical direction to promote reliable interconnection and operation of DER. It is recognized that DER may not be placed optimally and in areas where deliverability to load may not be ideal.  In this respect any specific information in this document must be considered in conjunction with the requirements  of the interconnecting distribution utility.

# NPCC DER Impact Reporting

In order to ensure the reliability and Resilience of the interconnected BPS in Northeastern North America as DER, both aggregated and single installations, continue to proliferate throughout the distribution systems within the NPCC Region, it is important to have a Regional DER impact reporting mechanism.  The NPCC Regional Standard Committee (RSC) created an impact reporting form and process that allows entities to report DER impacts and to seek guidance regarding emerging issues and reliability risks that affect or could affect the reliable performance of the BPS see Appendix A.  The Word version of form also is available on the NPCC website at:

BES Impact Reporting Form

Impact reporting and its associated process provide an orderly mechanism for NPCC to review reliability impacts submitted.  A Report will initiate a collaborative review by the Reliability Coordinating Committee and the Regional Standards Committee.

# DER BPS Impact Considerations

NPCC’s Regional Standards Committee (RSC) and Task Forces (i.e. Task Force on System Studies) reviews of DER as it pertains to the NPCC Region’s BPS performance have identified several areas which, going forward, may warrant further and continual monitoring and analysis.  NPCC has identified the following items that should be carefully considered as DER levels (total MWs) increase.

- DER performance with respect to voltage and frequency ride through

- DER ability to provide regulation and reserves

- DER availability and quality of forecasting.

- Observability and situational awareness of DER and importance of implementing Advanced Metering Infrastructure (AMI) if telemetry is not deployed

- DER impacts on Underfrequency Load Shed programs.

- Impacts of DER on the System Restoration and Black Start Plans.

Although DER markets, both wholesale and dual participation models, are not the focus of this document, due consideration should be given to their structure.  Market rules that allow aggregation also vary across the NPCC Region.  Some Areas allow injection of the aggregation across their market area while others require specific aggregations to be injected nearest to a transmission node.  DER are capable of providing ancillary services that are necessary to support reliability, if there are appropriate market mechanisms and incentives that allow and encourage them to do so. Wide-area aggregation and injection may create challenges for the system planners and operators as well as raise deliverability and operations concerns.

# NPCC Interconnection Guidance

This document and any detailed specifications which follow, are intended to provide examples of general information regarding DER interconnection. The examples do not constitute a Regional Criteria (which can only be implemented through NPCC Directories and approval of NPCC’s Full Members). There are numerous efforts underway in many forums and regulatory bodies that are expected to create new, more specific guidance. The level of detail and specificity provided is intended to be used as information and guidance for any NPCC Member Area which may not have yet seen the need to establish detailed operating parameters. This document shares the practices of some Members of NPCC which have already established detailed DER requirements, even in advance of upcoming applicable industry standards due to the rate of penetration of DER in their Area. NPCC Members considering improving or adding to their respective DER guidance are encouraged to reach out directly to other members which may have already addressed DER related reliability risk issues.

NERC and NPCC have criteria for resource and transmission planning. For transmission, criteria require transmission planners to simulate different transmission system events and ensure the transmission system remains reliable by meeting performance characteristics for these events. If the transmission system does not remain reliable, the planners are required to identify remediation, including upgrades or expansions of the transmission system. One aspect of the simulation is to account for the loss of generation resources. If a significant amount of DER trips for the simulated transmission event, the transmission system could become unreliable for that event and require remediation. This can occur in several scenarios such a peak load day with maximum output from DER like solar PV or a light load spring day where PV solar and small hydro make up a significant percentage of the generation. IEEE Std. 1547-2018 “Standard for Interconnection and Interoperability of Distributed Energy Resources with Associated Electric Power System Interfaces” addresses this issue by setting the default DER trip settings for Category II at a level that coordinate with NERC standard PRC-24-02. This is the standard that defines ride-through capability for generators connected to the transmission system. Requiring DER to ride-through disturbances, similarly to large generators, would be a significant step towards ensuring a reliable transmission system at the lowest possible cost.

IEEE 1547-2018 was approved in 2019 and also unanimously adopted by the National Association of Regulatory Utility Commissioners (NARUC).  The standard outlines the technical specifications and performance requirements which are universally needed for interconnection and interoperability of DER and will be sufficient for most installations. Implementation guidance for IEEE 1547-2018 may be found here: Guideline IEEE 1547-2018. The applicability of certain specifications and requirements are dependent on specific application considerations. For these, the requirements are provided in terms of a limited number of technology-neutral performance categories, for which it is the responsibility of the authority governing interconnection requirements (AGIR) to consider.  Within New England, interconnection requirements vary by state, and further, by Distribution Provider.  In New York a common set of DER interconnection requirements exists and there is a Coordinated Electric System Interconnection Request (CESIR) which outlines and initiates the process.  Several other the State and Provincial AGIR have developed local interconnection requirements which are listed in Appendix E of this document along with links which will be helpful to access specific interconnection information. These requirements are then supplemented by individual Distribution Provider interconnection agreements and standards.

The DER owner must follow interconnection agreements and any AGIR requirements for fault ride through.  Utilities and other AGIR entities should ensure that their requirements describe necessary DER performance with ride-through capabilities for frequency and voltage events.  Interconnection agreements and standards generally have requirements to provide documentation upon request.

In terms of resource adequacy and resource management there is also the possibility of over generation, as has been demonstrated in the state of California when the system operator runs out of load to absorb the available generation.  Operating procedures for selecting which generation to curtail should be in place requiring System Operator visibility of DER either individually or in aggregate. In lieu of operating procedures, some areas of the country are planning to use market mechanisms to address this issue.  Interconnection agreements or other state or local standards may require DER installations to provide communication channels so that generation can be coordinated with a central dispatch authority.

The DER owner’s protection and control equipment also must be capable of automatically disconnecting the generation from the system to which it is directly connected upon detection of frequency or voltage conditions outside of the applicable ride-through requirements. Note that those interconnection agreements and standards should account for both distribution protection and reliability of the BPS.  For three-phase installations, the over and under voltage function should be included for each phase and the over and under frequency protection on at least one phase. All phases of a generator or inverter interface should disconnect for appropriate voltage or frequency trip conditions sensed by the protective devices. Voltage protection should be wired phase to ground for single phase installations and for applications using wye grounded-wye grounded service transformers.  Automatic disconnect devices must be sized to meet all applicable local, state, and federal codes.

The specified size of the generation facility or energy storage system should be based on electrical generator or inverter AC nameplate ratings. The specific design of the protection, control, and grounding schemes will depend on the size and characteristics of the DER owner’s generation, as well the DER owner’s expected load level. Dynamic protection systems may be needed based on the characteristics of the particular portion of the utility’s system where the DER owner is interconnecting.

The settings referenced herein are generally intended for single-phase and three-phase applications using wye grounded- wye grounded service transformers or wye grounded-wye grounded isolation transformers. For applications using other transformer connections, a site-specific review should be performed by the utility and the revised settings identified in the DER Application Process.

The guidance set forth in this document is intended to be consistent with those specifications contained in the most current version of IEEE Std. 1547-2018. It is recommended that the requirements in IEEE 1547-2018 be referenced in the interconnecting utility requirements as well as any further state interconnection requirements as appropriate.

## Voltage Response

Within IEEE-1547 and in NY State Public Service Commission Interconnection Requirements, the operating range for the generators is generally intended to be from 0.88 to 1.10 per unit of nominal voltage magnitude. In addition, the generator should not cause the system voltage, at the Point of Common Coupling (PCC), to deviate from a range of 0.95 to 1.05 per unit of the utility system voltage. For excursions outside these limits with a duration longer than the applicable fault ride-through requirements, the protective device generally automatically initiates a disconnect sequence from the utility system as detailed in the most current version of IEEE Std. 1547-2018. Planning Coordinators and Transmission Planners should also be aware that DER installed with older interconnection agreements may reference prior versions of 1547 and may not meet current ride through requirements.  Clearing time is defined as the time the range is initially exceeded until the DER owner’s equipment ceases to energize the PCC and includes detection and intentional time delay. Other static or dynamic voltage functions may be permitted or required as agreed upon by the utility and DER owner. The industry is now in the process of promoting ride-through via several different standards initiatives which NPCC is tracking through its DER Forum

As described above, ensuring that DER can respond appropriately for various voltage conditions is critical for system reliability, as well as avoiding equipment damage and protecting personnel safety. Continuous operation over a wide band of voltage levels will ensure that DER do not prematurely trip and further deteriorate system conditions. IEEE Std. 1547-2018 includes ranges of trip settings. For inverter-based DER, the “shall trip under” voltage setting should be chosen to meet the requirements of NERC PRC-024-2, as described in Annex B of IEEE Std.1547-2018.

Quebec Interconnection

Ride through during system disturbances is of primary importance for resources connected to the grid, with the objective of maintaining system reliability. IEEE-1547-2018 addresses the topic, however, for voltage and frequency, what is required in the IEEE standard does not match the requirements in Quebec.

DER should have voltage related operational capability and protection settings set as prescribed by the area Electric Power System (EPS) operator and in accordance with IEEE Std. 1547-2018.

This subject area is a matter of facility installation and personnel policy of the asset owner, balancing both reliability and safety.  This information should be communicated to the interconnecting utility for proper protection system coordination.

In the Quebec interconnection voltage ranges and regulation requirements vary from the Eastern Interconnection. The requirements of the AGIR having jurisdiction should be followed (typically the Régie de l'énergie and Hydro-Québec).  Details for Quebec’s process may be found in Appendix E.

## Frequency Support

Frequency support is provided through the combined interactions of synchronous inertia and frequency response. Working in a coordinated way, these characteristics and services arrest the decline in frequency after a disturbance and eventually return the frequency to the desired level.  As increased levels of DER are introduced to the system, synchronous inertia will be displaced, which may have an impact on the frequency response performance of the system.  With increased penetration of DER it is becoming desirable for DER to remain connected even outside the prescribed frequency range if there is no risk to the DER equipment. The ride-through curves are “shall not trip within the acceptable range,” not “must trip immediately outside of the acceptable range.

Interconnection agreements should require DER distribution resources to have a frequency and voltage operating range that is equivalent to BPS connected resources consistent with the most limiting of PRC-006-NPCC, PRC-024 and the latest version of IEEE 1547. The sequence for a protective device to automatically initiate a disconnect sequence from the utility system is also detailed in the most current version of IEEE 1547-2018. Clearing time is defined as the time the range is initially exceeded until the DER owner’s equipment ceases to energize the point of common coupling (PCC) and includes detection and intentional time delay. Other static or dynamic frequency functionality may be permitted or required as agreed upon by the utility and DER owner. There is a need to establish a mechanism to ensure distribution provider transmit information to planners and operators as to which DER facilities are connected to distribution feeder that have UFLS protection systems.

Quebec Interconnection

Note that in the Quebec Interconnection the frequency operating range is wider than in the Eastern Interconnection. In Quebec, the acceptable steady-state frequency range is from 59.4 Hz to 60.6 Hz, and DER must be capable of riding through frequency as low as 55.5 Hz (for a short time period). Therefore in Quebec, UFLS systems must operate outside this operating rang in accordance with the Quebec variance to the PRC-006-NPCC UFLS-1 regional standard table 4.

## Reconnection to the Utility System

If the generation facility is disconnected as a result of the operation of a protective device, the DER owner’s equipment must remain disconnected until the utility’s service voltage and frequency have recovered to acceptable voltage and frequency limits for an acceptable amount of time. Interconnection agreements or local standards should address times for reconnection to the utility system.  Per IEEE 1547-2018 Clause 4.10.3, the allowable range of settings is 0-600 seconds with a default setting of 300 seconds. IEEE 1547-2003 in clause 4.2.6 allows an adjustable delay or a fixed delay of 5 minutes.  The time specified by the interconnection agreement should be coordinated to support BPS reliability as well as distribution requirements.

Systems greater than 25 kW that do not utilize inverter-based interface equipment should not have automatic recloser capability unless otherwise approved by the utility. If the interconnecting utility determines that a facility must receive permission to reconnect, then any automatic reclosing functions must be disabled and verified to be disabled during verification testing.

Utilities in other parts of the Eastern Interconnection who have experienced increased levels of DER have determined that during system restoration, DER should not be allowed to return to service until the system has been reestablished and is in a stable operating state. Interconnection agreements and standards should address necessary communications and SCADA requirements.  As traditional resources on the BPS are retired and the grid becomes increasingly reliant on grid edge DER on the distribution, Black Start and System Restoration plans will have to be adjusted accordingly.

## Inverters

A power inverter, or inverter, is a power electronic device or circuitry that changes direct current (DC) to alternating current (AC). The inverter itself does not produce any power. The power is provided by the DC source. Inverter design and/or configuration should be capable of ride-through for specified utility system events and are grouped into three separate performance Categories.

- Category I is based on minimal BPS reliability needs and is reasonably attainable by all DER technologies that are in common usage today.

- Category II covers minimum BPS reliability needs, and coordinates with NERC Reliability Standard PRC-024-2, which was developed to avoid adverse tripping of BPS generators during system disturbances.

- Category III provides the longest duration and widest bands for voltage ride-through capabilities that are attainable by inverter-based systems where there very high levels of DER penetration are expected or where momentary cessation requirements are seen as a desirable solution for coordinating with distribution system protection and safety. This category is intended to address DER integration issues like power quality and system overloads caused by DER tripping in the local Area EPS and to provide increased BPS reliability by further reducing the potential loss of DER during bulk system events.

Inverters intended to provide local grid support during system events that result in voltage and/or frequency excursions as described in this document and should be provided with the required onboard functionality to allow for the equipment to remain online for the duration of the event.

It is recommended that all applicable inverter-based applications should:

- be certified per the requirements of UL 1741 SA as a grid support utility interactive inverter

- have the voltage and frequency trip settings as specified by the interconnecting utility

- have the abnormal performance capabilities (ride-through)

- provide interactive inverter functions status

In New York State it is recommended that equipment be selected from the Department of Public Service “Certified Interconnection Equipment list” maintained on the NY Public Service Commission’s website. Interconnected DG systems utilizing equipment not found in such list should meet all functional requirements of the current version of IEEE Std. 1547-2018 and be protected by utility grade relays (as defined in these requirements) using settings approved by the utility and verified in the field. The field verification test in New York State must demonstrate that the equipment meets the voltage and frequency requirements detailed in this section.  Individual New England State interconnection standards and agreements also typically refer to IEEE Std. 1547-2018 functional requirements and include protection setting review requirements.

ISO-NE also has developed a technical bulletin, contained in Appendix F, which outlines required settings for inverters in New England.

## Certification per UL 1741 SA as grid support utility interactive inverters

Because Inverters certified for IEEE 1547-2003 do not currently provide adequate grid support functionality, in the interim period while IEEE P1547.1-2018 is not yet revised and published, certification of all inverter-based applications is needed. For example, in one NPCC Area the following approach was taken to assure having inverters installed with a standardized set of grid support functionality to ensure the reliability of the BPS (e.g. maintaining acceptable system frequency and voltage).:

- Should be compliant with only those parts of Clause 6 (Response to Area EPS abnormal conditions) of IEEE Std. 1547-2018 (2nd ed.)1 that can be certified per the type test requirements of UL 1741 SA (September 2016).

- May be sufficiently achieved by certifying inverters as grid support utility interactive inverters per the requirements of UL 1741 SA (September 2016) with either CA Rule 21 or Hawaiian Rule 14H as the Source Requirement Document (SRD). Such inverters are deemed capable of meeting the requirements of this document.

- Applications should have the voltage and frequency trip points and abnormal performance capabilities consistent with IEEE 1547-2018, PRC-024-2 and PRC-006-NPCC.

- Abnormal performance capability (ride-through) requirements for inverter-based applications should have the ride-through capability per abnormal performance Category II of IEEE Std. 1547-2018 (2nd ed.) as quoted in Tables III and IV. Additionally, an effort is underway at IEEE to amend 1547-2018 to expand the range of under-voltage trip settings in Category III. If the amendment is approved, Category III inverters should be recommended for use.

## Minimum Protective Functions

Protective system requirements for distributed generation facilities result from an assessment of many factors, including but not limited to:

• Type and size of the distributed generation facility

• Voltage level of the interconnection

• Location of the distributed generation facility on the circuit

• Distribution transformer

• Distribution system configuration

• Available fault current

• Load that can remain connected to the distributed generation facility under isolated conditions

• Amount of existing distributed generation on the local distribution system.

Local interconnection agreements and standards should require that synchronous, induction and inverter based DER include protection functions for Under/Over Voltage (27/59), Over/Under Frequency (81O/81U), Overcurrent (50P/50G/51P/51G) and Anti-Islanding Protection.  Reverse power protection should also be considered as appropriate for BPS support.  Interconnection agreements and standards should require that inverter based DER should be certified according to UL 1741SA as grid supportive.  DER protection equipment should utilize a non-volatile memory design such that a loss of internal or external control power, including batteries, will not cause a loss of interconnection protection functions or loss of protection set points.  Interconnection agreements and standards should require that DER protective devices utilize their own current transformers and potential transformers for protection and not share electrical equipment associated with utility revenue metering.

The need for additional protective functions will be determined by the utility on a case- by-case basis. If the utility determines a need for additional functions, it will notify the DER owner of the requirements. The notice should include a description of the specific aspects of the utility system that necessitate the addition, and ideally, explicit justification for the necessity of the enhanced capability. The connecting utility will specify and provide settings for those functions that the utility designates as being required to satisfy their individual protection practices. Any protective equipment or setting specified by the utility is not to be changed or modified at any time by the DER owner without consent from the utility.

The DER owner is responsible for ongoing compliance with all applicable local, state, and federal codes and standardized interconnection requirements as they pertain to the interconnection of the generating equipment.

All interface protection and control equipment should operate as specified by state and local interconnection agreements and standards.

In New England, for monitoring and control of new DG projects, Appendix E lists current interconnection documentation and standards for DER by State.  The DER communications hardware, protocols, and data models must comply with these state and local interconnection utility standards.

In New York, for monitoring and control of new DG projects, the most current version of the Monitoring and Control Criteria should be employed by the utilities to evaluate the need for such equipment in New York.  The New York Monitoring and Control Criteria document was developed and agreed to through a collaborative process as part of the Interconnection Technical Working Group (ITWG). The communications hardware, protocols, and data models must comply with local interconnection utility standards.

Also, and fundamentally, existing over-current protections in distribution system are typically designed to clear line and ground faults occurring downstream from their location, as the only source feeding the fault is the transformer station. Connecting a DER provides another source supplying the fault, and the fault contribution from the facility might cause protection to operate non-selectively for reverse faults, out of the protected zone. If the maximum reverse fault current through a non-directional fault-interrupting device exceeds the setting of the device, the fault-interrupting device should be considered with a directional feature to prevent tripping for reverse fault current flow. For instance, phase protection could be replaced with an impedance relay (function 21) if required.

## Metering

Advantages and Opportunities of Implementing Advanced Metering Infrastructure (AMI):

IEEE 1547-2018 interoperability requirements specify that the DER have communication capabilities and shall measure specific quantities and have this information available at the communications interface.  Most utilities, however, do not have and are not requiring DER owners to provide the communications needed to connect all DER to a grid SCADA system.  Such requirements tend to be placed only on large DER.  Most utilities do not have the information infrastructure necessary to interoperate with large numbers of small DER; however, implementation of AMI will help in this regard.

Depending on the level of analytics utilized by an Electric Distribution Company (EDC), AMI can provide varying levels of intelligence and operability about the electric distribution system.  Even if no analytics are implemented, value can be gained by reviewing and having access to the data provided by AMI.  If a full-fledged data analytics package is implemented, then significant benefits can be realized.

Without an analytics package, engineers or analysts can still review basic voltage information provided from AMI.  Using SAS, Excel or other simple tools, the voltage data provided, on a daily basis, can be quickly filtered down to exhibit meters that have high or low voltages exceeding the limits set by local Regulatory bodies.  With minimal research, it can be determined if high voltage is caused by the presence of DER, either for the meter affected or a nearby neighbor on the same secondary transformer.  The transformer can be evaluated by engineering to determine if new, larger equipment is needed.

With reports of abnormal voltage, Distribution Planning can evaluate the data and determine if voltage regulators need to be added towards the end of a circuit, if switching needs to occur to change circuit topology, or if other actions are needed.  If the low voltage only occurs at certain times of the day, then perhaps load tap changers at the substation may be used to address the issue.

If implementing a data analytics package, whether off-the-shelf or home grown, more details on system operating conditions can be found.  For instance, by evaluating the sum of meter usage for a specific transformer, secondary transformers can be determined to be over or under loaded.  If voltage interval data is available, the GIS model of the system can be evaluated to identify meters that are incorrectly assigned to transformers; the model can be corrected to properly assign meters to transformers.

With data analytics and near real-time data transfer from the head-end system then volt-var optimization can occur.  As LTCs, capacitor banks or voltage regulators are adjusted, live feedback from the system can be evaluated to ensure the expected responses are occurring.  If something unexpected is happening, then operators receive evidence of this quickly and can take remedial actions.

The specific benefits of AMI are still evolving, and as more analytical tools are made available, and as meters become more advanced, the data will be leveraged to provide more insights into the operation of the distribution network.

Metering requirements for SCADA purposes are usually determined by the local connecting utility and based on the configuration of the DER system prior to energization.  Whether SCADA metering can be integrated with revenue metering is a matter for the local connecting utility and connecting DER facility to decide. New metering or modifications to existing metering should be reviewed on a case-by-case basis and be consistent with metering requirements specified by the local connecting utility and any overarching requirements adopted by the local regulatory authority that has jurisdiction (e.g. state commission for example for revenue metering). Net Energy Metering should be required when a DER has the capability or potential to provide generation back into the utility distribution system, however, the eligibility of a DER provider to receive net metering will be subject to the rules of the interconnecting utility and the local regulatory authority that has jurisdiction.

IEEE-1547-2018 requires DER to be capable of providing monitoring of connection status, real power output, reactive power output, and voltage either at the point of connection or some agreed upon point if multiple DER facilities are involved.  Going forward, member utilities should consider developing IT Infrastructure plans to aggregate and report critical DER Status to BPS Operators, i.e. aggregate DER output within a given area. This information should be available to the system operator as required by the connecting utility. The monitoring equipment should be installed at the time of interconnection and meet the technical requirements of the connecting utility. The DER metering and monitoring communications will allow interoperability and the capability to provide system operators with situational awareness necessary for reliably operation of the interconnecting utility facilities.  As more DER is employed and base load generation is replaced with DER resources, it will be important for the Distribution Provider (DP) or interconnecting utility to be able to monitor the availability and production of electricity (power output and energy delivered) from the DER resources.

## Power Quality

The requirements for acceptable flicker levels should be in accordance with the latest version of IEEE Std. 1453 Recommended Practice for the Analysis of Fluctuating Installations on Power Systems. Short and long-term perception of flicker should be within the planning and compatibility levels delineated in any applicable requirements or standards.

## Power Factor

If the output power factor, as measured at terminals of the generator, does not meet the connecting utility’s power factor requirements, the method of power factor correction necessitated by the installation of the generator can be negotiated with the utility as a commercial item. If the average power factor of the DER over time is proven to be outside 0.9 (leading or lagging) by the customer and accepted by the utility, that power factor range may be used for any further utility facility design calculations and requirements.

Induction power generators may be provided with a VAR capacity from the utility system. The installation of VAR correction equipment by the generator- owner on the DER owner’s side of the PCC is to be reviewed and approved by the interconnecting utility prior to installation.

## Islanding

The guidance provided in this document is designed and intended to avoid islanding and may be superseded by local requirements. Additional protection schemes and system modifications may be necessary based on the capacity of the proposed system and the configuration and existing loading on the subject circuit.

The need for zero sequence voltage and direct transfer trip protection schemes should be evaluated based on minimum loads on the associated feeder and substation bus, including the impact of fault conditions resulting from DER installation to protect facilities for an islanded condition.

Transfer trip is needed in some instances (e.g. on DER connections to non-radial transmission or sub-transmission circuits) in order to protect the utility systems and DER facility from damage during faults and/or reclosing operations into faults. The decision as to the applicability of direct transfer trip and specific technology to be used form direct transfer trip communications rests with the connecting utility.

## Automatic Underfrequency Load Shedding (UFLS) Programs

UFLS is implemented to restore power system frequency stability if system frequency drops below the UFLS operational set point. Significant deviations in system frequency typically occur during major disturbances such as a loss of generation or events in excess of design contingencies used for planning purposes.    UFLS is considered the “safety net” for the BPS and a last resort automatic control operation designed to stabilize BPS islands for a generation deficiency. Various fractions of load are shed through this process, typically 25%.  UFLS is primarily installed on distribution feeders, where DER is increasingly being deployed.

NERC has a set of requirements in the PRC-006 standard and NPCC has more stringent requirements in NPCC’s Regional Standard, PRC-006-NPCC which outline expected UFLS performance.  Approved and effective versions of these standards may both be found on the NERC website.

SS-38 is the NPCC working group responsible for inter-Area dynamic analysis. The SS-38 Working Group regularly studies the UFLS performance within the Region and has recently completed sensitivity analysis showing that a moderate increase of DER penetration anticipated in the short term will not result in any significant degradation in the UFLS program performance based on the conditions and assumptions used in the analysis.

In the future, adopting a more flexible approach to UFLS may be necessary as DER penetrations reach higher levels.  There are utilities that are reviewing the feasibility of “Adaptive UFLS” which uses real time monitoring of distribution feeder loads and their DER to determine how much additional load may need to be tripped when DER has increased output. Some utilities, such as Duke Energy avoid choosing those distribution feeders for the UFLS program that have DER interconnected to them.

## Effective Grounding for DER

With the onset of high penetrations of DER, such as photovoltaic (PV) generation, utilities should consider interconnection of PV plants similarly to how they would interconnect synchronous generators.

Conventional generators are considered voltage sources as the magnetic flux within the generator tends to provide a constant voltage source during faults. In contrast, inverter-based DER plants are considered voltage-controlled current sources during faults.  Inverter-based plants generally provide less short-circuit current than similarly sized synchronous unit.

Solidly grounding a transformer neutral for a DER plant eliminates a possible phase overvoltage stemming from a single-line-to-ground fault. A potential problem with the solid grounding in the distribution line is that large fault currents can flow through the transformer neutral, which can desensitize the overcurrent protection coordination. In order to mitigate this issue, impedance grounding can limit the fault current and potential equipment damage, while allowing overvoltage to some limited magnitude.  Some utilities protect their distribution from overvoltage by using overvoltage protection so Effective Grounding isn’t a concern.   Further investigation on the how specific installations are grounded is warranted and being pursued by the Interconnection Technical Working Group (ITWG) in New York.

## Resource Adequacy

Forecasting resource adequacy is an import system reliability function. The reporting of generation capability and data is integral to this activity. Specific modelling information of intermittent DER resources is critical to planning and understanding system performance.  Information related to DER in-service dates, capacity value, availability, emergency assistance, scheduling, and deliverability should be available to the planners. Modeling, data, and other necessary information should be defined and made available to those needing it, such as planners and system operators. Any requirements associated with this information should be in Interconnection Agreements or Tariffs prior to any commissioning of the DER.  There are currently no mechanisms within NERC Standards or NPCC Criteria to require DER entities to provide this information.  It currently needs to be covered under other contractual agreements such as local utility Interconnection Agreements or Tariffs.

## Energy Storage Systems for DER

Battery storage technology is undergoing a rapid evolution from Lead Acetate to Absorbent Glass Mat to Li-Ion due to the expanding application of batteries to transportation and other sectors. Li-Ion batteries have been and continue to be deployed in a wide range of electric energy-storage applications, ranging from energy-type batteries of a few kilowatt-hours in residential systems with rooftop photovoltaic arrays to multi-megawatt containerized batteries for the provision of grid ancillary services.  The Energy Storage Association (ESA) anticipates at least 35 GW of new energy storage will be deployed in the United States by 2025.

NPCC is also observing marked increases in Hybrid Resources which are combinations of multiple technologies that are physically and electronically controlled by the Hybrid Owner/Operator behind the point of interconnection (“POI”) and offered to the grid as a single resource at that POI.  This arrangement usually involves energy storage at a photo-voltaic or wind turbine site.  It optimizes the use of DER and enables normally clipped energy (energy beyond the rating of an inverter or unneeded by the BPS) to be stored on-site and released in the future.  It also allows low outputs of DER which may be outside the operational range of an inverter to be harvested for charging on-site storage allowing better utilization of the total resource. In the figure below the red curve represents the capability of an inverter and the blue is the capability of the DER.  Areas between the curves may be used to charge or “harvested.”  This leads to a more efficient utilization of the DER and supports grid reliability and state of charge of the energy storage.  As shown below, the capability of an inverter can be exceeded by the capability of the DER behind it.  This is designed with due consideration of the degradation of DER, such as a solar panel over time.

Figure 1- Storage showing Clipped and Unused Energy

The ESA has an online report to manage any risks associated with Energy Storage.  Their report may be found here, Energy Storage, Operational Risk Management . Care should be used in placement of batteries and should avoid physical proximity (due to the risk of fire or explosion) and electrical proximity (due to harmonics and other power electronic interaction concerns) to other facilities that may be critical to the reliable operation of the BPS.

## System Control and Data Acquisition (SCADA) and Communications

As DER penetration increases all DER above a certain MW level, as determined by the interconnecting utility or System Operators, should be required to provide SCADA telemetry data to a control center to monitor their output.  It might be beneficial to have DER data be communicated to a Distribution System Operator, distribution system platform or similar, to provide analysis and aggregation of data for a concise summary to the transmission system operator.  IEEE-1547-2018 has a communication port requirement. This ensures that the output remains visible to the system operator. It allows the system operator to observe DER status when working on a feeder in emergent or planned outage situations. Some NPCC Members have encountered difficulty with obtaining information and data from the DER. DER owners should be encouraged to keep their end of any SCADA equipment functional and reconnect their telemetry devices when they have been disabled and this can be done through interconnection requirements. The operator should be alerted by the DER when telemetry is interrupted. Scan rates equivalent to the scan rates used by the system operator are preferred (typically in the 6 second range).  Although IEEE 1547-2018 defines and requires a communication port, the path that a utility may use for data from that communication port may pose a cyber-security risk.  It is suggested that full consideration be given to cyber security risks when transferring data until such time as the IEEE 1547 has been amended to require cyber security protections.

# DER Recommendations

As DER continues to penetrate the NPCC Region we suggest the following initial activities:

Participation in National DER Forums

- Participate in national efforts to fully understand the issues and best practices associated with DER.

- Engage NPCC and its members at the national level leading efforts to address the issues and provide expertise.

- As the understanding at the national level of the issues and best practices matures then NPCC will be well positioned to understand the regional differences that need to be considered.

Process and Risk Management Recommendations

- Continue with sensitivity analysis at the Transmission level for various levels of penetration of DER on the distribution facilities to determine effects of increased penetration levels of DER on BPS performance.

- Pursue further opportunities to coordinate distribution and transmission requirements for DER generating resources, share Member best practices, and promote consistency regarding DER installations where possible within the NPCC region.

- Continue to review and identify approaches to coordinate NPCC AGIR and utility interconnection requirements relative to DER to identify dissimilarities between Areas which may negatively impact reliability.

- Identify opportunities to share information regarding DER related reliability risk problems and problem solutions and promote sharing.

- Encourage consideration of developing IT Infrastructure plans to aggregate and report critical DER Status to BPS Operators.

- Continue to solicit and address observable reliability related issues of DER using NPCC’s DER Impact Reporting Forms and its associated process.

- Continue to discuss any changes required for System Restoration and Blackstart Plans, as a result of increased DER.

- Continue to follow DER related ESA ESS safety issues and associated recommendations and share the results with NPCC stakeholder.

- Avoid placement of UFLS on distribution feeders with DER unless sufficient telemetry exists to ensure proper functionality of the UFLS program as a whole.

Planning Related Recommendations Due to Changing Resource Mix

- Identify and consider new methods to obtain and facilitate collection of DER modeling and performance data to enable Long-Term Resource, Long-Term Transmission and Operational Planning of the BPS

- Clearly identify DER in the NPCC Region’s Area interconnection queues or forecasts where DER is being proposed for installation, including the magnitude and location relative to the existing resource base and load projections.

- Address masking of load by DER at the distribution level to ascertain its impact on the behavior of load, as well as the assumptions that underpin UFLS programs.

- Determine the appropriate entities responsible for providing DER data to the Planning Coordinator for the purposes of model building and maintenance and ensure that this data is provided.

Analytics and simulation recommendations to deal with increase system complexity

- Support interconnection wide inertia loss study efforts, to determine potential reliability impacts, as DER replaces conventional synchronous generation resources.

- Obtain DER modelling data to be able to model, predict and examine system behavior and assess the interactions between the new resources and the existing reliability preserving systems and programs. Examples include:

  - Dynamic behavior of the transmission system

  - Sudden loss of large amounts of DER due to transmission system events

  - Under Frequency Load Shedding,

  - Under Voltage Load Shedding,

  - Frequency response sharing mechanisms (BAL standards).

  - Analysis of system protection systems (both T and D) so that the parameters to set protection systems and other control systems are known to permit the most reliability benefits to be garnered from the new resources.

# Appendix A, NPCC DER Impact Reporting Form and Process

Please Complete and email this form to;   npccstandard@npcc.org

Distributed Energy Resource (DER), BES Impact Reporting Form

| Name |  | Date |  |
| --- | --- | --- | --- |
| Email |  | Company |  |
| Impact on Bulk Electric System |  | Area (NY, NE, State or Province etc.) |  |

Equipment Impacted

| Equipment | Location (substation name, etc.) | Impact (Positive reliability impact? Negative reliability impact-Protection System failure, Misoperation, load affected or lost?, power quality issue?, etc) | Duration of Impact, (start and stop times, length of impact, ongoing? etc.) |
| --- | --- | --- | --- |

Description of Impact on BES- What Happened or was observed?

Please describe below the details of all the impacts of the DER as it pertains to this report, such as load loss, loss of life, equipment failure or potential reliability improvement. A sequence of events showing the impact is helpful. Attach supporting information to this form if necessary.

Root Cause or additional Analysis

Please describe below the details of any investigation your company may have already done to identify causes or contributing factors to the incident. This will help NPCC route the issue properly to address it.

NPCC Review of Issue and Recommendations (i.e. refer to NERC, develop a Criteria, Guideline, Already Addressed or Identified, etc.)

NPCC Date of Resolution of Issue ______________

| Evaluation Process # Appendix B, NPCC Areas- Comparisons Key Inverter based specification extracts. ISO-NE Inverter Requirements; NG ESB 756 B, C, D; NY SIR; IESO F2 Technical Requirements. Inverter Certification; yes; yes; yes; yes. Voltage and frequency trip settings for inverter-based applications; yes; yes; yes; yes. Voltage Response; yes; yes; yes; yes. Frequency Response; yes; yes; yes. Abnormal performance capability (ride-through) requirements for inverter-based applications; yes; yes. Other grid support utility interactive inverter functions statuses; yes. Minimum protection functions; yes; yes. Monitoring and Control; yes; yes; yes. Reconnection to the System; yes; yes. Distribution Protection Coordination; yes; yes. Inverter Certification; yes; yes. Power Quality; yes. |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |

# Appendix C – SPIDER Working Group Reliability Guidelines & Activities

The NERC System Planning Impacts from Distributed Energy Resources Working Group (SPIDERWG) was formed to focus on the impacts that aggregate amounts of DER can have on transmission planning and BPS reliability. This SPIDERWG is seeking to provide high-level, technical recommended practices for ensuring BPS reliability in the face of growing penetrations of DER across North America. The recommended practices and guidance provided by SPIDERWG, in many cases, will need to be adapted to specific utility and Regional planning and operating practices. The following DER-related topics are covered, as described in NERC Staff’s “Summary of Activities: BPS-Connected Inverter-Based Resources and Distributed Energy Resources”:

Modeling: Representing aggregate DER in BPS reliability studies, advancing industry capabilities and expertise with representing DER in these reliability studies, developing robust and reasonable data sets for power flow and dynamic simulations

Verification: Ensuring that the models used in studies provide a reasonable and suitable representation of the actual aggregate performance of these resources, benchmarking software platforms to ensure uniformity in tools, recommending analysis techniques for accounting for aggregate DER during large BPS disturbances

Studies: Improving study techniques and methods to ensure the most stressed operating conditions are chosen for BPS reliability studies, identifying key operating conditions and sensitivities to perform, improving software tools and study capabilities

Coordination: Supporting coordination between transmission and distribution entities for improved data exchange and coordinating with IEEE to support the application of IEEE Std. 1547- 2018 across North America

A list of SPIDERWG Reliability Guidelines and other activities is provided in Table 1 and Table 2, respectively.

Table 1. SPIDER Working Group Reliability Guidelines

| Subgroup | Title | Description | Status |
| --- | --- | --- | --- |
| Modeling | DER Data Collection for Modeling | Guideline providing recommended practices for collecting DER data for the purpose of developing aggregate DER models for BPS reliability studies. | In Review – Draft Posted for Comment (here) |
|  | DER_A Model Parameterization | Guideline providing recommendations for using state-of-the-art aggregate DER dynamic models in BPS reliability studies. | Published (here) |
| Verification | DER Performance and Model Verification | Guideline providing recommended practices for performing model verification for aggregate DER dynamic models including placement of measurement devices, execution of verification simulations, and how to use the data collected through these practices. | In Development |
|  | DER Forecasting Practices and Relationship to DER Modeling for Reliability Studies | Guideline providing how forecasting practices are linked to DER modeling for reliability studies, specifically on how DER are accounted for in future reliability assessments. | In Development |
| Studies | Bulk Power System Planning under Increasing Penetration of Distributed Energy Resources | Guideline providing recommended practices for performing planning studies considering the impacts of aggregate DER behavior. | In Development |
|  | Recommended Approaches for Developing Underfrequency Load Shedding Programs with Increasing DER Penetration | Guideline regarding how to study UFLS programs and ensure their effectiveness with increasing penetration of DER. | Under Consideration |
| Coordination | BPS Reliability Perspectives on the Adoption of IEEE 1547-2018 | Guideline providing industry recommendations and BPS reliability perspectives on the implementation and adoption of IEEE 1547-2018. | Published (here) |
|  | Communication and Coordination Strategies for Transmission Entities and Distribution Entities regarding Distributed Energy Resources | Guideline recommending strategies to encourage coordination between Transmission and Distribution entities on issues related to DER such as information sharing, performance requirements, DER settings, etc. | In Development |

Table 2. SPIDER Working Group Other Activities

| Subgroup | Title | Description | Status |
| --- | --- | --- | --- |
| Modeling | Modeling Notification: Dispatching DER off Pmax in Case Creation | Notification of accounting for DER in powerflow and dynamics cases, particularly regarding accounting for power output levels with DER utilizing advanced grid-supportive features. | Posted (here) |
|  | DER Modeling Survey | Survey of SPIDERWG member organizations regarding the use of DER models in BPS planning studies. | Compiling Results |
| Studies | White Paper: Review of TPL-001-5 for Incorporation of DER | White paper discussing technical review of NERC TPL-001-5 in the context of increasing DER and their impacts to the BPS. Possible SAR development following completion of white paper, as needed. | In Review |
|  | White Paper: Recommended Simulation Improvements and Techniques | White Paper recommending simulation software improvements to enhance the ability to accurately account for and model DER. | In Development |
|  | White Paper: DER Impacts to Undervoltage Load Shedding | White Paper briefly discussing how DER may impact UVLS program development. | In Development |
|  | White Paper: Beyond Positive Sequence RMS Simulations for High DER | White Paper highlighting the use of tools that provide additional technical detail to DER studies beyond just positive sequence RMS simulation tools. | In Development |
| Coordination | Coordination of DER Terminology | Development and ongoing review of definitions and terminology pertaining to DER and related topics. | In Development |
|  | NERC Reliability Standards Review | White Paper reviewing NERC Reliability Standards and the impacts that increasing penetrations DER may have on BPS reliability and standards compliance/implementation. Possible SAR development following completion of white paper, as needed. | In Development |
|  | Tracking and Reporting DER Growth | Coordinated review of information regarding DER growth, including types of DER, size of DER, etc. Consideration for useful tracking techniques for modeling and reliability studies. | In Development |

# Appendix D, NPCC Reliability Principles

Using its membership structure and governance authority to create and apply Regional Criteria, NPCC Member adherence to Regional criteria contributes to a more robust level of reliability beyond NERC ERO reliability “results-based” standards / requirements.  For example, NPCC Criteria mandate specific design requirements for NPCC Member facilities. NPCC‘s approach to reliability and Resilience can be summarized in Principles that guide NPCC Members in their effort to meet or exceed NERC requirements.  NPCC’s core Reliability Principles and activities support the NERC Bulk Electric System and NPCC’s Bulk Power System reliability.

The NPCC Reliability Principles include:

- Focus on the most important system components: In order to focus resources to those portions of the power delivery system most important (critical) to overall reliability, NPCC Members employ mechanism(s) for identifying those facilities that are most critical to the reliable planning and operation of the power delivery assets in the NPCC region. These critical facilities collectively are identified as the NPCC Bulk Power System,.

- Application of Criteria beyond NERC requirements to identified critical facilities: Where, in the opinion of NPCC’s Membership, the NERC standards do not adequately specify a necessary performance or design outcome in a given technical, operation or planning area, NPCC Criteria govern the design of their respective portions of the NPCC Bulk Power System planning and operation activities.

- NPCC Members support the Criteria: NPCC’s Full Members in accordance with the NPCC Bylaws are committed to designing and operating their systems to meet the NPCC Criteria under peer review of the NPCC Full Members.

- No conflict with NERC Requirements: The NPCC Criteria supplement, improve upon where necessary, benefit, and do not conflict with or duplicate the results-based performance requirements of NERC standards where they apply to the NPCC Bulk Power System. NPCC adjusts its regional Criteria to retire or adapt to any new NERC requirements as they come into effect as necessary.

- Include design specifications where needed: The NPCC Criteria and related guidelines and procedures provide design criteria and practices to assure implementation.  NPCC Directories go into greater detail regarding how to accomplish a given reliability result, where NERC standards may simply require a “reliability result.”

- Resilience has always been an element of NPCC Criteria: Based on experience, resilience  is a necessary constituent component of reliability and it is important both to electricity consumers and regulatory authorities in NPCC’s Region.  NPCC Criteria provide substantial resilience benefits to the NPCC Bulk Power System by providing:

  - Robustness – The ability to withstand disturbances by supporting operations in a more secure state.

  - Resourcefulness – The ability to detect and manage a crisis as it unfolds.

  - Rapid recovery – The ability to get services back as quickly as possible in a coordinated and controlled manner.

  - Adaptability – The ability to absorb new lessons from events

NPCC Criteria serve to establish a superior pre-event starting point, make the trough less severe and the recovery faster

NERC, Model of Resilience

Figure 2.1 depicts a typical disruptive event and maps how the systems responds in a qualitative fashion.  The y-axis above is meant to represent a relative level of reliability and system response is plotted temporally. DER will increasingly fill a critical role with respect to reliability and Resilience of the Bulk Electric System.  Specifically, DER can contribute to the overall robustness of the system and provide increased resource support within islands during system separations. As DER continues to penetrate the system, changes to NPCC’s Underfrequency Load Shedding program may be required.

# Appendix E, State and Provincial AGIR Information

## New York State

Statewide Interconnection Technical Documents may be found at:

Interconnection Technical Working Group Webpage

## New England, by State

Inverter Source Requirement Document of ISO New England (ISO-NE)

Connecticut –

Department of Energy and Environmental Protection, Public Utilities Regulatory Authority (PURA)

Eversource Energy – Connecticut Interconnection Standard

https://www.eversource.com/content/general/about/about-us/doing-business-with-us/builders-contractors/interconnections/connecticut-application-to-connect

Summary of Facility Connection Requirements for Generation, Transmission and End Users Connecting to UI Transmission Facilities, Revision 4.0, December 7, 2015:

https://www.uinet.com/wps/wcm/connect/89138d72-c4a0-403b-9871-937a00f91c42/NERC%2BFAC-001%2BInterconnect%2Bsummary%2BDocument%2BRevision%2B4.pdf?MOD=AJPERES&CACHEID=ROOTWORKSPACE-89138d72-c4a0-403b-9871-937a00f91c42-mkr0qCb

Eversource/United Illuminating Guidelines for Generator Interconnection, Fast Track and Study Processes, April 5, 2019:

https://www.uinet.com/wps/wcm/connect/bd802aec-1e83-4051-8a6e-58f0cb98d1fd/Guideline_for_Generator_Interconnection_Fast_Track_and_Study_Process_5-12-10_doc_1577.pdf?MOD=AJPERES&CACHEID=ROOTWORKSPACE-bd802aec-1e83-4051-8a6e-58f0cb98d1fd-miUZQ4n

Maine –

Maine Public Utilities Commission

Chapter 324 Small Generator Interconnection Procedures

Central Maine Power Transmission and Distribution Interconnection Requirements for Generation, December 15, 2018:

https://www.cmpco.com/wps/wcm/connect/dee5fbf1-7af0-40ec-b06c-af3ec015e0be/SchB-TransmissionDistributionInterconnectionRequirementsforGeneration.pdf?MOD=AJPERES&CACHEID=ROOTWORKSPACE-dee5fbf1-7af0-40ec-b06c-af3ec015e0be-mwfmMCK

Emera Maine Interconnection Agreement:

https://www.emeramaine.com/energy-solutions/connecting-renewable-resources/small-generator-interconnection-process/

Massachusetts –

MA Department of Public Utilities (MADPU) interim guidance (DPU 19-55)

MADPU Massachusetts Department of Energy Resources

MADPU Interconnecting Renewable Energy webpages with links to: resources, past and present proceedings before the DPU, each electric distribution companies’ tariff, and the Ombudsperson dispute resolution process:  https://www.mass.gov/interconnecting-renewable-energy-facilities

MADPU is currently conducting a large-scale investigation into the rules and procedures by which distributed generation is interconnected in Massachusetts in docket D.P.U. 19-55.  This investigation includes implementation of IEEE 1547-2018.  Documents and information can be found in our online file room:  https://eeaonline.eea.state.ma.us/DPU/Fileroom/dockets/bynumber (enter “19-55”)

Massachusetts Technical Standards Review Group: https://sites.google.com/site/massdgic/home/interconnection/technical-standards-review-group

Renewable energy generally: https://www.mass.gov/topics/renewable-energy

MADPU Net Metering Information: https://www.mass.gov/net-metering

MADOER SMART Program Information:  https://www.mass.gov/info-details/solar-massachusetts-renewable-target-smart-program

Who to contact in MA for your renewable energy question: https://www.mass.gov/info-details/who-to-contact-about-my-renewable-energy-question-or-concern

Massachusetts Utilities

National Grid / Supplement to Specifications for Electrical Installations / ESB 756-2019 ver. 5.0 (Section 7.8 includes voltage and frequency ride through and control requirements);

https://www9.nationalgridus.com/non_html/shared_constr_esb756.pdf

NSTAR ELECTRIC COMPANY d/b/a EVERSOURCE ENERGY STANDARDS FOR

INTERCONNECTION OF DISTRIBUTED GENERATION, M.D.P.U. No. 55,

Effective: February 1, 2018:

https://author.eversource.com/content/docs/default-source/rates-tariffs/ma-electric/55-tariff-ma.pdf?sfvrsn=8582c462_6

Unitil Energy Systems, Inc.  Interconnection Standards for Inverters Sized up To 100 kVA:

https://unitil.com/sites/default/files/pdfs/UES%20100%20KVA%20Interconnect%20Standard%202009_08_21_1.pdf

Individual Massachusetts Municipal Electric Utility Entity Interconnection Requirements:

https://www.mass.gov/guides/net-metering-guide

New Hampshire –

New Hampshire Public Utilities Commission

Liberty Utilities Electricity Delivery Service Tariff – NHPUC No. 20:

https://www.puc.nh.gov/Regulatory/Docketbk/2018/18-183/INITIAL%20FILING%20-%20PETITION/18-183_2018-12-10_GSEC_TARIFF.PDF

New Hampshire Electric Co-op Net Metering Requirements:

https://www.nhec.com/wp-content/uploads/2017/02/2017-Interconnection-Application-Package.pdf

Public Service Company of New Hampshire Interconnection Standards for Inverters Sized Up to 100 KVA, August 2009:

https://www.eversource.com/content/docs/default-source/builders-contractors/eversource's-interconnection-standards-for-inverters.pdf?sfvrsn=2dd9cf62_0

Unitil Energy Systems, Inc.  Interconnection Standards for Inverters Sized up To 100 kVA:

https://unitil.com/sites/default/files/pdfs/UES%20100%20KVA%20Interconnect%20Standard%202009_08_21_1.pdf

Rhode Island –

State of Rhode Island Public Utilities Commission and Division of Public Utilities and Carriers

Block Island Power Company Net Metering Application:

https://blockislandpowercompany.com/net-metering-application-2/

The Narragansett Electric Company Standards for Connecting Distributed Generation, Effective September 6, 2018:

https://www9.nationalgridus.com/non_html/RI_DG_Interconnection_Tariff.pdf

Pascoag Utility District – Electric Net Metering Policy, Requested Effective Date: June 1, 2010:

https://www.pud-ri.org/wp-content9999/uploads/2015/07/Net-Metering-Policy.pdf

Vermont –

Vermont Public Utility Commission

The Vermont Public Utility Commission issued an interconnection rule in 2006 that was largely modeled on the FERC Small Generator Interconnection Procedures at that time.  The rule has not been updated since 2006.

Links to the current rule as well as an application form and application instructions:

PUC Rule 5.500 – Interconnection Rule

https://puc.vermont.gov/sites/psbnew/files/doc_library/5500-electric-generation-interconnection-procedures_0.pdf

PUC Rule 5.500 – Application Form

https://puc.vermont.gov/sites/psbnew/files/doc_library/5500-revised-application_0.pdf

PUC Rule 5.500 – Application Instructions

https://puc.vermont.gov/sites/psbnew/files/doc_library/5500-revised-application-instructions_0.pdf

In addition, the Department petitioned the PUC to initiate a rulemaking to make adjustments to the interconnection rule in 2016.  As of the date of this DER Guidance document there were some filings and a workshop, but the process recently ended without resolution.  The PUC has indicated that they are likely to take up the process again in the near future however has not provided NPCC with a date.  Information regarding this process can be found here:  https://puc.vermont.gov/about-us/statutes-and-rules/proposed-changes-rule-5500

## Province of Quebec (some references are only available in French)

Section 112 of the Act respecting the Régie de l'énergie (chapter R-6.01) (the Act) reads as follows:

112. The Government may make regulations determining

[…]

(2.1)  for a particular source of electric power supply, the corresponding energy block and maximum price established for the purpose of fixing the cost of electric power referred to in section 52.2 or for the purposes of the supply plan provided for in section 72, or for the purposes of a tender solicitation by the electric power distributor under section 74.1;

(2.2)  the timeframe applicable to a public tender solicitation by the electric power distributor under section 74.1;

(2.3)  the maximum production capacity referred to in section 74.3, which may vary with the source of renewable energy or the class of customers or producers specified;

[…]

In cases where energy needs are to be supplied out of an energy block, a regulation may provide that only certain classes of suppliers may be invited to tender by the electric power distributor and that the quantity of electric power required under each supply contract may be limited.

Consequently, the Government has taken the following regulations, regarding Distributed Energy Resources (or DER), between 2003 and 2013:

- CONCERNANT le Règlement sur l’énergie produite par cogénération (Décret 1319-2003, 10 décembre 2003);

- CONCERNANT le Règlement sur l’énergie éolienne et sur l’énergie produite avec de la biomasse (Décret 352-2003, 5 mars 2003);

- CONCERNANT le Règlement modifiant le Règlement sur l’énergie produite par cogénération (Décret 298-2004, 29 mars 2004);

- CONCERNANT le Règlement sur le second bloc d’énergie éolienne (Décret 926-2005, 12 octobre 2005);

- CONCERNANT le Règlement sur l’énergie produite par cogénération à la biomasse (Décret 916-2008, 24 septembre 2008);

- CONCERNANT le Règlement sur un bloc de 250 MW d’énergie éolienne issu de projets autochtones (Décret 1043-2008, 29 octobre 2009);

- CONCERNANT le Règlement sur un bloc de 250 MW d'énergie éolienne issu de projets communautaires (Décret 1045-2008, 29 octobre 2008);

- CONCERNANT le Règlement modifiant le Règlement sur l’énergie produite par cogénération à la biomasse (Décret 9-2009, 7 janvier 2009);

- CONCERNANT le Règlement modifiant le Règlement sur un bloc de 250 MW d’énergie éolienne issu de projets communautaires (Décret 179-2009, 4 mars 2009);

- CONCERNANT le Règlement modifiant le Règlement sur un bloc de 250 MW d’énergie éolienne issu de projets autochtones (Décret 180-2009, 4 mars 2009);

- CONCERNANT le Règlement sur la capacité maximale de production visée dans un programme d’achat d’électricité pour des petites centrales hydroélectriques (Décret 336-2009, 25 mars 2009);

- CONCERNANT le Règlement modifiant le Règlement sur un bloc de 250 MW d’énergie éolienne issu de projets autochtones (Décret 520-2009, 29 avril 2009);

- CONCERNANT le Règlement modifiant le Règlement sur un bloc de 250 MW d’énergie éolienne issu de projets communautaires (Décret 521-2009, 29 avril 2009);

- CONCERNANT le Règlement modifiant le Règlement sur un bloc de 250 MW d'énergie éolienne issu de projets communautaires (Décret 468-2010, 2 juin 2010);

- CONCERNANT le Règlement modifiant le Règlement sur un bloc de 250 MW d'énergie éolienne issu de projets autochtones (Décret 469-2010, 2 juin 2010);

- CONCERNANT le Règlement sur la capacité maximale de production visée dans un programme d'achat d'électricité produite par cogénération à base de biomasse forestière résiduelle (Décret 1085-2011, 26 octobre 2011);

- CONCERNANT le Règlement sur un bloc de 450 mégawatts d'énergie éolienne (Décret 1149-2013, 6 novembre 2013).

The following regulations, or modified regulations, (marked in yellow in the section above) have led to four tender solicitations, targeting precise quantities, or energy blocks, of wind Energy:

- CONCERNANT le Règlement sur l’énergie éolienne et sur l’énergie produite avec de la biomasse (Décret 352-2003, 5 mars 2003);

- CONCERNANT le Règlement sur le second bloc d’énergie éolienne (Décret 926-2005, 12 octobre 2005);

- CONCERNANT le Règlement modifiant le Règlement sur un bloc de 250 MW d'énergie éolienne issu de projets communautaires (Décret 468-2010, 2 juin 2010);

- CONCERNANT le Règlement sur un bloc de 450 mégawatts d'énergie éolienne (Décret 1149-2013, 6 novembre 2013).

The Régie considers the results of these tenders when examining Hydro-Québec’s supply plan, as per section 72 of the Act:

72. With the exception of private electric power systems, a holder of exclusive electric power or natural gas distribution rights shall prepare and submit to the Régie for approval, according to the form, tenor and intervals fixed by regulation of the Régie, a supply plan describing the characteristics of the contracts the holder intends to enter into in order to meet the needs of Québec markets following the implementation of the energy efficiency measures. The supply plan shall be prepared having regard to

(1)  the risks inherent in the sources of supply chosen by the holder;

(2)  as concerns any particular source of electric power, the energy block established by regulation of the Government under subparagraph 2.1 of the first paragraph of section 112; and

[…]

When examining a supply plan for approval, the Régie shall consider such economic, social and environmental concerns as have been identified by order by the Government.

Sections 74.1 and 74.2 of the Act provide that the Régie oversees the process of such tender solicitations:

74.1. To ensure that suppliers responding to a tender solicitation are treated with fairness and impartiality, the electric power distributor shall establish and submit for approval to the Régie, which shall make its decision within 90 days, a tender solicitation and contract awarding procedure and a tender solicitation code of ethics applicable to the electric power supply contracts required to meet the needs of Québec markets in excess of the heritage pool, or the needs to be supplied out of an energy block determined by regulation of the Government under subparagraph 2.1 of the first paragraph of section 112.

The tender solicitation and contract awarding procedure shall, in particular,

(1)  allow all interested suppliers to tender by requiring the tender solicitation to be issued in due time;

(2)  grant equal treatment to all sources of supply and energy efficiency projects unless the tender specifications provide that all or part of the needs met by a particular source of supply must be supplied out of an energy block determined by regulation of the Government;

(3)  favour the awarding of supply contracts based on the lowest tendered price for the required quantity of electric power and in keeping with the required conditions, taking into account the applicable transmission cost and, where the tender specifications provide that all or part of the needs met by a particular source of supply must be supplied out of an energy block, taking into account the maximum price established by regulation of the Government; and

(4)  provide that, following a tender solicitation, contracts may be awarded to two or more suppliers, in which case a supplier offering the required quantity of electric power may be invited to reduce the quantity offered without modifying the tendered unit price.

An energy efficiency project to which a tender solicitation applies under subparagraph 2 of the second paragraph must meet the stability, sustainability and reliability requirements that apply to conventional sources of supply.

The Régie may dispense the electric power distributor from soliciting tenders for short-term contracts or where urgent needs must be met.

For the purposes of this section, the promoter of an energy efficiency project is deemed to be an electric power supplier.

74.2. The Régie shall monitor the implementation of the tender solicitation and contract awarding procedure and code of ethics provided for in section 74.1 and ascertain whether they are complied with. To that end, the Régie may require any document or information it considers useful. The Régie shall report its findings to the electric power distributor and to the supplier chosen.

The electric power distributor may not enter into an electric power supply contract unless it has obtained the approval of the Régie, under the conditions and in the cases determined by regulation by the Régie.

The Régie’s Website lists every docket related to this jurisdiction over Québec’s electricity distributor (in French only): Approval of supply contracts.

The Régie also considers DER when adopting specific reliability standards. Sections 85.2 and 85.7 of the Act read as follows:

85.2. The Régie shall ensure that electric power transmission in Québec is carried out according to the reliability standards it adopts.

85.7. The Régie may request the reliability coordinator to modify a standard filed or submit a new one, on the conditions it sets. It shall adopt reliability standards and set the date of their coming into force.

The reliability standards may

(1)  subject to section 85.10, provide for a schedule of sanctions, including financial penalties, that apply if standards are not complied with; and

(2)  refer to reliability standards set by a standardization agency that has entered into an agreement.

Docket R-4070-2018 (in French only) relates to a request by the reliability coordinator (HQCMÉ) and is still under examination by the Régie. It aims the adoption of reliability standards associated with Special Protection System (Remedial Action Scheme) and Dispersed Power Producing Resources.

We know you also contacted Hydro-Québec in this matter, but just in case, the following sections of Québec’ electricity distributor and transmitter’s web site might be useful, since they list the applicable technical codes, standards and requirements:

- http://www.hydroquebec.com/transenergie/fr/commerce/raccordement_distribution.html ;

- http://www.hydroquebec.com/transenergie/fr/commerce/raccordement_transport.html

## Province of Ontario

The current connection requirements for all resources can be found in Chapter 4 appendices 4.2 and 4.3 of the Market Rules.  http://www.ieso.ca/-/media/Files/IESO/Document-Library/Market-Rules-and-Manuals-Library/market-rules/mr-chapter4appx.pdf?la=en

The Independent Electric System Operator (IESO) is in the process of making updates to these requirements to be more specific about the requirements that apply to all DERs (not just storage).  http://www.ieso.ca/Sector-Participants/Engagement-Initiatives/Engagements/Updates-to-Performance-Requirements-Market-Rule-Appendices-4-2-and-4-3

The IESO is working on several white papers.  The one that was posted in 2019 called “Exploring Expanded DER Participation in the IESO-Administered Markets “ sets out the participation models that exist for DER in wholesale markets in general and in the IESO-Administered Markets (IAM) today and also identify the range of options that exist for expanded participation in the future. In addition, this paper provides a working definition of DER, sets out principles for integrating them into wholesale markets, offers an initial review of participation models in other jurisdictions, and identifies key barriers that may limit DER participation in the IAMs.

http://www.ieso.ca/-/media/Files/IESO/Document-Library/White-papers/White-paper-series-Conceptual-Models-for-DER-Participation.pdf?la=en

As noted above, the Ontario Energy Board is also engaging in several stakeholder activities in this area.  Below are the links to those activities.  The Ontario Energy Board has combined the first two initiatives into one engagement.

- Responding to Distributed Energy Resources (DER)* - The purpose of this initiative is to develop a more comprehensive regulatory framework that facilitates investment and operation of DER based-on value to consumers and supports effective DER integration so the benefits of sector evolution can be realized.

https://www.oeb.ca/industry/policy-initiatives-and-consultations/responding-distributed-energy-resources-ders

- Utility Remuneration*  -   The purpose of this initiative is to identify how to remunerate utilities in ways that make them indifferent to traditional or innovative solutions, better supports their pursuit of least cost solutions, strengthens their focus on long-term value and requires them to reflect the impact of sector evolution in their system planning and operations.

https://www.oeb.ca/industry/policy-initiatives-and-consultations/utility-remuneration

- DER Connections Review – The purpose of this initiative to review its requirements regarding the connection of distributed energy resources (DER) by licensed electricity distributors. The purpose of this initiative is to identify any barriers to the connection of DER, and where appropriate to standardize and improve the connection process. The review will be focused on connection of electricity generation and storage facilities connected to the distribution system, either in front or behind the distributor's meter.

https://www.oeb.ca/industry/policy-initiatives-and-consultations/distributed-energy-resources-der-connections-review

The contact for this information would be Customer Relations (customer.relations@ieso.ca)

## Province of New Brunswick

Within the province, DER is referred to as “Embedded Generation” or “Distributed Generation.”  Regulation from the New Brunswick Energy and Utility Board may be found here:

http://laws.gnb.ca/en/ShowPdf/cs/2013-c.7.pdf

Ènergie NB Power’s embedded generation may be found here:

https://www.nbpower.com/en/products-services/embedded-generation/

# Appendix F, ISO New England

ISO-NE specific Inverter requirements are as follows in the below table and the link

Inverter Source Requirement Document of ISO New England

The following additional performance requirements are applied in one NPCC Area and are provided as an example:

- In the Permissive Operation region above 0.5 p.u., inverters shall ride-through in Mandatory Operation mode, and

- In the Permissive Operation region below 0.5 p.u., inverters shall ride-through in Momentary Cessation mode.

Table I: Inverters’ Voltage Trip Settings

| Shall Trip – IEEE Std 1547-2018 (2nd ed.) Category II |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Shall Trip Function | Required Settings |  | Comparison to IEEE Std 1547-2018 (2nd ed.) default settings and ranges of allowable settings for Category II |  |  |
|  | Voltage (p.u. of nominal voltage) | Clearing Time(s) | Voltage | Clearing Time(s) | Within ranges of allowable settings? |
| OV2 | 1.20 | 0.16 | Identical | Identical | Yes |
| OV1 | 1.10 | 2.0 | Identical | Identical | Yes |
| UV1 | 0.88 | 2.0 | Higher (default is 0.70 p.u.) | Much shorter (default is 10 s) | Yes |
| UV2 | 0.50 | 1.1 | Slightly higher (default is 0.45 p.u.) | Much longer (default is 0.16 s) | Yes |

Table II: Inverters’ Frequency Trip Settings

| Shall Trip Function | Required Settings |  | Comparison to IEEE Std 1547-2018 (2nd ed.) default settings and ranges of allowable settings for Category I, Category II, and Category III |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Frequency (Hz) | Clearing Time(s) | Frequency | Clearing Time(s) | Within ranges of allowable settings? |
| OF2 | 62.0 | 0.16 | Identical | Identical | Yes |
| OF1 | 61.2 | 300.0 | Identical | Identical | Yes |
| UF1 | 58.5 | 300.0 | Identical | Identical | Yes |
| UF2 | 56.5 | 0.16 | Identical | Identical | Yes |

Table III: Inverters’ Voltage Ride-through Capability and Operational Requirements

| Voltage Range (p.u.) | Operating Mode/ Response | Minimum Ride-through Time(s) (design criteria) | Maximum Response Time(s) (design criteria) | Comparison to IEEE Std 1547-2018 (2nd ed.) for Category II |
| --- | --- | --- | --- | --- |
| V > 1.20 | Cease to Energize | N/A | 0.16 | Identical |
| 1.175 < V ≤ 1.20 | Permissive Operation | 0.2 | N/A | Identical |
| 1.15 < V ≤ 1.175 | Permissive Operation | 0.5 | N/A | Identical |
| 1.10 < V ≤ 1.15 | Permissive Operation | 1 | N/A | Identical |
| 0.88 ≤ V ≤ 1.10 | Continuous Operation | infinite | N/A | Identical |
| 0.65 ≤ V < 0.88 | Mandatory Operation | Linear slope of 8.7 s/1 p.u. voltage starting at 3 s @ 0.65 p.u.: 𝑇 = 3 s + 8.7 s (𝑉 − 0.65 p.u.) 𝑉𝑅𝑇 1 p. u. | N/A | Identical |
| 0.45 ≤ V < 0.65 | Permissive Operation a,b | 0.32 | N/A | See footnotes a & b |
| 0.30 ≤ V < 0.45 | Permissive Operation b | 0.16 | N/A | See footnote b |
| V < 0.30 | Cease to Energize | N/A | 0.16 | Identical |

The following additional operational requirements can be used. Provided as an example:

- In the Permissive Operation region above 0.5 p.u., inverters shall ride-through in Mandatory Operation mode, and

- In the Permissive Operation region below 0.5 p.u., inverters shall ride-through in Momentary Cessation mode with a maximum response time of 0.083 seconds.

Table IV: Inverters’ Frequency Ride-through Capability

| Frequency Range (Hz) | Operating Mode | Minimum Time(s) (design criteria) | Comparison to IEEE Std 1547-2018 (2nd ed.) for Category II |
| --- | --- | --- | --- |
| f > 62.0 | No ride-through requirements apply to this range |  | Identical |
| 61.2 < f ≤ 61.8 | Mandatory Operation | 299 | Identical |
| 58.8 ≤ f ≤ 61.2 | Continuous Operation | Infinite | Identical |
| 57.0 ≤ f < 58.8 | Mandatory Operation | 299 | Identical |
| f < 57.0 | No ride-through requirements apply to this range |  | Identical |

Table V: Grid Support Utility Interactive Inverter Functions Status

| Function | Default Activation State |
| --- | --- |
| SPF, Specified Power Factor | OFF2 |
| Q(V), Volt-Var Function with Watt or Var Priority | OFF Default value: 2% of maximum current output per second |
| SS, Soft-Start Ramp Rate | ON |
| FW, Freq-Watt Function OFF | OFF |

# Appendix G, State Renewable and Green Energy Requirements

New York State

70% renewable energy by 2030

85% reduction of Greenhouse Gas emissions by 2050

6,000 MW of distributed solar by 2025

3,000 MW of energy storage by 2025

Carbon free electricity system by 2040

Connecticut

Carbon free electricity system by 2040

Renewable Portfolio Standard - https://portal.ct.gov/PURA/RPS/Renewable-Portfolio-Standards-Overview

Vermont

90% of Vermont's overall energy needs from renewable sources by 2050

Reduce Vermont's greenhouse gas (GHG) emissions by 50% from the 1990 baseline level by 2028, and by 75% from the 1990 level by 2050

New Hampshire

20% to 25% reduction in Greenhouse Gas emissions by 2032

25.2% renewable energy by 2025

Rhode Island

100% renewable energy by 2030

1,000 MW of new clean energy installed in 2020

Maine

80% renewable energy by 2030

An example of a reliability risk not addressed is remote dispatch of DER. A significant challenge that has been found by some NPCC members is that DER Operators can be anywhere in the world and that as a result, communications can be significantly delayed, leading to reliability risks. This includes time zone challenges and language challenges,

“reliable operation” is defined in 16 U.S. Code § 824o and means “operating the elements of the bulk-power system within equipment and electric system thermal, voltage, and stability limits so that instability, uncontrolled separation, or cascading failures of such system will not occur as a result of a sudden disturbance, including a cybersecurity incident, or unanticipated failure of system elements.”

https://www.cpuc.ca.gov/Rule21/      Electric Rule 21 is a tariff that describes the interconnection, operating and metering requirements for generation facilities to be connected to a utility’s distribution system. The tariff provides customers wishing to install generating or storage facilities on their premises with access to the electric grid while protecting the safety and reliability of the distribution and transmission systems at the local and system levels.

At the time of this guidance document development, these include but are not limited to: NERC (e.g. SPIDER WG, IRPTF, Events Analysis, Modelling and Standards process), Inverter- Based Resources Task Force), IEEE (IEEE Std 1547-2018, P2800), and various state initiatives such as the New York ITWG, Other Regional, Provincial and State  initiatives.

At this time there has not been an assessment of potential change in sensitivity (increase or decrease) to the effects of GMD from the presence of high DER penetration. This is a potential reliability risk to be evaluated in the future.

NERC report on Loss of Wind Turbines During System Disturbances : NERC Report-Loss of Wind Turbines

This document can be found on the Department of Public Service website (www.dps.ny.gov) at the Distributed Generation/Interconnections tab under Interconnection Technical Working Group Information.

Questions exist regarding which entities should be responsible for providing DER data to the Planning Coordinator for the purposes of model building.  NERC is working on this issue.

NY SIR is the New York Standardized Interconnection Requirement.

The functionality is required to be present, but the default state is to have this functionality disabled unless otherwise directed by the area EPS operator

The functionality is required to be present, but the default state is to have this functionality disabled unless otherwise directed by the area EPS operator

Available here: https://www.nerc.com/comm/PC/Documents/Summary_of_Activities_BPS-Connected_IBR_and_DER.pdf

See NERC Rule of Procedure #313 on page 15 of the NERC Rules of Procedure 3-9-2018.

The Reliability Principles were summarized in the NPCC 2018 Strategic Review Report.

The method of identifying critical facilities is currently embodied in the NPCC A-10 Classification of bulk power system Elements document, currently under review by the CP-11 Working Group with a due date of October 31, 2018.

The NPCC bulk power system is identified by a specific list of facilities in the NPCC region deemed critical by the NPCC A-10 classification process. This list is not determined based on the definition of the ERO bulk power system, which is defined in the US 2005 EPACT as:

‘‘(A) facilities and control systems necessary for operating an interconnected electric energy transmission network (or any portion thereof); and

‘‘(B) electric energy from generation facilities needed to maintain transmission system reliability.

The term does not include facilities used in the local distribution of electric energy.

There are other documents which supplement the Directories, for instance the NPCC Compliance Guidance Statements. These documents usually refer to NERC standards applicability and can be found here: NPCC CGS

NERC Rule of Procedure #313 (page 15) permits the following: “Regional Entities may develop Regional Criteria that are necessary to implement, to augment, or to comply with NERC Reliability Standards, but which are not Reliability Standards. Regional Criteria may also address issues not within the scope of Reliability Standards, such as resource adequacy. “

Reference NERC’s recent filing with FERC regarding Resilience for a more complete discussion of the relationship between resilience, the NERC standards and the NAICS Resilience Framework. FERC is expected to define resilience in the course of its current examination of electric system resilience concepts.

In the US, Presidential Policy Directive – 21 defines resilience as “The ability to prepare for and adapt to changing conditions and withstand and recover rapidly from disruptions. Resilience includes the ability to withstand and recover from deliberate attacks, accidents, or naturally occurring threats or incidents”.