Contents

Executive Summary	3

Introduction and Objective	3

NPCC Reliability Principles	4

NPCC DER Impact Reporting	7

DER BES Impact Considerations	8

NPCC Interconnection Guidance	8

Voltage Response	9

Frequency Support	9

Reconnection to the Utility System	10

Inverters	10

Certification per UL 1741 SA as grid support utility interactive inverters	11

Minimum Protective Functions	13

Metering	15

Power Quality	15

Power Factor	15

Islanding	15

Underfrequency Load Shedding Programs	16

Effective Grounding for DER	16

Energy Storage Systems for DER	17

DER BES Recommendations	17

Appendix A NPCC DER Impact Reporting Form	18

Appendix B NPCC Area Comparison	20

# Executive Summary

The Northeast Power Coordinating Council, Inc. (NPCC) is responsible for promoting and enhancing the reliability of the international, interconnected bulk power system in Northeastern North America.

As Distributed Energy Resources (DER), installed on the distribution system, continue to replace traditional industry generation resources this transformation will impact the reliability and resilience of the Bulk Electric System (BES).  Historically, the North American Electric Reliability Corporation (NERC) Reliability Standards have not been applicable to equipment on the distribution system unless such equipment has a direct impact on the reliable operation of the BES; however as penetration of DER increases planning and operating assessments will need to accurately represent how DER interacts with the load characteristics of the distribution system.   Development of this document was initiated by the NPCC Board of Directors to develop Regional guidance and suggested approaches to assist NPCC Members in modelling assessments for the operation and planning of DER within the NPCC Region. This initial guidance does not consider specific rooftop solar or individual installations of wind turbines or other localized behind the revenue meter DER. (although there is process described in this document which allows entities to identify impacts to NPCC so they can be addressed and acknowledged).  NPCC Staff has developed this guidance as an initial document to leverage existing interconnection requirements at the distribution level and identify opportunities and potential gaps that may exist in order to promote good utility interconnection practices beneficial to reliability of the NPCC Region.

DER for the purpose of this guidance means any non-BES real or reactive resource (generating unit, multiple generating units at a single location, distributed generation, battery storage, etc.) located within the boundary of any distribution utility and not behind revenue metering, unless specifically indicated.

# Introduction and Objective

As DERs continue to penetrate the electric system at the “grid edge” or distribution system, and replace conventional transmission grid connected carbon producing and nuclear generation resources, there is an increasing reliability related need to understand the effect of these DER resources.  It is important to understand how DERs are interconnected, planned, operated and how they interact with the transmission grid.  Reliably and securely integrating DER into the electric system will require a comprehensive approach utilizing perspectives from areas, such as, DER design, modeling, planning, relay coordination, and operations as well as consideration of regulatory and jurisdictional issues from both a U.S. and Canadian perspective.  Appendix B of this document provides a comparison of NPCC’s Area requirements to help identify opportunities for guidance.

DERs are capable of bringing a number of enhancements to reliability.  As an example, inverters, which convert direct current to alternating current, have microprocessor based control systems. These microprocessors operate with a very high internal clock speed (on the order of MHz) and are capable of fine resolution frequency measurement and electronically controlling the upward ramping of DER output and downwards ramping of DER output potentially ceasing the injection of current into the electric system at very high speeds depending on control decisions. Inverters are capable of remaining physically connected (breaker closed) and not injecting current well within normal 3-5 cycle breaker clearing times.  This type of response can provide significant reliability benefits if control systems are properly configured to reliably implement it. Additionally, for upward ramping, the distribution level connected resource must be available and operate with the “headroom.”  In order to realize the benefits which DER are capable of to enhance reliability it is important to understand the hosting capacity of the distribution system feeders where they are being located and the DER’s expected capabilities, capacity, and operation.  In addition to improving system response, DER will enhance Resilience by decentralizing generation and affording flexibility during restoration beyond that of normal system restoration plans.

While DERs present opportunities to enhance reliability, they also introduce challenges at the transmission/distribution interface.  Interoperability with the transmission system is not solely determined at the point of interconnection. System needs such as visibility of generation state is essential for transmission operators to maintain situational awareness for operations purposes, for forecasting and integrated system planning to ensure reliability is maintained.  Presently there are no study tools in general use to perform fully integrated studies of transmission and distribution which would allow both systems to be modeled and studied (in steady state and dynamically) together, although work is underway in this regard.

In recognition of both benefits and challenges, the approach taken with this first NPCC DER                                                       guidance document was to collect interconnection requirements within the NPCC Region as well as in other areas of the NERC Electric Reliability Organization (ERO) Enterprise.  There are some specific issues where opportunity exists to ensure coordination across the NPCC Region.  The intent of this document is to identify risks and establish guidance, where possible, for interconnection of DER. NPCC will leverage existing requirements and proposed modifications for processes for a NPCC Region-wide approach to interconnecting DER to distribution systems and reliably operating DER in conjunction with the BES.  It must be recognized that DERs may not be placed optimally and in areas where deliverability to load may not be ideal.  In this respect any specific recomendations in this document will be subject to the requirements  of the interconnecting distribution utility.

# NPCC Reliability Principles

Using its membership structure and governance authority to create and apply Regional Criteria, NPCC Member adherence to Regional criteria contributes to a more robust level of reliability beyond NERC ERO reliability “results-based” standards / requirements.  For example, NPCC Criteria mandate specific design requirements for assets in NPCC Member facilities. NPCC‘s approach to reliability and resilience can be summarized in Principles that guide NPCC Members in their effort to meet or exceed NERC requirements.  NPCC’s core Reliability Principles and supporting activities support the NERC Bulk Electric System and NPCC’s Bulk Power System reliability.

Also recognized is the critical role that DER will have with respect to reliability and resilience of the Bulk Electric System.  Specifically, DER can contribute to the Robustness of the system and provide increased resource support within islands during any system separations. As DER continues to penetrate the system changes to NPCC’s Underfrequency Load Shedding program may be required.

The NPCC Reliability Principles include:

- Focus on the most important system components: In order to focus resources to those portions of the power delivery system most important (critical) to overall reliability, NPCC Members employ mechanism(s) for identifying those facilities that are most critical to the reliable planning and operation of the power delivery assets in the NPCC region. These critical facilities collectively are identified as the NPCC Bulk Power System.

- Application of Criteria beyond NERC requirements to identified critical facilities: Where, in the opinion of NPCC’s Membership, the NERC standards do not adequately specify a necessary performance or design outcome in a given technical, operation or planning area, NPCC Criteria govern the design of their respective portions of the NPCC Bulk Power System planning and operation activities.

- NPCC Members support the Criteria: NPCC’s Full Members in accordance with the NPCC Bylaws are committed to designing and operating their systems to meet the NPCC Criteria under peer review of the NPCC Full Members.

- No conflict with NERC Requirements: The NPCC Criteria supplement, improve upon where necessary, benefit, and do not conflict with or duplicate the results-based performance requirements of NERC standards where they apply to the NPCC Bulk Power System. NPCC adjusts its regional Criteria to retire or adapt to any new NERC requirements as they come into effect as necessary.

- Include design specifications where needed: The NPCC Criteria and related guidelines and procedures provide design criteria and practices to assure implementation.  NPCC Directories go into greater detail regarding how to accomplish a given reliability result, where NERC standards may simply require a “reliability result.”

- Resilience has always been an element of NPCC Criteria: Based on experience, resilience  is a necessary constituent component of reliability and it is important both to electricity consumers and regulatory authorities in NPCC’s Region.  NPCC Criteria provide substantial resilience benefits to the NPCC bulk power system by providing:

  - Robustness – The ability to withstand disturbances by supporting operations in a more secure state.

  - Resourcefulness – The ability to detect and manage a crisis as it unfolds.

  - Rapid recovery – The ability to get services back as quickly as possible in a coordinated and controlled manner.

  - Adaptability – The ability to absorb new lessons from events.

NPCC Criteria serve to establish a superior pre-event starting point, make the trough less severe and the recovery faster

NERC RISC Proposed Model of Resilience

# NPCC DER Impact Reporting

In order to ensure the reliability of the interconnected bulk power system in Northeastern North America as DER continues to proliferate throughout the distribution systems within the NPCC Region, it is important to have a centralized DER impact reporting mechanism.  The NPCC Regional Standard Committee (RSC) created an impact reporting form and process that allows entities to report DER impacts and to seek guidance regarding emerging issues and reliability risks that affect or could affect the reliable performance of the Bulk Electric System (BES) see Appendix A.  The Word version of the below form resides on the NPCC website at:

BES Impact Reporting Form

Impact reporting and associated process provide an orderly mechanism to review reliability impacts submitted to NPCC which is a collaborative review by the Reliability Coordinating Committee and Regional Standards Committee.  The process is shown below.

# DER BES Impact Considerations

NPCC’s Regional Standards Committee and Task Force review of DER as it pertains to the NPCC Region’s BES performance has identified a number of areas which, going forward, may warrant further and continual monitoring and analysis.  NPCC has identified the following items that should be carefully tracked as DER levels (total MWs) increase.

- DER performance with respect to voltage and frequency ride through as well as the ability to provide regulation and reserves need to be consistent with the specifications of resources on the BES.

- DER availability and quality of forecasting to determine interoperability and day-ahead commitment.

- Observability:  System operators must have sufficient situational awareness of DER to reliably operate the BES.

- Increasing penetration of DER will eventually affect Underfrequency Load Shed programs.

- Effect of Non-linear devices such as inverters producing harmonics on the power system.

- Impact of increasing DER on System Restoration and Black Start Plans.

- DER Markets: Encouraging Points of Common Coupling and injection to where it is best utilized and at appropriate levels.

# NPCC Interconnection Guidance

The DER owner must be prepared to provide appropriate protection and control equipment, including a protective device and communications system that utilizes an automatic disconnecting device which will disconnect the generation under various conditions. For example in the event that the portion of the utility system that serves the generator is de-energized for any reason or for a fault in the generator-owner’s system.  There is also the possibility of over generation as has been demonstrated in CA, when the system operator runs out of load to absorb the available generation.  Operating procedures for selecting which generation to curtail need to be in place. Some areas of the country are planning to use market mechanisms to address this issue. The DER owner’s protection and control equipment also shall be capable of automatically disconnecting the generation from the system to which it is connected upon detection of a utility system fault.

The type and size of the generation facility or energy storage system is based on electrical generator or inverter AC nameplate rating.

The DER owner’s protection and control scheme must be designed to ensure that the generation remains in operation when the frequency and voltage of the utility system is within the limits specified by the required operating ranges. Upon request from the utility, the DER owner shall provide documentation detailing compliance with the requirements set forth in this document.

The specific design of the protection, control, and grounding schemes will depend on the size and characteristics of the DER owner’s generation, as well the DER owner’s load level, in addition to the characteristics of the particular portion of the utility’s system where the DER owner is interconnecting.

The DER owner should have, as a minimum, an automatic disconnect device(s) sized to meet all applicable local, state, and federal codes and operated by over and under voltage and over and under frequency protection. For three-phase installations, the over and under voltage function should be included for each phase and the over and under frequency protection on at least one phase. All phases of a generator or inverter interface shall disconnect for voltage or frequency trip conditions sensed by the protective devices. Voltage protection shall be wired phase to ground for single phase installations and for applications using wye grounded-wye grounded service transformers.

The settings below are listed for single-phase and three-phase applications using wye grounded- wye grounded service transformers or wye grounded-wye grounded isolation transformers. For applications using other transformer connections, a site-specific review will be performed by the utility and the revised settings identified in Step 6 of the Application Process.

The requirements set forth in this document are intended to be consistent with those contained in the most current version of IEEE Standard 1547, Standard for Interconnecting Distributed Resources with Electric Power Systems. The requirements in IEEE 1547 above and beyond those contained in this document shall be followed and any other Standards included in or referenced to in IEEE Std. 1547 shall be adhered to.

## Voltage Response

Operating range for the generators should be from 0.88 to 1.10 per unit of nominal voltage magnitude. In addition, the generator should not cause the system voltage at the Point of Common Coupling (PCC) to deviate from a range of 0.95 to 1.05 per unit of the utility system voltage. For excursions outside these limits the protective device should automatically initiate a disconnect sequence from the utility system as detailed in the most current version of IEEE Std. 1547. Clearing time is defined as the time the range is initially exceeded until the DER owner’s equipment ceases to energize the PCC and includes detection and intentional time delay. Other static or dynamic voltage functionalities shall be permitted as agreed upon by the utility and DER owner.

## Frequency Support

Frequency support is provided through the combined interactions of synchronous inertia and frequency response. Working in a coordinated way, these characteristics and services arrest the decline in frequency and eventually return the frequency to the desired level.  As increased levels of DER are introduced to the system synchronous inertia will be displaced.  Future work in the study of inertia on both an interconnection-wide and local basis will certainly be done in the future.

The operating range for the DER distribution connected resources should be similar to that of BES connected resources.  The operating band for frequency of a DER resource’s operating range should be at least from 59.3 Hz to 60.5 Hz as required by NPCC and NERC UFLS standards.  If deemed necessary, due to abnormal system conditions, the utility may request that the generator operate at frequency ranges below 59.3 Hz in coordination with the current under frequency load shedding schemes of NPCC and the local utility system. For excursions outside these limits the protective device shall automatically initiate a disconnect sequence from the utility system as detailed in the most current version of IEEE 1547. Clearing time is defined as the time the range is initially exceeded until the DER owner’s equipment ceases to energize the PCC and includes detection and intentional time delay. Other static or dynamic frequency functionalities shall be permitted as agreed upon by the utility and DER owner.

## Reconnection to the Utility System

If the generation facility is disconnected as a result of the operation of a protective device, the DER owner’s equipment shall remain disconnected until the utility’s service voltage and frequency have recovered to acceptable voltage and frequency limits as defined in the most current version of IEEE Std. 1547 for a minimum of five (5) minutes. Systems greater than 25 kW that do not utilize inverter based interface equipment shall not have automatic recloser capability unless otherwise approved by the utility. If the utility determines that a facility must receive permission to reconnect, then any automatic reclosing functions must be disabled and verified to be disabled during verification testing.

Utilities in other parts of the Eastern Interconnection who have experienced increased levels of DER have determined that during system restoration, DER should not be allowed to return to service until the system has been reestablished and is in a stable operating state.  As traditional resources on the BES are retired and the grid is will be increasingly reliant on grid edge DER on the distribution, Black Start and System Restoration plans will have to be adjusted accordingly.

## Inverters

Direct current generation can only be installed in parallel with the utility’s system using a synchronous inverter. The design shall be such as to disconnect the synchronous inverter upon a utility system event. Inverters intended to provide local grid support during system events that result in voltage and/or frequency excursions as described in this document and shall be provided with the required onboard functionality to allow for the equipment to remain online for the duration of the event.

All applicable inverter-based applications shall:

- be certified per the requirements of UL 1741 SA as a grid support utility interactive inverter

- have the voltage and frequency trip settings as specified by the interconnecting utility

- have the abnormal performance capabilities (ride-through)

- comply with other grid support utility interactive inverter functions statuses

It is recommended that equipment be selected from the Department of Public Service “Certified Interconnection Equipment list” maintained on the Commission’s website. Interconnected DG systems utilizing equipment not found in such list must meet all functional requirements of the current version of IEEE Std 1547 and be protected by utility grade relays (as defined in these requirements) using settings approved by the utility and verified in the field. The field verification test must demonstrate that the equipment meets the voltage and frequency requirements detailed in this section.

Synchronization or re-synchronization of an inverter to the utility system shall not result in a voltage deviation that exceeds the requirements contained in Section II.E, Power Quality. Only inverters designed to operate in parallel with the utility system shall be utilized for that purpose.

## Certification per UL 1741 SA as grid support utility interactive inverters

In the interim period while IEEE P1547.1 is not yet revised and published, certification of all inverter-based applications:

- Shall be compliant with only those parts of Clause 6 (Response to Area EPS abnormal conditions) of IEEE Std 1547-2018 (2nd ed.)1 that can be certified per the type test requirements of UL 1741 SA (September 2016). IEEE Std. 1547-2018 (2nd ed.) in combination with this document replaces other Source Requirements Documents (SRDs), as applicable;

- May be sufficiently achieved by certifying inverters as grid support utility interactive inverters per the requirements of UL 1741 SA (September 2016) with either CA Rule 21 or Hawaiian Rule 14H as the Source Requirement Document (SRD). Such inverters are deemed capable of meeting the requirements of this document.

- Applications should have the voltage and frequency trip points specified in Tables I and II below.

- Abnormal performance capability (ride-through) requirements for inverter based applications shall have the ride-through capability per abnormal performance category II of IEEE Std 1547-2018 (2nd ed.) as quoted in Tables III and IV.

The following additional performance requirements shall apply for all inverters:

- In the Permissive Operation region above 0.5 p.u., inverters shall ride-through in Mandatory Operation mode, and

- In the Permissive Operation region below 0.5 p.u., inverters shall ride-through in Momentary Cessation mode.

Table I: Inverters’ Voltage Trip Settings (ISO-NE Tech Bulletin)

| Shall Trip – IEEE Std 1547-2018 (2nd ed.) Category II |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Shall Trip Function | Required Settings |  | Comparison to IEEE Std 1547-2018 (2nd ed.) default settings and ranges of allowable settings for Category II |  |  |
|  | Voltage (p.u. of nominal voltage) | Clearing Time(s) | Voltage | Clearing Time(s) | Within ranges of allowable settings? |
| OV2 | 1.20 | 0.16 | Identical | Identical | Yes |
| OV1 | 1.10 | 2.0 | Identical | Identical | Yes |
| UV1 | 0.88 | 2.0 | Higher (default is 0.70 p.u.) | Much shorter (default is 10 s) | Yes |
| UV2 | 0.50 | 1.1 | Slightly higher (default is 0.45 p.u.) | Much longer (default is 0.16 s) | Yes |

Table II: Inverters’ Frequency Trip Settings

| Shall Trip Function | Required Settings |  | Comparison to IEEE Std 1547-2018 (2nd ed.) default settings and ranges of allowable settings for Category I, Category II, and Category III |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Frequency (Hz) | Clearing Time(s) | Frequency | Clearing Time(s) | Within ranges of allowable settings? |
| OF2 | 62.0 | 0.16 | Identical | Identical | Yes |
| OF1 | 61.2 | 300.0 | Identical | Identical | Yes |
| UF1 | 58.5 | 300.0 | Identical | Identical | Yes |
| UF2 | 56.5 | 0.16 | Identical | Identical | Yes |

Table III: Inverters’ Voltage Ride-through Capability and Operational Requirements

| Voltage Range (p.u.) | Operating Mode/ Response | Minimum Ride-through Time(s) (design criteria) | Maximum Response Time(s) (design criteria) | Comparison to IEEE Std 1547-2018 (2nd ed.) for Category II |
| --- | --- | --- | --- | --- |
| V > 1.20 | Cease to Energize | N/A | 0.16 | Identical |
| 1.175 < V ≤ 1.20 | Permissive Operation | 0.2 | N/A | Identical |
| 1.15 < V ≤ 1.175 | Permissive Operation | 0.5 | N/A | Identical |
| 1.10 < V ≤ 1.15 | Permissive Operation | 1 | N/A | Identical |
| 0.88 ≤ V ≤ 1.10 | Continuous Operation | infinite | N/A | Identical |
| 0.65 ≤ V < 0.88 | Mandatory Operation | Linear slope of 8.7 s/1 p.u. voltage starting at 3 s @ 0.65 p.u.: 𝑇 = 3 s + 8.7 s (𝑉 − 0.65 p.u.) 𝑉𝑅𝑇 1 p. u. | N/A | Identical |
| 0.45 ≤ V < 0.65 | Permissive Operation a,b | 0.32 | N/A | See footnotes a & b |
| 0.30 ≤ V < 0.45 | Permissive Operation b | 0.16 | N/A | See footnote b |
| V < 0.30 | Cease to Energize | N/A | 0.16 | Identical |

The following additional operational requirements shall apply for all inverters:

- In the Permissive Operation region above 0.5 p.u., inverters shall ride-through in Mandatory Operation mode, and

- In the Permissive Operation region below 0.5 p.u., inverters shall ride-through in Momentary Cessation mode with a maximum response time of 0.083 seconds.

Table IV: Inverters’ Frequency Ride-through Capability

| Frequency Range (Hz) | Operating Mode | Minimum Time(s) (design criteria) | Comparison to IEEE Std 1547-2018 (2nd ed.) for Category II |
| --- | --- | --- | --- |
| f > 62.0 | No ride-through requirements apply to this range |  | Identical |
| 61.2 < f ≤ 61.8 | Mandatory Operation | 299 | Identical |
| 58.8 ≤ f ≤ 61.2 | Continuous Operation | Infinite | Identical |
| 57.0 ≤ f < 58.8 | Mandatory Operation | 299 | Identical |
| f < 57.0 | No ride-through requirements apply to this range |  | Identical |

Table V: Grid Support Utility Interactive Inverter Functions Status

| Function | Default Activation State |
| --- | --- |
| SPF, Specified Power Factor | OFF2 |
| Q(V), Volt-Var Function with Watt or Var Priority | OFF Default value: 2% of maximum current output per second |
| SS, Soft-Start Ramp Rate | ON |
| FW, Freq-Watt Function OFF | OFF |

## Minimum Protective Functions

Protective system requirements for distributed generation facilities result from an assessment of many factors, including but not limited to:

• Type and size of the distributed generation facility

• Voltage level of the interconnection

• Location of the distributed generation facility on the circuit

Distribution transformer

• Distribution system configuration

• Available fault current

• Load that can remain connected to the distributed generation facility under isolated conditions

• Amount of existing distributed generation on the local distribution system.

It is not possible to standardize protection requirements according to any single criteria. Minimum protective function requirements shall be as detailed in the Table VI below. Function numbers, as detailed in the latest version of ANSI C37.2, are listed with each function. All voltage, frequency, and clearing time set points shall be field adjustable.

Table VI: Grid Support Minimum Protective Functions

| Synchronous Generators | Induction Generators | Inverters |
| --- | --- | --- |
| Over/Under Voltage (Function 27/59) | Over/Under Voltage (Function 27/59) | Over/Under Voltage (Function 27/59) |
| Over/Under Frequency (Function 81O/81U) | Over/Under Frequency (Function 81O/81U) | Over/Under Frequency (Function 81O/81U) |
| Anti-Islanding Protection | Anti-Islanding Protection | Anti-Islanding Protection |
| Overcurrent (Function 50P/50G/51P/51G) | Overcurrent (Function 50P/50G/51P/51G) | Overcurrent (Function 50P/50G/51P/51G) |

For energy storage systems or distributed generation where net export is limited, Reverse Power (Function 32) should be required.

The need for additional protective functions will be determined by the utility on a case- by-case basis. If the utility determines a need for additional functions, it will notify the DER owner of the requirements. The notice should include a description of the specific aspects of the utility system that necessitate the addition, and ideally, explicit justification for the necessity of the enhanced capability. The connecting utility will specify and provide settings for those functions that the utility designates as being required to satisfy their individual protection practices. Any protective equipment or setting specified by the utility must not be changed or modified at any time by the DER owner without consent from the utility.

The DER owner shall be responsible for ongoing compliance with all applicable local, state, and federal codes and standardized interconnection requirements as they pertain to the interconnection of the generating equipment. Protective devices shall utilize their own current transformers and potential transformers and not share electrical equipment associated with utility revenue metering.

A failure of the DER owner’s protective devices, including loss of control power, shall open the automatic disconnect device, thus disconnecting the generation from the utility system. A DER owner’s protection equipment shall utilize a non-volatile memory design such that a loss of internal or external control power, including batteries, will not cause a loss of interconnection protection functions or loss of protection set points.

All interface protection and control equipment shall operate as specified independent of the calendar date.

For monitoring and control of new DG projects, the most current version of the Monitoring and Control Criteria should be employed by the utilities to evaluate the need for such equipment in New York and considered in the NPCC region if no other local criteria are available. The New York Monitoring and Control Criteria document was developed and agreed to through a collaborative process as part of the Interconnection Technical Working Group (ITWG). This document can be found on the Department of Public Service website (www.dps.ny.gov) at the Distributed Generation/Interconnections tab under Interconnection Technical Working Group Information. The communications hardware, protocols, and data models must comply with local utility standards.

Also and fundamentally, existing over-current protections in distribution system are typically designed to clear line and ground faults occurring downstream from their location, as the source feeding the fault is only the transformer station. Connecting a DER provides another source supplying the fault, and the fault contribution from the facility might cause protection to operate non-selectively for reverse faults, out of the protected zone. If the maximum reverse fault current through a non-directional fault-interrupting device exceeds the setting of the device, the fault-interrupting device should be considered with a directional feature to prevent tripping for reverse fault current flow. For instance, phase protection could be replaced with an impedance relay (function 21) if required.

## Metering

Metering requirements shall be determined by the configuration of the DER system. New metering or modifications to existing metering will be reviewed on a case-by-case basis and shall be consistent with metering requirements required by the local connecting utility and adopted by the local regulatory jurisdiction. Net Energy Metering should be installed when a DER has the capability or potential to provide resources back into the Distribution System, however, the eligibility of a DER provider to receive net metering will be subject to the rules of the interconnecting utility.

A DER connected to the point of connection should be capable of providing monitoring connection status, real power output, reactive power output, and voltage either at the point of connection or aggregate connection, as required by the distribution utility. The monitoring equipment should be installed at time of interconnection. The distributor and the generator must mutually agree upon communication media options. The DER metering and monitoring communications will allow interoperability and the capability to provide system operators with situational awareness as deemed necessary by the interconnecting utility.  As more DER is employed and base load generation is replaced with DER grid-edge resources, it will be important to be able to monitor the availability and production of energy from these resources.

## Power Quality

The requirements for acceptable flicker levels shall be in accordance with the latest version of IEEE Std. 1453 Recommended Practice for the Analysis of Fluctuating Installations on Power Systems. Short and long-term perception of flicker shall be within the planning and compatibility levels delineated in this standard. Mitigation measures necessary to comply with these requirements shall at the DER owner’s expense.

## Power Factor

If the average power factor, as measured at the PCC, is less than 0.9 (leading or lagging), the method of power factor correction necessitated by the installation of the generator will be negotiated with the utility as a commercial item. If the average power factor of the generator is proven to be above the minimum of 0.9 (leading or lagging) by the customer and accepted by the utility, that power factor value shall be used for any further utility design calculations and requirements.

Induction power generators may be provided VAR capacity from the utility system at the DER owner’s expense. The installation of VAR correction equipment by the generator- owner on the DER owner’s side of the PCC must be reviewed and approved by the utility prior to installation.

## Islanding

Systems must be designed and operated so that islanding is not sustained on utility distribution circuits or on substation bus and transmission systems. The requirements listed in this document are designed and intended to prevent islanding and subject to be superseded by local requirements. Special protection schemes and system modifications may be necessary based on the capacity of the proposed system and the configuration and existing loading on the subject circuit.

The need for zero sequence voltage and direct transfer trip protection schemes will be evaluated based on minimum loads on the associated feeder and substation bus, including certain fault conditions resulting from system installation to protect for an islanded condition.

## Underfrequency Load Shedding Programs

Under frequency load shedding is implemented to restore power system frequency stability if system frequency drops below the operational set point during major disturbance such as a loss of generation or events in excess of design based contingencies.  The importance of an effective automatic UFLS program cannot be overemphasized.  UFLS is considered a “safety net” for the BES and a last resort of automatic control operations designed to stabilize BES islands of load and generation for a specific amount of imbalance, typically a 25% deficiency of generation.  UFLS is primarily armed on distribution feeders, where DER is increasingly being deployed.

NERC has a set of requirements in their PRC-006 standard and NPCC has more stringent requirements in NPCC’s Regional Standard, PRC-006-NPCC which outline expected performance.  Approved and effective versions of these standards may both be found on the NERC website.

An NPCC Load Modeling Working Group, SS-38, has studied the UFLS performance of the Region and determined that no change, at this time, is necessary in the UFLS program.  The SS-38 has also performed some sensitivity analysis and determined that increased levels of DER penetration in the short term will not result in any significant degradation in UFLS performance.

As DER penetrates in the longer term it may be necessary to adopt a more flexible approach to UFLS.  There are utilities that are reviewing the feasibility of “Adaptive UFLS” which uses real time monitoring of distribution feeder loads and their DER to determine how much additional load may need to be tripped when DER has increased output.  This increased automation is not necessary within NPCC at this time however our technical groups will continue to assess and affirm the NPCC UFLS program is effective in maintaining reliability.

## Effective Grounding for DER

With the onset of high DER such as photovoltaic (PV) penetration, utilities should consider interconnection of PV plants similarly to how they would interconnect synchronous generators. Conventional generators are considered to be voltage sources as they provide constant AC voltages controlled by excitation systems. In contrast, an inverter-based PV plant is modeled as a current source and the DER terminal voltage is dependent on the feeder to which it is connected.

Solidly grounding a transformer neutral for a DER eliminates a possible phase overvoltage stemming from a single-line-to-ground fault. A potential problem with the solid grounding in the distribution line is that large fault currents can flow through the transformer neutral, which can desensitize the overcurrent protection coordination. In order to mitigate this issue, impedance grounding can limit the fault current and potential equipment damage, while allowing overvoltage to some limited magnitude.  Some utilities protect their distribution from overvoltage by using overvoltage protection so Effective Grounding isn’t a concern.   Further investigation on the how specific installations are grounded is warranted and being pursued by the Interconnection Technical Working Group (ITWG) in New York.

## Energy Storage Systems for DER

Li-ion batteries have been and continue to be deployed in a wide range of energy-storage applications, ranging from energy-type batteries of a few kilowatt-hours in residential systems with rooftop photovoltaic arrays to multi-megawatt containerized batteries for the provision of grid ancillary services.  The Energy Storage Association (ESA) anticipates at least 35 GW of new energy storage in the United States by 2025 and that the amount of energy storage will double from 2018 levels during 2019.

The ESA in conjunction with over 25 vendors and utilities have formed a task force and made a commitment to optimize safety standards.  Care should be used in placement of batteries.  Suggested placements should avoid proximity to other facilities that may be critical the reliability of the BES.

# DER BES Recommendations

As DER continues to penetrate the NPCC Region we suggest the following initial activities:

Process and Risk Management Recommendations

- Continue with sensitivity analysis at the Transmission level for various levels of penetration of DER on distribution facilities to determine any adverse effects on UFLS performance.

- Pursue further opportunities to coordinate distribution and transmission reporting requirements for generating resources and promote NPCC Regional consistency where possible.

- Continue to review NPCC Area authorities having jurisdiction and utility interconnection requirements documents to identify dissimilarities which may negatively impact reliability.

- Identify opportunities to share information regarding problems and problem solving.

- Continue to solicit and address observable reliability issues of DER initiated BES impact through the use of NPCC’s DER Impact Reporting Forms and its associated process.

- Continue to discuss any changes required for System Restoration and Blackstart Plans, as a result of increased DER.

- Continue to follow ESA ESS safety issues and associated recommendations and share the results with NPCC stakeholders.

Planning Related Recommendations Due to Changing Resource Mix

- Obtain DER modeling and performance data to enable Operational Planning of the BES

- Clearly identify DER in the NPCC Region’s Area queues, where DER is being proposed for installation and the magnitudes relative to the existing resource base and load projections.

- Obtain modeling data to enable modelling of the BES for the purposes of Long-Term Resource Planning with DER

- Obtain modeling data to enable modelling of the BES for the purposes of Long-Term Transmission Planning

- Address masking of load by DER at the distribution level to ascertain its impact on the assumptions that underpin UFLS programs

Analytics and simulation recommendations to deal with increase system complexity

- Support interconnection wide inertia loss study efforts, to determine potential reliability impacts, as DER increasingly replaces conventional synchronous generation resources.

- Obtain modelling data to be able to predict and examine system behavior and assess the interactions between the new resources and the existing reliability preserving systems and programs. Examples include:

  - Under Frequency Load Shedding,

  - Under Voltage Load Shedding,

  - Frequency response sharing mechanisms (BAL standards).

  - Analysis of system protection systems (both T and D) so that the parameters to set protection systems and other control systems are known so as to permit the most reliability benefits to be garnered from the new resources.

# Appendix A NPCC DER Impact Reporting Form

Please Complete and email this form to;   npccstandard@npcc.org

Distributed Energy Resource (DER), BES Impact Reporting Form

| Name |  | Date |  |
| --- | --- | --- | --- |
| Email |  | Company |  |
| Impact on Bulk Electric System |  | Area (NY, NE, State or Province etc.) |  |

Equipment Impacted

| Equipment | Location (substation name, etc.) | Impact (Positive reliability impact? Negative reliability impact-Protection System failure, Misoperation, load affected or lost?, power quality issue?, etc) | Duration of Impact, (start and stop times, length of impact, ongoing? etc.) |
| --- | --- | --- | --- |

Description of Impact on BES- What Happened or was observed?

Please describe below the details of all the impacts of the DER as it pertains to this report, such as load loss, loss of life, equipment failure or potential reliability improvement. A sequence of events showing the impact is helpful. Attach supporting information to this form if necessary.

Root Cause or additional Analysis

Please describe below the details of any investigation your company may have already done to identify causes or contributing factors to the incident. This will help NPCC route the issue properly to address it.

NPCC Review of Issue and Recommendations (i.e. Refer to NERC, develop a Criteria, Guideline, Already Addressed or Identified, etc.)

NPCC Date of Resolution of Issue ______________

|  | # Appendix B, NPCC Areas- Comparisons Key Inverter based specification extracts |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | ISO-NE Inverter Requirements | NG ESB 756 B, C, D |  |  | NY SIR | IESO F2 Technical Requirements |  |  |  |
|  | Inverter Certification | yes | yes |  |  | yes | yes |  |  |  |
|  | Voltage and frequency trip settings for inverter based applications | yes | yes |  |  | yes | yes |  |  |  |
|  | Voltage Response | yes | yes |  |  | yes | yes |  |  |  |
|  | Frequency Response | yes |  |  |  | yes | yes |  |  |  |
|  | Abnormal performance capability (ride-through) requirements for inverter based applications | yes | yes |  |  |  |  |  |  |  |
|  | Other grid support utility interactive inverter functions statuses | yes |  |  |  |  |  |  |  |  |
|  | Minimum protection functions |  | yes |  |  | yes |  |  |  |  |
|  | Monitoring and Control |  | yes |  |  | yes | yes |  |  |  |
|  | Reconnection to the System |  | yes |  |  | yes |  |  |  |  |
|  | Distribution Protection Coordination |  | yes |  |  |  | yes |  |  |  |
|  | Inverter Certification |  | yes |  |  | yes |  |  |  |  |
|  | Power Quality |  |  |  |  | yes |  |  |  |  |

Reliable Operation is defined in 16 U.S. Code § 824o and means “operating the elements of the bulk-power system within equipment and electric system thermal, voltage, and stability limits so that instability, uncontrolled separation, or cascading failures of such system will not occur as a result of a sudden disturbance, including a cybersecurity incident, or unanticipated failure of system elements.”

See NERC Rule of Procedure #313 on page 15 of the NERC Rules of Procedure 3-9-2018.

The method of identifying critical facilities is currently embodied in the NPCC A-10 Classification of Bulk Power System Elements document, currently under review by the CP-11 Working Group with a due date of October 31, 2018.

The NPCC Bulk Power System is identified by a specific list of facilities in the NPCC region deemed critical by the NPCC A-10 classification process. This list is not determined based on the definition of the ERO Bulk Power System, which is defined in the US 2005 EPACT as:

‘‘(A) facilities and control systems necessary for operating an interconnected electric energy transmission network (or any portion thereof); and

‘‘(B) electric energy from generation facilities needed to maintain transmission system reliability.

The term does not include facilities used in the local distribution of electric energy.

There are other documents which supplement the Directories, for instance the NPCC Compliance Guidance Statements. These documents usually refer to NERC standards applicability and can be found here: NPCC CGS

NERC Rule of Procedure #313 (page 15) permits the following: “Regional Entities may develop Regional Criteria that are necessary to implement, to augment, or to comply with NERC Reliability Standards, but which are not Reliability Standards. Regional Criteria may also address issues not within the scope of Reliability Standards, such as resource adequacy. “

Reference NERC’s recent filing with FERC regarding Resilience for a more complete discussion of the relationship between resilience, the NERC standards and the NAICS Resilience Framework. FERC is expected to define resilience in the course of its current examination of electric system resilience concepts.

In the US, Presidential Policy Directive – 21 defines resilience as “The ability to prepare for and adapt to changing conditions and withstand and recover rapidly from disruptions. Resilience includes the ability to withstand and recover from deliberate attacks, accidents, or naturally occurring threats or incidents”.