## Slide 1: Testing and analysis of the dynamic and transient behavior of inverters used in solar residential project

## Slide 2: Test and analysis of the dynamic and transient behavior of inverters used in solar residential project
HQ TransÉnergie
Vincent Morissette, Julie Lacroix, Pierre-Luc Martel, Charles Desbiens, Jean-François Haché
IREQ
Dmitry Rimorov, Olivier Tremblay
Notes: Working group IREQ/TÉ
Some slide are from a presentation done at the IEEE general meeting last summer (D.Rimorov)

## Slide 3: Agenda
Introduction
Power-hardware-in-the-loop
Tested cases
Results
Conclusion
References

## Slide 4: Introduction
Increased penetration of solar residential photovoltaïc (PV) is a concern for transmission network planning.
We tested voltage and frequency ride-through.
Then, we did additional tests with Hypersim and power hardware in the loop. It allowed us to test: faults, dynamic and transient phenomena of different network events with a wide frequency range (up to 25kHz). We have performed in-depth analysis of ride-through performance.

## Slide 5: Power-hardware-in-the-loop tests (IREQ simulation laboratory)
PV emulator
Equipement under test
Differents real time network events with Hypersim simulator
Notes: Hypersim : Real-time digital simulator for electrical networks (software+hardware)
close loop test
PV emulator: Keysight (N8937APV) programmable CC source

## Slide 6: Devices under test
MPPT : Maximum power point tracking
Notes: Commercially available inverters

## Slide 7: Tests cases
Hypersim tests :
Dynamic under frequency
Dynamic over frequency
Low voltage ride through
Low voltage dynamic event
Rate of change of frequency
Sudden phase angle shift
Decrease the system strengh
Network faults in weak network condition and high penetration level
Frequency response
Notes: A quick list of different test performed

## Slide 8: Voltage and frequency ride-through

## Slide 9
Inverter | under-frequency
A | trips after 1.3 sec. at 59.27Hz
B | trips after 1,43sec. at 59,2Hz
C | stays connected
D (without MPPT) | trips after 1,42sec. at 59,2Hz

## Slide 10
Inverter | Overfrequency
A | trips after 1.04 sec. at 60,5Hz
B | trips after 1.18sec. at 60,58Hz
C | trips after 1.07sec. at 60,53Hz
D (without MPPT) | trips after 1,15sec. at 60,57Hz
Notes: HQ do generation rejection at à 60.9, 61.1 et 61.3 Hz.
We hope new technologies inverters will have a better immunity to overfrequency. If not, stability system can be affect by the too fast disconnection.

## Slide 11
Inverter | LVRT
A | trips instantaneously
B | trips after 0,02sec.
C | trips after 0,12sec.
D (without MPPT) | trips after 0,14sec.
Notes: 2 inverters trip in less than 6 cycles.
2 inverters trip in less than 9 cycles.

## Slide 12
Inverter | Dynamic LVRT
A | trips after 0,14s. reconnects after 4,2sec.
B | stays connected
C | stays connected
D (without MPPT) | stays connected

## Slide 13: Rate of change of frequency
Case | Inverter ( generated power in % ) | Rate of change of frequency ( Hz / sec. ) | Time before inverter blocking ( seconds ) | Network frequency at blocking ( Hz )
1 | 100 | +1 | 0.58 | 60.58
2 | 100 | +2 | 0.36 | 60.72
3 | 100 | +4 | 0.25 | 61
4 | 100 | +8 | 0.18 | 61.44
5 | 100 | -1 | 0.8 | 59.2
6 | 100 | -2 | 0.47 | 59.06
7 | 100 | -4 | 0.29 | 58.84
8 | 100 | -8 | 0.2 | 58.4
… | … | … | … | …
17 | 30 | +1 | 0.6 | 60.6
18 | … | … | … | …
The rate of change of frequency affects the delay before the inverter blocking
or the total operating time of the frequency protection.
Notes: Even with a fixe definite time delay for frequency protection (ex: 61.7Hz, time delay 0.3sec.) -> the time to measure the frequency need few cycles and the rate of change affect the measure, then the operating time detection.

## Slide 14: Sudden voltage phase angle shift (15o, 30o and 45o)
1 inverter block for a phase shift of 30o in 9msec.
2 inverters block for a phase shift of 45o in respectively 148msec. and 28 msec.
1 inverter did not block at 15, 30 and 45o
Notes: Phase shift represent line switching events
Some inverters have a better immunity
Some inverters trip faster than protection (too fast).
Tested with a strong network

## Slide 15: Weak source

## Slide 16: Increase network source impedance
until inverter trip or until a connexion incapacity
Previous source impedance value = weak network condition
Notes: Increase source impedance (=Decrease system strengh)
We increase the source impedance until we observe the inverter trip after a fault or a connexion incapacity. We did that for the 4 inverters. Then, we decrease the source impedance to the previous value to obtain no disconnexion (steady state condition).

## Slide 17
Inverter connect to a weak source (steady state)
Notes: Weak source in steady state
The good performance of the inverter without MPPT suggest that the MPPT tracking can play a role in those distrotions.

## Slide 18
Maximum power point tracking (MPPT)
Nonlinear characteristic of the PV panel (V-I curve)
The results suggest that the PV dynamic is influenced by the MPPT
Notes: Non linear P-V curve
The MPPT control the DC output of the PV pannel to obtain the maximum power from the PV panel in function of the irradiance of the sun.

## Slide 19: Linear analysis
Notes: Open and close loop linear analysis is measuring how stable is a system.

## Slide 20: Linear analysis
PV inverter (DUT) is a “black box”
  Analytical (linearized) model not available
Frequency response was measured by the direct method
  Superimpose low level voltage modulation with frequency on a fundamental
  Measure component of DUT current
  Calculate impedance at
  Vary

## Slide 21
Linear analysis
Closed-loop stability analysis in frequency domain
Gain and phase margins, oscillation frequency are determined via Bode plots

## Slide 22
Linear analysis
ID |  |  |  | 5 | 
 |  | Phase margin, deg | , Hz | Phase margin, deg | , Hz
A | 28 | 14 | 546 | 29 | 321
B | 27 | 21 | 322 | 10 | 127
C | 23 | 46 | 502 | 25 | 216
D | 6 | 29 | 301 | 27 | 301
ID |  |  |  |  | 
 |  | Phase margin, deg |  | Phase margin, deg | 
A | 28 | 14 | 546 | 29 | 321
B | 27 | 21 | 322 | 10 | 127
C | 23 | 46 | 502 | 25 | 216
D | 6 | 29 | 301 | 27 | 301
Gain margins were not determined (limited frequency range)
Stability margins decrease as SCL decreases
Frequency of resonance decreases as SCL decreases
: Short-circuit ratio between the point of connexion and the power produced by the inverter.
SCL: Short-circuit level
Notes: The phase margin is an indicator of the stability of a system

## Slide 23
Experimental results, simple network
ID |  | Observed behavior
A | 28 | DUT voltage distortion problems staying connected and frequent trips
B | 27 | Sustained undamped DUT current oscillations at low frequency (below 60Hz)
C | 23 | Sustained undamped DUT voltage and current oscillations, frequency of 500Hz
D | 6 | DUT voltage waveform distortion
ID |  | Observed behavior
A | 28 | DUT voltage distortion problems staying connected and frequent trips
B | 27 | Sustained undamped DUT current oscillations at low frequency (below 60Hz)
C | 23 | Sustained undamped DUT voltage and current oscillations, frequency of 500Hz
D | 6 | DUT voltage waveform distortion
  Inverter A : Voltage distortion is observed
  Any small disturbance in the grid causes the inverter to trip

## Slide 24: Model based on existing distribution feeder in rural Quebec Low short circuit level + high PV penetration level

## Slide 25: Test results: distribution feeder model
Model based on existing distribution feeder in rural Quebec
  Includes nonlinear house load
  Variable number of houses (current multiplier)
  Low load, high PV production conditions with overall active power supplied to the grid

## Slide 26
Test results: distribution feeder model
ID | Number of houses |  | Observed behavior
A | 10 | 140 | DUT voltage distortion, reconnection problems
B | 41 | 34 | DUT voltage distortion, undamped DUT current oscillations at low frequency
C | 4 | 250 | Sustained undamped DUT voltage and current oscillations
D | 150 | 9 | DUT voltage waveform distortion
ID | Number of houses |  | Observed behavior
A | 10 | 140 | DUT voltage distortion, reconnection problems
B | 41 | 34 | DUT voltage distortion, undamped DUT current oscillations at low frequency
C | 4 | 250 | Sustained undamped DUT voltage and current oscillations
D | 150 | 9 | DUT voltage waveform distortion
: Short-circuit ratio between the point of connexion and the power produced by the inverter.

## Slide 27
Source impedance or penetration level = Resonant frequency
Adverse effects of resonnance conditions :
DUT voltage and current distortion, oscillation, reconnection problems, disconnection after a disturbance in the grid

## Slide 28
EMT generic model
All inverters have filter to reduce switching harmonics.
Some inverter have also an active filtering control strategy that can reduce low harmonics.
That reactive component plays a role in resonances observed in our tests.
Notes: Filter impedance is changing with the frequency.

## Slide 29: Conclusions
Some commercially available residential PV inverters are better than others to meet voltage and frequency ride-through requirements. Overfrequency ride-through is challenging and the the rate of change have to be consider.
The nonlinear characteristics of the PV panel must be taken into account in models and simulations.
Increasing the PV penetration level or decreasing the source strength can cause instability (resonances).
* need to study summer network with high penetration level of PV and light load
* a high penetration scenario can be specific to certain areas: a local network, a substation, a distribution line
The MPPT and the filters are two important components to represent in the PV EMT (Electromagnetic transients) models to study resonances and instability observed.
The residential load, mainly resistive, is moving to be more reactive. It has a destabilising effect.

## Slide 30: References
[1] D. Rimorov, O. Tremblay, J-F Haché, V. Morissette, C. Desbiens, J. Lacroix, P-L Martel, « Power Hardware-in-the-loop testing of residential PV inverters in the conditions of weak network », IEEE PESGM, 2020.
[2] O. Tremblay, H. Fortin-Blanchette, R. Gagnon, and Y. Brissette, “Contribution to stability analysis of power hardware-in-the-loop simulators,” IET Generation, Transmission & Distribution, vol. 11, no. 12, pp. 3073–3079, 2017.
[3] O. Tremblay, D. Rimorov, R. Gagnon, and H. Fortin-Blanchette, “A multi-time-step transmission line interface for power hardware-in-theloop simulators,” IEEE Transactions on Energy Conversion, pp. 1–1, 2019.