## Slide 1
October 15, 2020 Holyoke, Massachusetts
Senior Engineer
NPCC DER Forum
ISO-NE Distribution-Connected Generation Interconnection, Modeling, & Study Procedures
Brad Marszalkowski

## Slide 2: Purpose of the Presentation
Provide guidance regarding the procedural and technical requirements for new Distribution-Connected Generation
Discuss stakeholder coordination and Affected System Operator (ASO) Studies

## Slide 3: Background

## Slide 4: ISO New England Control Area
(1986/1990)
DC
AC
AC
AC
350 dispatchable generators in the region
31,200 MW of generating capacity
9,000 miles of high-voltage transmission lines (115 kV and above)
13 transmission interconnections to neighboring power systems in New York and Eastern Canada:
  New York (8 AC ties, 1 DC tie)
  Hydro Québec (2 DC ties)
  New Brunswick (2 AC ties)
Region’s all-time summer peak demand set on August 2, 2006 at 28,130 MW
Region’s all-time winter peak demand set on January 15, 2004 at 22,818 MW
New Brunswick
Hydro Québec
New
York
(1985)
DC
AC (1970s)
AC (2007)
AC
AC
AC
AC
AC
DC
Note: AC stands for Alternating Current and DC stands for Direct Current

## Slide 5: TARIFF REQUIREMENTS
ISO-NE PUBLIC
4

## Slide 6: What are FERC Jurisdictional Distribution Facilities? What are State Jurisdictional Distribution Facilities?
A Distribution-Connected Generator developer should contact the ISO or the owner of the Distribution Facilities to determine whether the facilities are state or FERC jurisdictional. The Distribution Company and the ISO will coordinate the identification of Jurisdiction – as necessary.
FERC Jurisdictional Facilities
FERC jurisdictional Distribution Facilities are Distribution Facilities that are being used for FERC jurisdictional purposes (i.e., to facilitate sales of electricity at wholesale) and are subject to the ISO Tariff.
State Jurisdictional Facilities
State jurisdictional Distribution Facilities are Distribution Facilities that are not being used for FERC jurisdictional purposes (i.e., to facilitate sales of electricity at wholesale).

## Slide 7: What interconnection process does a new Distribution-Connected Generator follow?
The status of the distribution facility at the time of the interconnection request is a factor in determining which interconnection process applies
A developer proposing to interconnect a Distribution- Connected Generator to a:
  State jurisdictional Distribution Facility needs to follow the associated state interconnection process
  FERC jurisdictional Distribution Facility needs to follow the ISO interconnection process under Schedule 22 or 23 of the OATT, as applicable
The state interconnection process will apply if a Distributed-Connected Generator is
interconnecting to a FERC jurisdictional facility and the project will:
Produce energy to be consumed only on the retail customer’s site,
Not sell its energy into the ISO markets, or
Sell 100% of its output as a Qualifying Facility to the interconnecting utility

## Slide 8: What interconnection process applies to a generator that is being modified?
A Distribution-Connected Generator that was interconnected under the state interconnections process and is now being modified needs to follow the state interconnection process if the Distribution Facility to which it is connected is still state jurisdictional
  Otherwise, they would need to follow the ISO interconnection process
under Schedule 22 or 23 of the OATT
A Distribution-Connected Generator that was interconnected under the FERC interconnection process and is now being modified needs to follow the ISO interconnection process under Schedule 22 or 23 of the OATT
  A request to participate in the ISO markets for an existing behind-the- meter generator may trigger the ISO interconnection process

## Slide 9: To Whom does a new Distribution-Connected Generator apply?
If subject to the ISO interconnection process
Interconnections that are subject to the ISO’s interconnection process are administered in accordance with Schedules 22 and 23 of the OATT Interconnection request forms are available electronically in the Interconnection Request Tracking Tool (IRTT), which is located on the ISO Website A requestor must create an account in IRTT in order to gain access Interconnection requests are completed within and submitted to the ISO using the IRTT
If subject to the state interconnection process
State jurisdictional interconnection applications are available from the Distribution Company/owner of the state jurisdictional Distribution Facility Completed applications are to be submitted to the Distribution Company/owner of the state jurisdictional Distribution Facilities

## Slide 10: What type of Interconnection Service may be requested under Schedules 22 and 23?
There are two levels of Interconnection Service available under
Schedules 22 and 23:
  Network Resource Interconnection Service (energy); and
  Capacity Network Resource Interconnection Service (energy and capacity)
All Distribution-Connected Generators that interconnect under Schedules 22 and 23 are eligible to participate in the ISO markets
Depending on the purpose of the interconnection, a Distribution- Connected Generator that interconnected under state interconnection procedures may be eligible to participate in the ISO markets
  E.g., a generator interconnected behind the meter or for retail consumption does not have the interconnection rights to put power onto the grid

## Slide 11: Proposed Plan Approval (I.3.9)
In addition to an interconnection request submittal, a new Distribution-Connected Generator or a modification to an existing Distribution-Connected Generator resulting in an increase or a change in its operating characteristics may need to submit a Proposed Plan Application pursuant to Section I.3.9 of the Tariff
  This is true regardless of the jurisdiction of the interconnection process
  If the Generator Owner is not a Market Participant, the interconnecting Transmission Owner will submit on the generator’s behalf
Distribution-Connected Generators that are 5 MW require a proposed plans application
Distribution-Connected Generators that are 1 MW to less than 5 MW may only require a less than 5 MW Notification Form
Distribution-Connected Generators that are less than 1 MW do not
have an I.3.9 requirement

## Slide 12: Stakeholder coordination & Data collection

## Slide 13: Coordination Practices
Stakeholder Review & Information Exchange
  New interconnections (>1MW) must submit either a Small Generator Notification or Proposed Plan Application regardless of POI
  Interconnections are channeled through the Reliability Committee which allows affected parties to have a chance to voice concerns (I.3.9 process)
  Transmission System Impact Studies (SIS) sometimes needed based on size or location of interconnection
What we do with the information
  Tracking DER interconnections
  Determination of study requirements
  Data from forms and SIS used in steady state and dynamics modeling

## Slide 16: Iso-ne der model development

## Slide 17: Study Conditions/Assumptions Modeling assumptions within dynamics cases
DER in NE primarily solar
  Normalized PV profiles used
  Fractional value multiplied by nameplate of PV installation for total output
Battery Energy Storage
  Operational Characteristics such as charging and discharging
  State of Charge (SOC) can also be important
Time of year
  PV outputs differ based on available irradiance which differs based on time of year
  Gross loads and DER penetration levels

## Slide 18: Study Conditions/Assumptions Modeling assumptions within dynamics cases (cont.)
Year of Study
  DER penetration increasing as states continue to solar incentives
  Utilization of synchronous units decreasing, and retirements more likely, as load is reduced
  DER mix will change based on study year
  DER interconnection requirements are dependent on year project applied (IEEE 1547-2003, IEEE 1547-2018, ISO-SRD, etc)

## Slide 19: DER Modeling Practices U-DER & R-DER Modeling assumptions
DER (MW ≥ 5)
  Referred to as U-DER
  Explicitly tracked & modeled as generators in cases
  Use NERC & WECC modeling guidelines and equivalencies
  Specific dynamic models to be provided by developer (2nd gen renewable energy models)
DER (1 < MW < 5)
  Generally referred to as R-DER
  Locational data is tracked (both address and electrical interconnection)
  Modeled at low side of distribution bus
  DER_A model is used and parametrized based on requirements coincident with application approval date
DER (MW ≤ 1)
  Referred to as R-DER with unknown location
  Output values come from PV forecast
  Currently modeled as negative loads distributed across dispatch zones and normalized according to load at each bus
  No dynamic models are added
*Reference https://www.nerc.com/comm/PC_Reliability_Guidelines_DL/Reliability_Guideline_DER_A_Parameterization.pdf

## Slide 20: DER Modeling Practices U-DER & R-DER Modeling assumptions (cont.)
Voltage/Frequency control modes
  Most DER’s installed without reactive power output, or at fixed PF as voltage/frequency control is often not allowed on feeders
  Both 2nd generation WECC models and DER_A model support voltage and frequency control setups for the few that do
Constant power factor mode
  Power factor equal to 1 in most cases
    Modeling of R-DER in loadflow requires adjustment of DER (P & Q) to account for avoided distribution losses and maintain planned power factors of TOs/DOs at distribution transformers
Distribution Loss Assumption
  Current assumption of transmission and distribution losses is 8%
    Transmission – 2.5% (calculated by PSSE)
    Distribution – 5.5% (included in calculation of loads)
  Increased penetration of DER on distribution feeders can change distribution losses

## Slide 21: Affected System Operator studies

## Slide 22: Why is it important to study Distribution-Connected Generation?
Overall bulk system ride-through performance
  No individual project of 5 MW or greater, nor more than 20 MW of dispersed energy resources can trip offline for a design contingency per ISO-NE Planning Procedure 3
(Possible) Provision of bulk system Essential Reliability Services such as voltage and frequency response
  Projects 1 MW and greater registering in the markets may need to provide voltage control per ISO Operating Procedure 14 (OP-14)
  Projects 10 MW and greater registering in the markets must provide frequency control per ISO Operating Procedure 14 (OP-14)
  TO may have their own requirements for units that are not registered in the markets
Impacts on transmission connected generators
  Reduced system strength due to fewer online synchronous resources
Impacts on specific transmission equipment or system performance caused by large accumulations of distribution-connected generators at specific substations

## Slide 23: Overall Bulk System Ride-Through Performance Addressed through interim IEEE 1547 Implementation
ISO New England plans and operates the transmission system to ensure that the loss of a large source of supply (source loss) does not adversely impact the reliability of the Eastern Interconnection
Historically, the concern has been source loss due to large generators being disconnected or going unstable and tripping
Tripping of large quantities of distributed energy resources (DER) for a transmission fault would add to source loss
If total source loss exceeds the amount allowed by the planning criteria, a system upgrade would be required, and this could negatively impact the benefits of state policies to encourage renewable energy
The acceptable maximum source loss is limited by New England’s interconnections to other regions to approximately 1,200 MW for normal design contingencies

## Slide 24: Bulk System Essential Reliability Services To be addressed through the full implementation of IEEE 1547
Future system operation conditions may include scenarios where the majority of on-line generation will be distribution-connected
The bulk system must still exhibit stable voltage and frequency responses to system events
Essential reliability services such as voltage and frequency response may be provided by distributed generation – OR – additional upgrades may be required on the transmission system
Transmission
System
Events on the
Transmission System
Distribution System with significant accumulation of distribution-connected generators

## Slide 25: Study Requirements Per ISO-NE Planning Procedures 3, 5-1, 5-3, & 5-6
Affected system operator studies are required by the planning procedures
All individual non-FERC jurisdictional projects 5MW or greater require full level III analysis (Steady State, Short Circuit, Stability, possibly EMT)
Groups of projects individually less than 5MW’s that are electrically close and aggregate to 20MW or more require full level III analysis
Non-FERC jurisdictional studies are completed by the interconnecting TO and reviewed by the ISO.

## Slide 26
Other Coordination
ISO-NE PUBLIC
13
A review of the successful outcome achieved as a result of the work with the Massachusetts Technical Standards Review Group

## Slide 27: Interim Solution
Due to the rapid growth of solar PV in New England and because the timeline for full implementation of the revision to IEEE 1547 is 2020 or later, ISO New England pursued an interim solution for obtaining ride-through for voltage and frequency variations*
Inverters meeting the requirements of UL 1741 SA have the capabilities required by ISO New England in the interim
Choosing performance requirements for these inverters required input from distribution engineers, solar PV developers, and inverter manufacturers
The ISO worked with the Massachusetts Technical Standards Review Group (TSRG) to get input from these entities
* Technical details are provided in the Appendix

## Slide 28: Interim Solution
Development of inverter performance requirements and an implementation plan required addressing multiple issues
  Transmission reliability
  Distribution protection
  Retaining maximum trip time
  Anti-islanding protection
  Conformance with the revised IEEE 1547
  Allowing time for manufacturers to develop
software to implement ISO New England settings
Balancing these and other issues, ISO New England and the Massachusetts TSRG developed a Preferred Utility-Required Profile and an implementation plan

## Slide 29: Interim Solution – Timeline for Massachusetts
The ISO’s interim solution was adopted in 2018 across multiple utility systems
The following schedule was implemented in Massachusetts
  All inverter-based solar PV projects ≤ 100kW with applications submitted on or after June 1, 2018 are subject to the ISO New England Source Requirement Document
  All inverter-based solar PV projects > 100 kW with applications submitted on or after March 1, 2018 are subject to the ISO New England Source Requirement Document
  Inverter-based solar PV projects with applications submitted prior to the above dates were encouraged to comply with the ISO New England Source Requirement Document with the approval of the interconnecting utility

## Slide 30: Interim Solution – Timeline for Rest of New England
National Grid implemented the same requirements in Massachusetts and Rhode Island
Eversource and United Illuminating required that all Connecticut inverter-based solar PV project applications submitted on or after June 1, 2018 be subject to the ISO New England Source Requirement Document
Eversource and Unitil required that all New Hampshire inverter-based solar PV project applications submitted on or after June 1, 2018 be subject to the ISO New England Source Requirement Document
Maine and Vermont utilities implemented the interim solution as of September 1, 2018 and November 2, 2018, respectively

## Slide 31: NEXT STEPS AND ADDITIONAL CONSIDERATIONS
ISO-NE PUBLIC
18
Full Implementation of IEEE 1547-2018

## Slide 32: Potential Benefits of Full Implementation
IEEE 1547-2018 defines the requirements to support the provision of Essential Reliability Services by distribution- connected resources, including:
  Voltage response
  Frequency response
Utilizing the response capabilities of today’s inverters could:
  Reduce the transmission and distribution upgrades needed to ensure the reliable addition of distribution-connected resources
  Enable the continued addition of further distribution-connected resources in a reliable manner

## Slide 33: Next Steps
The ISO is working with Municipal Utilities and Co-ops to implement the ISO New England Source Requirement Document on their systems
The ISO is working with the Massachusetts TSRG on the full implementation of IEEE 1547-2018
  More than 50 responsibilities have been identified in IEEE 1547-2018
  Area Electric Power System (EPS) Operators have a role in more than 40 of these responsibilities, some of which require input from the Regional Reliability Coordinator and the Responsible Transmission Planners
  A subcommittee of the Massachusetts TSRG has plans to meet at least monthly to make the decisions required for the full implementation of IEEE 1547-2018

## Slide 34: Additional Considerations
After several TSRG meetings on the implementation of 1547-2018, a few additional issues have surfaced
  Utilities expressed the need for early identification of required updates to state regulations to allow time for those regulations to be revised
  Utilities expressed concerns about the interaction between frequency regulation (frequency droop) and anti-islanding protection for existing and new DERs
  Transmission Operators expressed the need for considering 1547-2018 “enter service” settings in black start studies
  Transmission planners expressed the need to track the location of the various additions of DERs (1547-2003, ISO-NE SRD and 1547-2018)
  Developers expressed the need to choose communication protocols to allow lead time for the manufacturers

## Slide 36: Appendix A
Interim implementation – technical details

## Slide 37: Interim Solution Voltage Trip Settings
Shall Trip – IEEE Std 1547-2018 (2nd ed.) Category II |  |  |  |  | 
Shall Trip Function | Required Settings |  | Comparison to IEEE Std 1547-2018 (2nd ed.) default settings and ranges of allowable settings for Category II |  | 
 | Voltage (p.u. of nominal voltage) | Clearing Time(s) | Voltage | Clearing Time(s) | Within ranges of allowable settings?
OV2 | 1.20 | 0.16 | Identical | Identical | Yes
OV1 | 1.10 | 2.0 | Identical | Identical | Yes
UV1 | 0.88 | 2.0 | Higher (default is 0.70 p.u.) | Much shorter (default is 10 s) | Yes
UV2 | 0.50 | 1.1 | Slightly higher (default is 0.45 p.u.) | Much longer (default is 0.16 s) | Yes

## Slide 38: Interim Solution Voltage Ride-Through Capability and Additional Operational Requirements
Voltage Range (p.u.) | Operating Mode/ Response | Minimum Ride-Through Time(s) (design criteria) | Maximum Response Time(s) (design criteria) | Comparison to IEEE Std 1547-2018 (2nd ed.) for Category II
V > 1.20 | Cease to Energize | N/A | 0.16 | Identical
1.175 < V ≤ 1.20 | Permissive Operation | 0.2 | N/A | Identical
1.15 < V ≤ 1.175 | Permissive Operation | 0.5 | N/A | Identical
1.10 < V ≤ 1.15 | Permissive Operation | 1 | N/A | Identical
0.88 ≤ V ≤ 1.10 | Continuous Operation | infinite | N/A | Identical
0.65 ≤ V < 0.88 | Mandatory Operation | Linear slope of 8.7 s/1 p.u. voltage starting at 3 s @ 0.65 p.u.: | N/A | Identical
0.45 ≤ V < 0.65 | Permissive Operation a,b | 0.32 | N/A | See footnotes a & b
0.30 ≤ V < 0.45 | Permissive Operation b | 0.16 | N/A | See footnote b
V < 0.30 | Cease to Energize | N/A | 0.16 | Identical
The following additional operational requirements shall apply for all inverters: In the Permissive Operation region above 0.5 p.u., inverters shall ride-through in Mandatory Operation mode, and In the Permissive Operation region below 0.5 p.u., inverters shall ride-through in Momentary Cessation mode with a maximum response time of 0.083 seconds. |  |  |  | 
Voltage Range (p.u.) | Operating Mode/ Response | Minimum Ride-Through Time(s) (design criteria) | Maximum Response Time(s) (design criteria) | Comparison to IEEE Std 1547-2018 (2nd ed.) for Category II
V > 1.20 | Cease to Energize | N/A | 0.16 | Identical
1.175 < V ≤ 1.20 | Permissive Operation | 0.2 | N/A | Identical
1.15 < V ≤ 1.175 | Permissive Operation | 0.5 | N/A | Identical
1.10 < V ≤ 1.15 | Permissive Operation | 1 | N/A | Identical
0.88 ≤ V ≤ 1.10 | Continuous Operation | infinite | N/A | Identical
0.65 ≤ V < 0.88 | Mandatory Operation |  | N/A | Identical
0.45 ≤ V < 0.65 | Permissive Operation a,b | 0.32 | N/A | See footnotes a & b
0.30 ≤ V < 0.45 | Permissive Operation b | 0.16 | N/A | See footnote b
V < 0.30 | Cease to Energize | N/A | 0.16 | Identical
The following additional operational requirements shall apply for all inverters: In the Permissive Operation region above 0.5 p.u., inverters shall ride-through in Mandatory Operation mode, and In the Permissive Operation region below 0.5 p.u., inverters shall ride-through in Momentary Cessation mode with a maximum response time of 0.083 seconds. |  |  |  | 

## Slide 39: Interim Solution Frequency Trip Settings
Shall Trip Function | Required Settings |  | Comparison to IEEE Std 1547-2018 (2nd ed.) default settings and ranges of allowable settings for Category I, Category II, and Category III |  | 
 | Frequency (Hz) | Clearing Time(s) | Frequency | Clearing Time(s) | Within ranges of allowable settings?
OF2 | 62.0 | 0.16 | Identical | Identical | Yes
OF1 | 61.2 | 300.0 | Identical | Identical | Yes
UF1 | 58.5 | 300.0 | Identical | Identical | Yes
UF2 | 56.5 | 0.16 | Identical | Identical | Yes

## Slide 40: Interim Solution Frequency Ride-Through Capability
Frequency Range (Hz) | Operating Mode | Minimum Time(s) (design criteria) | Comparison to IEEE Std 1547-2018 (2nd ed.) for Category II
f > 62.0 | No ride-through requirements apply to this range |  | Identical
61.2 < f ≤ 61.8 | Mandatory Operation | 299 | Identical
58.8 ≤ f ≤ 61.2 | Continuous Operation | Infinite | Identical
57.0 ≤ f < 58.8 | Mandatory Operation | 299 | Identical
f < 57.0 | No ride-through requirements apply to this range |  | Identical

## Slide 41: Interim Solution Grid Support Utility Interactive Inverter Functions Status
Function | Default Activation State
SPF, Specified Power Factor | OFF
Q(V), Volt-Var Function with Watt or Var Priority | OFF
SS, Soft-Start Ramp Rate | ON Default value: 2% of maximum current output per second
FW, Freq-Watt Function | OFF