# Please Complete and email this form to;   npccstandard@npcc.org

# Distributed Energy Resource (DER), BES IMpact Reporting Form

| # Name | Herb Schrayshuen | # Date | 8/12/2021 |
| --- | --- | --- | --- |
| # Email | herb@poweradvisorsllc.com | # Company | Power Advisors, LLC |
| # Impact on Bulk Electric System | High penetration of DER on distribution feeders, weakening the effectiveness of load shed levels assumed UFLS processes | # Area (NY, NE, State or Province etc.) | All “Areas” where DER penetration results in masking of load which is planned to be shed if UFLS frequency trigger limits are reached |

### Equipment Impacted

| # Equipment | # Location (substation name, etc.) | # Impact (Positive reliability impact? Negative reliability impact-Protection System failure, Misoperation, load affected or lost? power quality issue? etc.) | # Duration of Impact, (start and stop times, length of impact, ongoing? etc.) |
| --- | --- | --- | --- |
| Distribution feeders with penetration of DER at levels where the feeder is at times a net resource | Any | If a distribution feeder, which is included in a UFLS program and relied on for BPS UFLS functionality, has an impactful penetration of DER (possibly even appearing as a net resource, rather than load at the time of the UFLS triggering frequency event), shedding that feeder is not necessarily desirable or effective in arresting frequency decline. | Any time UFLS program effectiveness ( the last line of defense of the BPS/BES), is weakened where DER penetration is not taken into account in UFLS programs feeder selection. |

### Description of IMpact on BES- What Happened or was observed?

# Please describe below the details of all the impacts of the DER as it pertains to this report, such as load loss, loss of life, equipment failure or potential reliability improvement. A sequence of events showing the impact is helpful. Attach supporting information to this form if necessary.

Not observed yet. the prospective concern is that NPCC should, in the interest of resilience (and reliability) be proactive with repect to this concnern. In some areas of north America it is becoming difficult to find feeders for inclusion in UFLS programs which do not have DER on them. to date, the solution is to omit feeders with high DER pentration from UFLS programs. That approach is not likely to be viable in the long term. Other UFLS approaches (perhaps dynamic UFLS based on time of day or loading / flow direction) need to be developed and considered. IEEE standards related to interconnection of DER resources do not fully take this bps/bes level program concern into account. The effectiveness of UFLS programs to arrest frequency decline, as the resilience supporting last line of defense of the BPS/BES, is at its core a resource adequacy issue. frequency will continue to decline if resources and loads are not balanced immediately following a system distrubance.

### Root Cause or additional Analysis

# Please describe below the details of any investigation your company may have already done to identify causes or contributing factors to the incident. This will help NPCC route the issue properly to address it.

Root cause of reliability risk – feeders inlcuded in ufls programs where high penetration of der occurs may not yield the desired load reductions neccesary to arrest frequency decline. in the long term the inability of UFLS program managers to find enough feeders without der to include in ufls programs. Analysis - The NPCC review of “Area” UFLS pRograms should at a minimum ask the npcc “area” submitters of UFLS data into the NPCC UFLS review certain questions about DER pentration on Feeders selected for inlcusion in UFLS programs. Since Directory 12 is being retired, this issue needs to be considered elsewhere in NPCC Criteria or Guidance. Perhaps in D1 under resource adequacy, or in another NPCC document. Active engagement by NPCC staff or NPCC member representatives with NERC activities in this area is recommended.

### NPCC Review of Issue and RecoMmendations (i.e. Refer to NERC, develop a Criteria Guideline, Already ADDRESSED, or IdentifieD, etc.)

NPCC Date of Resolution of Issue ______________