## Readme
ABOUT THE INFORMATION IN THIS EXCEL TEMPLATE | COST-BENEFIT ANALYSIS RESULTS
Information presented in this excel file has been downloaded from ENTSO-E's TYNDP 2024 projects platform, accessible to project promoters at https://tyndp2024.entsoe.eu/projects-map/transmission/ and https://tyndp2024.entsoe.eu/projects-map/storage/. This excel files contains, for all or part of the projects depending on the filters applied before downloading: - TYNDP 2024 transmission projects data, at project level and at investment level - TYNDP 2024 storage projects data - Results of the cost-benefit analysis performed by ENTSO-E About the data Information presented in the tabs Trans.Projects, Trans.Investments and Stor.Projects was submitted by project promoters. CBA results presented in tabs 2030NT, 2040NT and 2040DE are the outcome of the assessment performed by ENTSO-E. Information presented in the tabs Trans.ProjectLevelBenefits and Stor.ProjectLevelBenefits was provided by project promoters. | Tabs 2030NT, 2040NT and 2040DE present the results of the cost-benefit analysis performed by ENTSO-E, for each scenario studied in the TYNDP 2024. Refer to the following table for information on each indicator. Results in the tabs 2030NT, etc are for the full area covered by the study (see TYNDP 2024 CBA Implementation Guidelines).
Indicators
| Shortcut | Full name | Indicator | Unit
| ΔSEW | Annual Socio-Economic Welfare (SEW) increase (excluding Energy Not Served cost) | B1 | M€ / year
| ΔSEW_CO2 | Annual Socio-Economic Welfare variation resulting from CO2 emmisions | B1_CO2 | M€ / year
| ΔSEW_RES | Annual Socio-Economic Welfare increase resulting from RES integration | B1_RES | M€ / year
| ΔCO2_market | Annual CO2 varation from market simulation | B2a | ktonnes / year
| ΔCO2_network | Annual CO2 varation due to network losses | B2b | ktonnes / year
| ΔCO2_market_monetised | Annual Societal cost variation resulting from CO2 variation from market simulation | B2a_€ | M€ / year
| ΔCO2_network_monetised | Annual Societal cost variation resulting from CO2 variation from network simulation | B2b_€ | M€ / year
| ΔRES | Annual avoided curtailment (RES integration) | B3 | GWh / year
| ΔRES_MW | Connected RES | B3a | MW
| ΔNOx | Nitrogen oxides | B4a | kg / year
| ΔNH3 | Ammonia | B4b | kg / year
| ΔSO2 | Sulphur dioxide | B4c | kg / year
| ΔPM5 | Particulate matter 5 | B4d | kg / year
For questions on TYNDP 2024 data, contact tyndp@entsoe.eu | ΔPM10 | Particulate matter 10 | B4e | kg / year
| ΔNMVOC | Non-methane volatile organic compounds | B4f | kg / year
| Δlosses | Variation of network losses | B5 | GWh / year
| Δlosses_monetised | Variation of network losses monetised | B5_€ | M€ / year
| ΔSoS | Annual reduction in Energy Not Served | B6 | MWh / year
| ΔSoS_monetised | Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served | B6_€ | M€ / year

## Trans.Projects
TYNDP 2024 - General information on transmission projects | [17 empty] | Needs addressed by the project |  |  |  | Expected transfer capacity increase |  |  | CBA
Project ID | Project Name | Description of the project | Promoters | Country | National development plan(s) | Commissioning Year estimated by the promoter | Status ID 1 : Under Consideration, 2 : In Planning but not permitting, 3 : In permitting, 4 : Under Construction | Is the project cross-border? | Is the project internal? | Type of project - Is it an upgrade of existing infrastructure? | Is the project on the 5th PCI list? | PCI number | Reason for investment clustering | Inclusion in previous TYNDPs | Is the project in the 2030 reference grid? | Is the project in the 2035 reference grid? | Where can one find more information on the project? (ex: project website url) | Needs addressed by the project | Explanation by the promoter on how the project addresses the need | Relevant system needs study results in 2030 (Border - Capacity Increase) | Relevant system needs study results in 2040 (Border or country - Capacity Increase - Storage flexibility) | Border | Transfer capacity increase A-B (MW) | Transfer capacity increase B-A (MW) | Comments on CBA results by the project promoter

## Trans.Investments
TYNDP 2024 Transmission projects - General information on transmission investments | [8 empty] | Technical characteristics of the investment | [10 empty] | Costs of the investment |  |  |  | CBA indicators at investment level – B8.0 Stability (Transient, voltage and frequency stability) |  |  | Residual environmental impact |  |  | Residual social impact |  |  | Other residual impact
Investment number | Investment Name | This investment belongs to project number… | Description of the investment | Commissioning Year | Status ID 1 : Under Consideration, 2 : In Planning but not permitting, 3 : In permitting, 4 : Under Construction | Is Main Investment(s) | Progress of the investment since TYNDP2022 | Explanation in case of delay or reclustering | Type of Element | Substation From | Substation To | Technology | Type of HVDC | Total route length (km) | Nominal voltage (kV) | Capacity of the investment (MW) | MVA | Type of converter | Mvar | Estimated CAPEX (MEUR) | Sustaining CAPEX (Meuro) | Estimated OPEX (MEUR) | Cost Uncertainty Range | Transient stability | Voltage stability | Frequency stability | Distance (km) | Type of sensitivity | Additional information | Distance (km) | Type of sensitivity | Additional information | Other residual impact

## Stor.Projects
TYNDP 2024 - General description of storage projects | [17 empty] | Needs addressed by the project |  |  |  | Projects costs |  |  |  | Technical characteristics of the project |  |  |  |  | Residual impact of the project |  |  | CBA
Project ID | Project Name | Promoters | Country | National development plan(s) | Storage technology | Project description | Commissioning year estimated by the promoter(s) | Status ID 1 : Under Consideration 2 : In Planning but not permitting 3 : In permitting 4 : Under Construction | Progress of the project since TYNDP2022 | Explanation in case of delay | Type of project - Is it an upgrade of existing infrastructure? | Is the project on the 5th PCI list? | PCI number | Inclusion in previous TYNDPs | Is the project in the reference grid 2030? | Is the project in the reference grid 2035? | Where can one find more information on the project? (ex: project website url) | Needs addressed by the project | Explanation by the promoter on how the project addresses the system needs | Relevant system needs study results in 2030 | Relevant system needs study results in 2040 | Estimated CAPEX (MEUR) | Sustaining CAPEX (Meuro) | Estimated OPEX (MEUR/year) | Cost Uncertainty Range | Total turbining capacity (MW) | Storage Capacity (GWh) | Total Pumping Capacity of Pump Storage (MW) | Roundtrip efficiency (%) | Operational lifetime (Years) | Residual Environmental Impact | Residual Social Impact | Other Residual Impact | Comments on CBA results by the project promoter
1001 | Kaunertal Extension Project | TIWAG-Tiroler Wasserkraft AG | Austria | APG Netzentwicklungsplan 2021 für das Übertragungsnetz der Austrian Power Grid AG (APG), mentioned page 18 and 122; https://www.apg.at/stromnetz/netzausbau/netzentwicklungsplan-2021/ | HydroPumpedStorage | Extension of the existing Kaunertal hydro storage power station by: The new pumped hydro storage power station Versetz and the new reservoir Platzertal and the integration of the new natural water inflow from Ötztal into Reservoir Gepatsch. Regarding "Storage capacity": 1060 GWh is the estimated yearly generation of Pumped Hydro Storage Versetz whereas the total energy delivered to grid when the reservoir is totally emptied is 64 GWh related to the power station Versetz. The round trip efficiency of 75,4% is related to the pumped hydro storage power plant Versetz. The "Kaunertal Extension project" is recognized within the national network development plan 2021 of Austrian Power Grid AG "APG Netzentwicklungsplan 2021 für das Übertragungsnetz der Austrian Power Grid AG (APG), Austria, 2021" mentioned at page 18 and 122. TSO in charge of operating at connection point is APG. | 08-2035 | 3 | Rescheduled |  | MostlyUpgrade | True | 1.11 | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Project Homepage: https://www.tiwag.at/unternehmen/unsere-kraftwerke/ausbauvorhaben/ausbau-kaunertal/ | Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Capability for Black Start & Islanding Operation | Provision of all sorts of ancillary services at high ramp rates in both energy directions (FCR, aFRR, mFRR, and expected future short-, medium- and long-term flexibility products). This facility helps to reduce the lack of winter energy being designed as a seasonal energy storage Provision of all sorts of ancillary services at high ramp rates in both energy directions (FCR, aFRR, mFRR, and expected future short-, medium- and long-term flexibility products) cross border provision of high capacity (MW) and energy (GWh) provision for all sorts of ancillary services at high ramp rates in both energy directions: FCR, aFRR, mFRR, and expected future short-, medium- and long-term flexibility products, redispatch reserves This energy storage facility will significantly support the coordinated grid restoration following the national and international agreements for grid restoration. It will help to reduce critical grid situations and to reduce the risk/extent of socio economomic damage by blackouts. | Austria - Germany - 3100 Austria - Switzerland - 200 Austria - Italy - 500 | Austria - - <1000 Austria - Germany - 3100 - Austria - Switzerland - 1200 - Austria - Italy - 1000 - | 1555.9 | 291.05 | 5.5 | Downward: - 1%; upward: +6%; | 440 | 64 | 400 | 75 | 90 | (1) Extended climate change risk management (flood warning, flood protection/control, avalanche protection/control) in the Ötztal, Kaunertal, Inntal. (2) Enhanced hydrological situation at the river Inn, caused by additional tailwater reservoirs to reduce hydropeaking and surge-effects. (3) Hydrologic influence due to water diversion from the Ötztal to the Gepatsch reservoir. (4) Increased traffic while construction phase. (5) Direct/indirect avoidance of emissions (CO2 and other emissions) by RES-generation. We will provide the societal cost used for monetization of emissions within the CBA process 2024 as well as a new study we will deliver in time in 2024. For the time we refer to the values and results at our study provided by Technical University Vienna 2022 regarding additional benefits of our project - monetization has to be valorized to 2024 (This means preliminary for 2030: 346 €/t and for 2040: 597 €/t as social cost of carbon in 2024 value) . No monetisation here to avoid double counting. (6) The electric power will be transported by cable to the existing Kaunertal Power Station at Prutz via an existing tunnel what causes no additional residual impact. | (1) No relocation of residents. (2) Extended climate change risk management (flood warning, flood protection/control, avalanche protection/control) in the Ötztal, Kaunertal, Inntal. (3) Tax revenues for communities and the province of the Tyrol. (4) Increased revenue for local enterprises. (5) Avoided cost for flood damage = Benefit 52 M€/a. (6) Avoided public cost for flood protection = Benefit 18 M€. (7) Avoided public cost for avalanche protection = Benefit 41 M€. (8) Avoided public cost for traffic infrastructure = Benefit 53 M€. | (1) Estimated reduced income for touristic rafting providers = Negative Benefit: 0,20 M€/a; Reduced income for rafting providers is based on information of the rafting association “Tiroler Raftingverband” provided at a press conference at 03.04.2014 and resulting calculations and assumptions of TIWAG. (2) Added value for industry in EU induced by CAPEX 1555.9 M€ multiplied by 1.63 = Benefit 2536 M€, Sustaining CAPEX 291.05 M€ multiplied by 1.63 = Benefit 474 M€ - undiscounted Price Base 2024 during lifetime of 90 years. (3) Added value induced by OPEX, Price Base 2024: Mean value = Benefit 5.5 M€ operation costs incl. annual maintenance costs.
1003 | Hydro-pumped storage in Bulgaria - Yadenitsa | NATSIONALNA ELEKTRICHESKA KOMPANIA EAD | Bulgaria | Plan for the development of the transmission electricity network of Bulgaria (NDP) for the period 2023-2032, Bulgaria, 2023, pp.12-13, https://www.eso.bg/fileObj.php?oid=4515 | HydroPumpedStorage | PSHPP Chaira has a generating capacity of 864 MW (4 units x 216 MW) and a pumping capacity of 788 MW (4 units x 197 MW). The implementation of Yadenitsa project – by constructing Yadenitsa Dam and a reversible pressure tunnel, will increase the useable capacity (volume) of the lower reservoir of PSHPP Chaira (Chaira Dam) by 9.2 mcm - from 4.2 to 13.4 mcm and thus enable a weekly operating mode of PSHPP Chaira by increasing the generating mode to 20 hours and the pumping mode to 22 hours. The project, as a part of the hydropower complex “Belmeken- Sestrimo- Chaira”, has been declared a national site. The project is of strategic significance for the electricity system in the Republic of Bulgaria and the region of Southeast Europe as it will provide a greater storage capacity for the integration of more renewable energy sources and will significantly increase the balancing flexibility of the European grid. | 2030 | 3 | Delayed | Administrative reasons: The entry into force of the Environmental impact assessment was delayed due to appeals, which were rejected by the competent courts. This impacted all other subsequent necessary project implementation activities. The delay also accumulated due to the non-issuance of a permit for water abstraction and use of surface body water by the competent basin directorate. The latter process has now come to its completion by obtaining a Permit for water abstraction and use of surface water body №31140123/17.10.2022. | Upgrade | False |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | https://nek.bg/index.php/en/our-business/electricity-generation/yadenitsa-project | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project “Yadenitsa” will allow PSHPP “Chaira” to operate for 22 hours in pumping mode, thereby increasing significantly the amount of stored renewable energy during periods of low prices and releasing them in peak hours, facilitating the reduction of RES curtailment and the management of peak loads. Project “Yadenitsa” prepares the national grid for future energy scenarios by increasing PSHPP “Chaira”’s storage capacity and enabling increased cross-border energy flows. The project supports regional energy exchanges, ensuring stability in the single energy market and contributing to the further integration of the European energy network. In case of energy deficit/surplus in one country, the increased storage capacity of PSHPP “Chaira” through project “Yadenitsa” will redistribute energy, easing cross-border flows and the exchange of energy reserves between countries, enabling the coordinated use of reserve capacity and providing short-term and seasonal flexibility. Project Yadenitsa will enable PSHPP Chaira to operate for 22 hours in pumping mode, significantly increasing the storage of renewable energy during periods of low prices and releasing it during peak demand. This reduces RES curtailment, supports the integration of high volumes of RES, and improves grid efficiency and cost-effectiveness. | Bulgaria - Serbia - 1490 Bulgaria - Turkey - 2100 | Bulgaria - Serbia - 1490 - Bulgaria - Turkey - 2100 - | 234 | 0 | 2 | 20 % | 864 | 86 | 788 | 87 | 100 | No impact according to the methodology in 5.14 of the published 4th ENTSO-E Guideline for cost-benefit analysis of grid development projects. | No impact according to the methodology in 5.15 of the published 4th ENTSO-E Guideline for cost-benefit analysis of grid development projects. | Expected impact, subject to pending additional evaluation.
1004 | Estonian PHES (pumped-hydro energy storage) | Energiasalv Pakri OÜ | Estonia | Draft update of Estonia’s National Energy and Climate Plan for 2030, 2023, page86, https://commission.europa.eu/system/files/2023-08/Estonia_Draft_Updated_NECP_2021-2030_en_1.pdf;National Development Plan of the Energy Sector until 2030, 2017, https://www.mkm.ee/sites/default/files/ndpes_2030_eng.pdf, pp.30; "Estonia’s 2030 National Energy and Climate Plan (NECP 2030)", Estonia, 2019, Page no84; Url: https://ec.europa.eu/energy/sites/ener/files/documents/ee_final_necp_main_en.pdf; | HydroPumpedStorage | The Project is an innovative underground pumped-hydro storage plant powered by Zero Terrain technical concept, see https://energiasalv.ee. The upper reservoir is the Finnish Gulf (sea water with very low salinity) and lower reservoir is the >5mill m3 cavern in depth of -600m in the gneiss body. The installed nominal rated power is 506MW, nominal storage capacity per 1 cycle (12 hours) is 6 GWh. | 2032 | 3 | Delayed | COVID-19, delayed public involvement processes for appr. 0,5 to 1 year | New | True | 3.2 | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | https://energiasalv.ee/en/ |  |  |  | Estonia - - <1000 Estonia - Finland - 700 - Estonia - Latvia - 700 - Latvia - - <1000 | 730 | 168 | 3.9 | 15 | 520 | 6 | 500 | 78 | 60 | Our innovative (zero terrain) concept allows the development of greenfield pumped hydro without the main risks of traditional hydro storage: no flooding and no risks from dams. According to EIA, mitigation measures are set for design, construction and operation. By following the mitigation measures insignificant negative environmental impact is foreseen. During the construction phase, the project is able to provide over 4 million m3 of excavated aggregates, and thereby reducing the need for new mining sites. That has a positive influence on land use and availability of necessary materials (for road and railway construction as an example). | During the construction phase, 450 direct jobs will be created (in addition to indirect jobs). That will provide additional tax revenues and opportunities for local enterprises. (estimated increase of GDP during the construction period is 196 M€) Due to the existing port and railway, Paldiski has huge potential for industries, by providing energy reliability the project increases that potential even further. For the construction of the project, local roads and railway will be repaired. | Increasing the stability of energy price at lower level, project has a positive influence on the whole region (for industries and habitats). According to models, the project would be a "price maker" and just operating this plant would reduce energy prices in the region by 55M€ annually. During the first 20 years of operation estimated influences to Estonian electricity consumers: the project would reduce electricity prices by 705 M€ and, due to regulated calculation for network fees, also decrease network fees by 58 M€. By providing LFC (load frequency control services), the project will provide support to control the frequency of Baltic countries (desynchronised from Russia).
1006 | HPS AMFILOCHIA | TERNA ENERGY - PUMPED STORAGE I (special purpose vehicle of TERNA ENERGY S.A) | Greece | TEN - YEAR DEVELOPMENT PLAN (ADMIE) 2022-2031- GREECE - 12/09/2022-Pages 48617, 48670 and 48811, https://www.admie.gr/systima/anaptyxi/dekaetes-programma-anaptyxis | HydroPumpedStorage | The project Hydro Pumped Storage System in Amfilochia, consists of two independent upper reservoirs, Ag. Georgios & Pyrgos respectively, while the existing Kastraki lake will serve as a lower reservoir (Owned by the Public Power Corporation). According to the latest EIA amendment, issued on 21.08.2023, and due to the increase of the height of the Dam of Agios Georgios, the total net volume of the upper reservoirs is 8,7 million m^3 and the total storage capacity of both projects, is 4.88 GWh. The purpose of the project is to absorb energy for pumping from wind, photovoltaic or thermal energy in order to store water in the upper reservoirs during periods of low load consumption or renewables overproduction. Subsequently, energy is recovered via turbine mode during the peak load. The electromechanical equipment will be installed in a single building (Powerhouse), on the right bank of the Kastraki lake. Total installed capacity is 680 MW for production and 730 MW for pumping. The construction of the Project started in November 2022. | 2026 | 4 | Delayed | Long permitting procedures as concerns the Environmental Permits. State Aid approval in December 2021. Private and forest land acquisition up to June 2022. Issuance of construction permits in October 2022. Start of construction November 2022. | New | True | 2.9 | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | In October 2013 the European Commission has included the Project in a list of 248 key energy infrastructure projects under the new guidelines for trans-European energy infrastructure, carrying the label “Projects of Common Interest” (PCI) (as PCI 3.24). These projects contribute to the market integration, enhance the security of supply and reduce the CO2 emissions; hence they benefit from faster and more efficient permit procedures and financial granting. Moreover, the Project has been classified as a Strategic Investment by the Greek Authorities. In August 2014 Terna Energy, after a CEF- Energy call, applied for co-financing of the Project Design and Environmental Impact Assessment. The relevant Contract with INEA was signed in March 2015. The Design Studies (Engineering and Detailed) and a large programme of geological and geotechnical works was completed successfully in December 2016. In January 2018 the Ministerial Decision approving Environmental Terms was issued. This Decision is the most critical step in permitting procedure. The remain licensing stages, up to the Construction Permit issuance, is a standard process, without the risk of unfavorable results. In the meantime a modification of the connection arrangement was needed, according to IPTO instructions and the substitution of the open-air UHV Centre by GIS. The relevant modification of the Environmental Study was issued to the permitting authority in March 2019. The modified environmental Decision was issued in April 2021 in delay, due to Covid 19, which created many problems in permitting authorities. For more information: https://www.terna-energy.com/activities-en/pumped-storage-projects/ |  |  | Greece - North Macedonia - 500 Greece - Italy - 1500 Cyprus - Greece - 1000 Greece - Turkey - 1600 | Greece - North Macedonia - 1000 - Albania - Greece - 1000 - Greece - Italy - 500 - Cyprus - Greece - 1000 - Greece - Turkey - 1100 - | 646.3 | 135 | 18.1 | 5% | 680 | 5 | 730 | 75 | 50 | For the installation of the Project an area of 1,48 km2 will be permanently occupied. It mainly concerns forestry land, without any environmental "sensitivity". A small percentage are abandoned farms. The initial Environmental Impact Assessment Study was carried out and submitted to the relevant authorities in 2016. The overall environmental impacts from the project (waterbodies, air, noise, landscape etc) have been assessed in detail in the 2016 Environmental Impact Assessment study. Their positive overall assessment led to the approval of the above Study by the Authorities and the issuance of the Environmental Terms (it includes the Approval of Forestry land occupation). The Project does not affect environmentally sensitive areas. The Decision approving Environmental Terms was issued in January 2018. For the Forestry land occupation, a right of use is paid. For the private areas, the Company bought them.The Project does not create movement of population and does not affect cultural heritage. The roads to be constructed will improve the access to the remote villages, at the Project area. It does not change significantly the waterbodies. The landscape is affecting by the two dams construction, which will bound the two upper reservoirs of 2,0 million m3 and 6,7 million m3. All the other components of the Project are mainly underground works. | The project is located in the western Greece region, prefecture of Aitoloakarnania, Valtos province. A remoted, economically poor and degraded area where local residents are engaged in small-scale livestock farming and land cultivation. At the peak of the construction phase, around 900 people are expected to be employed, directly and indirectly, while a variety of machinery and raw materials will be utilized. During operation, local specialized and auxiliary personnel will be employed in 60 new jobs. Additionally the engineers and technicians will enhance their technical experience. The project will relieve internal and external immigration. Apart from constructing dams, powerhouse and reservoirs, the Project’s implementation also includes the maintenance, improvement and extension of the infrastructure network in the area (roads, etc.), which will also have a positive impact on the region. The Project Owner has carried out a communication and visibility Plan, including website, information leaflets, newsletters, presentations, reports & internal project deliverables etc. As a result of all the above, rarely a private Project has been so positively expected by local population, in terms of social acceptance, than Amfilochia Hydro Pumped Storage. Last but not least, this Project has a very high Added European Value. | All impacts expected due to the Project’s implementation have been thoroughly assessed in the initial (2016) Environmental Impact Assessment Study and its amendments, which have already been approved by the relevant authorities.
1012 | Purifying -Pumped Hydroelectric Energy Storage Navaleo (P-PHES Navaleo) | "CDR TREMOR, S.L." | Spain |  | HydroPumpedStorage | P-PHES NAVALEO in Leon, Spain, is pure pumped plant (CLOSED LOOP) with an installed capacity of 552 Mw. (3 x 184 Mw.) in generating mode and 548 Mw in pumping mode and generate an annual capacity of 1332 Gwh/year. The projects consists in two reservoirs with a volume of 2,23 Mio m3. The total rated flow are 90 m3/s in generating mode and 70 m3/s in pumping mode. Normal static head is 710 m. The cycle efficiency is up to 77,8%. Moreover the energy storage, the P-PHES NAVALEO has another 3 IMPORTANT DIMENSIONS: ENVIRONMENTAL: The power plant is integrated in a puryfing cycle of water flowing trough abandoned mines that are currently being directly discharged to the rivers. SOCIAL: Located in the economically depressed region of Castilla y León with unemployment rates of 20% - 30%. P-PHES NAVALEO will contribute to the reintegration of unemployed professionals and shift to a low carbon regional economy. INNOVATIVE: The Hybrid purification – generation – storage process was awarded a patent by the WIPO for the highest ratings to all claims for its novelty, inventiveness and industrial applicability" | 06-2027 | 3 | Delayed | Developmnt is progressing according to the schedule. We have updated the commissioning date, due to an update of the construction (civil works) timeframe of the project. | New | True | 1.12 | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | More information of the project is available in www.cdrnavaleo.eu |  |  | France - Spain - 3000 | Spain - - >10000 France - Spain - 4500 - Portugal - Spain - 1000 - | 340 | 0 | 4.207 | 15% | 552 | 4 | 548 | 78 | 75 | In July 2021, P-PHES NAVALEO finally obtained a positive outcome in Environmental Impact Assessment ”EIA” (in Spain, Declaración de Impacto Ambiental “DIA”) process by the competent authorities including directly the project improvements in the management of residual materials in the construction phase. No significant environmental impact was specifically informed by the competent authorities. | During permitting process and public consultation evaluation, no significant social impact was informed. | During permitting process, no other residual impact was informed.
1013 | CAES Zuidwending, NL | Corre Energy BV | Netherlands | Not applicable in Netherlands | CompressedAirEnergyStorage | This project will deploy advanced compressed air energy storage (CAES) technology using air storage caverns to be developed in salt deposits. In particular the project will facilitate increased integration of onshore and offshore wind by providing balancing services and system services. The project is configured as two generation (expansion) trains, each of 160 MW capacity, and two compression trains, each of 110 MW capacity. The project will deploy hydrogen-fuelled CAES technology to provide a 100% renewable, highly flexible and cost effective long duration energy storage solution that can be rolled out across Europe to facilitate increased integration of RES. 100% H2 fuelling is anticipated from 2030, after which the project will have zero CO2 emissions. As a substantial customer for green hydrogen, the project will act as a key catalyst in the transition to the hydrogen economy in the Netherlands and across Europe. | 2027 | 3 | Rescheduled | Rescheduled to allow additional design to minimise NOx emissions for compliance with NL environmental legislation. | New | False |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | https://correenergystorage.nl/the-project/ | Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Storage of up to 27 GWh, providing “time shifting” of energy, added generation capacity, avoided investment in conventional thermal generation. Synchronous compression and generation, flexible, fast ramping and extremely low minimum generation level. Provides balancing services as a hedge for variable RES against forecast error. Synchronous compression and generation, flexible, fast ramping from very low minimum generation level. Provides up and down regulation in both compression and generation at lower cost than conventional thermal plant. Rapid change in power intake and output in response to changes in system frequency and voltage. Storage of up to 27 GWh, allowing “time shifting” of energy to enable dispatchable RES. Synchronous compression and generation, flexible, fast ramping and extremely low minimum generation level to support non-synchronised RES. Provides balancing services as a hedge for variable renewables against forecast error. Storage of up to 27 GWh, allowing “time shifting” of energy, reducing curtailment. Balancing ancillary services: aFRR, mFRR and RR. Synchronous compression and generation provide system inertia; fast ramping and rapid change in power intake/output addresses fluctuations in system frequency and voltage, thus supporting RES integration. | Belgium - The Netherlands - 1000 The Netherlands - UK - 2000 | The Netherlands - - 1000 - 5000 Belgium - The Netherlands - 1000 - The Netherlands - UK - 2000 - Germany - The Netherlands - 1000 - | 450 | 30 | 4.5 | +/- 10% | 320 | 27 | 220 | 60 | 35 | Under investigation - Environmental studies and engineering design work in progress to assess and minimise environmental impact including NOx emissions at Natura 2000 sites within 25km radius of the project site. | No | Substantial positive impacts deriving from local investment and employment (100 FTEs). EU-wide innovation value leading to roll-out of hydrogen-fuelled CAES at many sites across Europe.
1025 | Silvermines Hydroelectric Power Station | Siga Hydro Limited | Ireland |  | HydroPumpedStorage | Silvermines Hydro is a strategically situated hydroelectric pumped storage plant in Tipperary. The Project aims to repurpose a historic mining site to generate, store, and transmit energy, with a daily design capacity of up to 1.8GWh, a 360MW. Ireland's hydro capacity is relatively limited compared to other EU power systems, making Silvermines Hydro the second hydroelectric pumped storage power generation source in the State. Silvermines Hydro is a flexible power source that serves as a generation asset, load asset, and grid asset. It can provide crucial system support services to the Transmission System Operator (TSO) and respond swiftly to changing energy demands, making it highly valuable for managing power systems, especially during intermittent renewable generation periods. The Project's intergenerational attributes, dependability, and flexibility significantly enhance Ireland's renewable energy initiatives and aid in managing Ireland's planned low-carbon power system effectively. The benefits include reduced wind curtailment, lower carbon emissions, and decreased electricity production and operation costs. Silvermines Hydro improves Ireland's security of energy supply, mitigates isolation risks as an Island power system on the periphery of Europe and enhances the overall efficiency of the power system. | 12-2030 | 3 | Project on time | Project is in permitting since 08-2023 | New | True | 1.13 | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | website available at www.silvermineshydro.com | Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Silvermines Hydro contributes directly to system adequacy by serving peak loads with energy from excess renewable generation. Capacity derating factors are in the range 0.4 to 0.5 meaning up to 180MW of dispatchable power can be included in system adequacy models Pumped storage provides excellent support for system stability. Silvermines Hydro could provide up to 2000MWs of inertia and ramping capability of over 10MW/s to improve system ramp rate, contribute to transient stability and manage RoCoF Pumped storge is widely recognized as an excellent provider of balancing energy. Silvermines Hydro will be capable of providing up to 600MW of balancing energy Wind curtailment in Ireland reached 1,663 GWh in 2023. Silvermines Hydro could reduce future curtailment levels by up to 530GWh per year representing over €40m worth of energy | Island of Ireland - Great-Britain - 1450 Island of Ireland - France - 700 | Ireland - - 1000 - 5000 Island of Ireland - Great-Britain - 1954 - Island of Ireland - France - 700 - | 565 | 15 | 7.7 | The current uncertainty range is +/- 10%. This uncertainty is associated with design optimization and variances in quantities, rates and prices | 360 | 2 | 360 | 80 | 50 | The Project will impact on Silvermines SAC and SPA in accordance with the Birds and Habitats Directive. This impact can be mitigated and the cost of same are included in the total Capex under indicator C1. | The Project is re-using a brownfield historic mining site and can uniquely offer potential for environmental enhancement and social benefits on realisation of the Project. This social impact indicator is zero or negative in this instance, in that the Project has beneficial environmental and social impact. | The re-use of the Project Site (a former brownfield mining site) can offer beneficial environmental and social impact. There is a positive residual impact (other residual impacts due to improvements and environmental enhancements) of €20m on commissioning of the Project in 2028.
1026 | Hydro pumped storage Riedl | Donaukraftwerk Jochenstein AG | Germany | NDP Germany 2037/2045 (2023), Approval of the scenario framework 2023-2037/2045, List of power plants, BNetzA-ID: BNAP098 (page 33), TSO_ID: 2303a, 2303b | HydroPumpedStorage | A pumped storage power plant at the German / Austrian border is planned upstream from existing Jochenstein hydro power plant at the Danube. Drawdown and return of water will be ensured via Danube and a storage lake will be built southwest of Gottsdorf village, approx. 350 m above the storage of Jochenstein dam. The upstream water conduit is designed as an inclined shaft. The power shaft will be located in the best possible situation given the encountered geological conditions. The downstream water conduit joins the intake/outlet structure on the Danube underground. The project focuses mainly on the integration of RES (Wind, PV), reduction of CO2 and non direct GHG emissions as well as system flexibilty. Currently, extensive work is in progress in order to obtain the approval of the authorities. | 2030 | 3 | Delayed | Claim for supplementary expertise by the permission authority | New | True | 1.14 | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Promoter requested to keep the financial information confidential since the project is part of business exposed to competition; Promoter has provided the Cost figures via the official TYNDP communication channels. Project Homepage: www.energiespeicher-riedl.com | Capability for Black Start & Islanding Operation Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | The project is capable of islanding operation as well as black start. It prevents socio-economic damage of 1 to 1.5 MEuro/year by avoided blackouts. | Czech Republic - Germany - 1000 Austria - Germany - 3100 | Germany - - 5000 - 10000 Czech Republic - Germany - 1000 - Austria - Germany - 3100 - | 400 | 66.9 | 2.97 | +/- 5 %, based on company's experience with similar pumped storage plants | 300 | 4 | 300 | 80 | 100 | The project ist partly located inside area protected under terrestrial Habitats directive and national law. Negative residual terrestrical Impacts are not expected due to continous functionality measures, which were erected in 2011. Since then their funtion is checked yearly and confirmed by environmental experts. Impacts on Danube river protected under aquatic Habitats directive are possible. Negative residual impacts are not expected due to continous functionality measures, which will be simultaneously erected with the project and fully functional before commissioning starts. | The project area is scarcely populated. Residual social impact is excluded due to emission-free operation of the project. Parts of the project area are protected by national landscape law, possible negative effects are mitigated by underground arangement of the project (i.e. waterways, machine shaft). | Positive effects of the project: Economic strengthening of the region. Intensification of tourism. Job creation during construction and operation (about 10 permanent posts)
1027 | Purifying -Pumped Hydroelectric Energy Storage CUA (P-PHES CUA) | CENTRAL DEPURADORA REVERSIBLE DEL RIO CUA, S.L. | Spain | Pag. 3/8 | HydroPumpedStorage | P-PHES CUA is an innovative project that combines the power storage by pumping with purifying mine water contaminated with toxic metals. The scheme is as follows: mine waters discharged to the river currently untreated and after homogenization and purification, are introduced into the hydraulic circuit of a pumping plant consisting of 2 tanks dug outside the river with a slope of 322 m. Through the transfer of water between reservoirs by pumping and turbine hereinafter the oxygen needed to precipitate contaminants which are removed periodically and managed in accordance with the rules of residues. Subsequently, the water is returned to the river purified allowing to meet "good ecological status" under Directive 2000/60/EC Water Framework. Moreover the energy storage, the P-PHES CUA has another 3 IMPORTANT DIMENSIONS: ENVIRONMENTAL: The power plant is integrated into a purifying cycle of water flowing through abandoned mines that are currently being directly discharged to the rivers. SOCIAL: Located in the economically depressed region of Castilla y León with unemployment rates of 20%-30%. P-PHES CUA will contribute to the reintegration of unemployed professionals and shift to a low carbon regional economy. INNOVATIVE: The Hybrid purification – generation – | 01-2028 | 3 | Project on time |  | New | False |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False |  |  |  | France - Spain - 3000 | Spain - - >10000 France - Spain - 4500 - Portugal - Spain - 1000 - | 275 | 0 | 3 | 15% | 375.82 | 3 | 378 | 79 | 75 | The Project is currently involved in the environmental impact assessment process (in Spain, Declaración de Impacto Ambiental “DIA”). No significant environmental impact was identified or informed by the competent authorities. | No significant social impact was identified or informed by the competent authorities and during the public consultations. | No other significant residual impact was identified or informed during the permitting process.
1029 | PSPP Kozjak | "Dravske elektrarne Maribor d.o.o., Obrezna 170, 2000 Maribor" | Slovenia | Slovenian Network Development Plan 2023-2032, page 37: https://www.eles.si/Portals/EN/Documents/EN/ELES_development_plan_2023-2032.pdf?ver=2023-06-16-154317-607 | HydroPumpedStorage | The project PSPP Kozjak has adopted the national spatial plan since 2011. An SIA was also carried out as part of the adoption process of that plan. As the share of renewable energy sources in the Electricity System of Slovenia increases, in accordance with the adopted NECP, so enhances the need for services that HPP Kozjak will be able to offer in the system. Project is in the permitting phase and in accordance with Slovenian legislation, obtaining a building permit process is carried out in parallel with an additional environmental impact analysis (EIA). Strategic Environmental Assesment was finished within national spatial planning proces. Basic data: - Max. gross head: h = 714,2 m - Effective storage capacity: V = 3.000.000 m3, cca 5GWh - Installed power in turbine mode: 2x 220 MW - Installed power in pump mode: 2x 215 MW - connection to grid: 2 x 400 kV transmission line | 2030 | 3 | New Project | Project is on time. It may be delayed in permitting proces (e.g. acquiring land) | New | False |  | TYNDP 2024 | False | False | Companys homepage: https://www.dem.si/en/development-opportunities/electricity-storage/ Approved National spatial plan (Official Slovenian Journal, in Slovene language): http://www.pisrs.si/Pis.web/pregledPredpisa?id=URED5745 Slovenian Network Development Plan 2023-2032: https://www.eles.si/Portals/EN/Documents/EN/ELES_development_plan_2023-2032.pdf?ver=2023-06-16-154317-607 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | ČHE Kozjak project, with its 400 kV transmission infrastructure, supports increased transmission capacity, enabling efficient cross-border energy flows between EU and non-EU countries. By facilitating energy trading and balancing, it helps reduce price differentials, ensuring better use of transmission networks and improving market integration across regions ČHE Kozjak project, with its 400 kV transmission capacity, enhances infrastructure for future energy scenarios by facilitating cross-border power flows and mitigating loop flows. Its increased capacity supports the integration of renewable energy, improving grid flexibility and stability, and accommodating dynamic energy exchanges across borders for future needs ČHE Kozjak project supports sustainable energy integration by storing excess renewable energy, reducing RES curtailment during periods of overproduction. Its 400 kV grid connection enables efficient, cost-effective grid integration of high RES volumes, optimizing energy flows and enhancing system sustainability through flexible storage and generation ČHE Kozjak project improves system flexibility and stability by rapidly adjusting its 2x 220 MW turbine and 2x 215 MW pump modes. This fast response enhances ramp rates and transient stability, helping manage fluctuations, improving Rate of Change of Frequency, and stabilizing the grid during demand or supply variations |  |  | 570 | 40 | 2.9 | -5/+20% | 440 | 5 | 430 | 74 | 80 | The environmental impacts examined in the Environmental Report and the National Spatial Plan are acceptable - The Environmental Report for the PSPP Kozjak has been approved by the Government of the Republic of Slovenia by passing the National Spatial Plan in 2011.http://www.pisrs.si/Pis.web/pregledPredpisa?id=URED5745 | Huge impact on visual appearance remains after commissioning, because OHT line runs close to residential areas and on top of hills. This may induce additional costs. | Operation of PSPP effects the operation of Drava river HPPs chain, because the lower accumulation reservoir of PSPP is the river itself, upper water level of HHP Fala exactly.
1035 | Ptolemaida Battery Energy Storage System | Prolemaida Storage SMSA (Member of Eunice Energy Group) | Greece |  | ElectrochemicalStorage | A state-of-the-art Battery Energy Storage System(BESS) plant is proposed with a rated power of 250 MW. A storage capacity equal to 1000 MWh is foreseen (equivalent to 4 h of operation at rated output power), substantially larger than the required minimum to achieve an annual energy generation capability of 250 GWh. The plant will consist of Li-ion battery groups connected to multiple DC/AC converters. The BESS will perform energy arbitrage on the daily load curve, will enhance RES penetration through absorption of RES energy that otherwise would be curtailed and will provide the full range of ancillaries and flexibility to the system. The plant will be installed close to existing lignite power stations in Western Macedonia,Greece that will be soon decommissioned and will connect to the 400kVEHV transmission network, via its own EHV substation, satisfying the relevant TYNDP eligibility requirement. The plant can go into operation in a short time after its final licensing procedure as a project, being able to fill gaps in capacity adequacy and flexibility arising from thermal plants decommissioning, demand increase and introduction of substantial additional new RES capacity - https://bess-ptolemaida.eu | 2027 | 3 | Project on time |  | New | True | 2.10 | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | https://eunice-group.com/projects/battery-energy-storage-system-bess/ | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | The goals of EU and high targets of the revised Greek NECP stipulate an increased penetration of RES in Greece (reaching installed capacity of 27 GW ). Ptolemaida BESS being a utility scale storage project facilitates the operation of existing and new RES portofolio and decreases curtailments. The proposed project will participate in local and International Energy Markets. Its role in the region's balancing markets will be beneficial as it can pool/share significant energy amounts. The proposed project will be eligible to perform P-f control, thus offering ancillary services, improving transient stability and offering RoCoF according to system needs. All the above will result to facilitate and accomodate future scenarios for cross-border or loop flows | Greece - North Macedonia - 500 Greece - Italy - 1500 Cyprus - Greece - 1000 Greece - Turkey - 1600 | Greece - North Macedonia - 1000 - Albania - Greece - 1000 - Greece - Italy - 500 - Cyprus - Greece - 1000 - Greece - Turkey - 1100 - | 228 | 95 | 1.6 | 5% | 250 | 1 | 250 | 87 | 25 | An environmental impact assessment for the project is currently being completed and the relative environmental study has been approved by the competent Greek Authorities since 2023 | Disclaimer Note based on CBA Guideline 4.0: Given the maturity of the investment , a residual impact assessment is not yet available. | No other
1038 | CAES Zuidwending Extension | Corre Energy B.V. | Netherlands | Not relevant in Netherlands | CompressedAirEnergyStorage | This project is an extension of CAES Zuidwending, Project 1013. This project will deploy advanced compressed air energy storage (CAES) technology using air storage caverns to be developed in salt deposits. In particular the project will facilitate increased integration of onshore and offshore wind by providing balancing services and system services. The project is configured as two generation (expansion) trains, each of 160 MW capacity, and two compression trains, each of 110 MW capacity. The project will deploy hydrogen-fuelled CAES technology to provide a 100% renewable, highly flexible and cost effective long duration energy storage solution that can be rolled out across Europe to facilitate increased integration of RES. 100% H2 fuelling is anticipated from 2030, after which the project will have zero CO2 emissions. As a substantial customer for green hydrogen, the project will act as a key catalyst in the transition to the hydrogen economy in the Netherlands and across Europe. | 2029 | 1 | Rescheduled | Rescheduled to allow additional design to minimise NOx emissions for compliance with NL environmental legislation | New | False |  | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | https://correenergystorage.nl/caes-the-project/ | Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Storage of up to 27 GWh, providing “time shifting” of energy, added generation capacity, avoided investment in conventional thermal generation. Synchronous compression and generation, flexible, fast ramping and extremely low minimum generation level. Provides balancing services as a hedge for variable RES against forecast error. Synchronous compression and generation, flexible, fast ramping from very low minimum generation level. Provides up and down regulation in both compression and generation at lower cost than conventional thermal plant. Rapid change in power intake and output in response to changes in system frequency and voltage. Storage of up to 27 GWh, allowing “time shifting” of energy to enable dispatchable RES. Synchronous compression and generation, flexible, fast ramping and extremely low minimum generation level to support non-synchronised RES. Provides balancing services as a hedge for variable renewables against forecast error. Storage of up to 27 GWh, allowing “time shifting” of energy, reducing curtailment. Balancing ancillary services: aFRR, mFRR and RR. Synchronous compression and generation provide system inertia; fast ramping and rapid change in power intake/output addresses fluctuations in system frequency and voltage, thus supporting RES integration. | Belgium - The Netherlands - 1000 The Netherlands - UK - 2000 | The Netherlands - - 1000 - 5000 Belgium - The Netherlands - 1000 - The Netherlands - UK - 2000 - Germany - The Netherlands - 1000 - | 420 | 0 | 4.5 | +/- 10% | 320 | 27 | 220 | 60 | 35 | NA | NA | Positive impact of €1.5 - 2 billion over 25 years. See comments below
1041 | Purifying-Pumped Hydroelectric Energy Storage "Velilla del Río Carrión" (P-PHES VELILLA) | C.D.R. CARRIÓN, S.L. | Spain |  | HydroPumpedStorage | P-PHES VELILLA DEL RÍO CARRIÓN in Palencia, Spain, is pure pumped plant (CLOSED LOOP) with an installed capacity of 143,81 Mw. (2 x 71,91 Mw.) in generating mode and 144,40 Mw in pumping mode and generate an annual capacity of 306 Gwh/year. The projects consists in two reservoirs with a volume of 1,015 Mio m3. The total rated flow are 47 m3/s in generating mode and 34 m3/s in pumping mode. Normal static head is 363,90 m. The cycle efficiency is up to 77,8%. Moreover the energy storage, the P-PHES VELILLA has another 3 IMPORTANT DIMENSIONS: ENVIRONMENTAL: The power plant is integrated in a purifying cycle of water flowing trough abandoned mines that are currently being directly discharged to the rivers. SOCIAL: Located in the economically depressed region of Castilla y León with unemployment rates of 20% - 30%. P-PHES VELILLA will contribute to the reintegration of unemployed professionals and shift to a low carbon regional economy. INNOVATIVE: The Hybrid purification – generation – storage process was awarded a patent by the WIPO for the highest ratings to all claims for its novelty, inventiveness and industrial applicability. | 01-2028 | 3 | Project on time |  | New | True | 2.28.5 | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | More Project information is available in www.cdrvelilla.eu |  |  | France - Spain - 3000 | Spain - - > 10000 France - Spain - 4800 - Portugal - Spain - 1000 - | 99 | 0 | 2 | 15% | 143.81 | 1 | 144 | 78 | 75 | The Project have been involved in the environmental impact assessment process (in Spain, Declaración de Impacto Ambiental “DIA”). No significant environmental impact was identified or informed by the competent authorities. | No significant social impact was identified or informed by authorities and public consultations results. | No other significant residual impact was identified or informed during the permitting process.
1044 | Green Hydrogen Hub CAES | Corre Energy BV | Denmark | n/a in Denmark | CompressedAirEnergyStorage | This project will deploy advanced compressed air energy storage (CAES) technology using air storage caverns to be developed in salt deposits. In particular the project will facilitate increased integration of onshore and offshore wind by providing balancing services and system services. The project is configured as two generation (expansion) trains, each of 160 MW capacity, and two compression trains, each of 110 MW capacity. The project will deploy hydrogen-fuelled CAES technology to provide a 100% renewable, highly flexible and cost effective long duration energy storage solution that can be rolled out across Europe to facilitate increased integration of RES. 100% H2 fuelling is anticipated from 2030, after which the project will have zero CO2 emissions. As a substantial customer for green hydrogen, the project will act as a key catalyst in the transition to the hydrogen economy in the Netherlands and across Europe. | 2028 | 3 | Rescheduled | Rescheduled to allow alignment with the development and construction timelines of the electrolyser and hydrogen storage components of the Green Hydrogen Hub. | New | True | 1.16 | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | https://greenhydrogenhub.dk/ | Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Storage of up to 27 GWh, providing “time shifting” of energy, added generation capacity, avoided investment in conventional thermal generation. Synchronous compression and generation, flexible, fast ramping and extremely low minimum generation level. Provides balancing services as a hedge for variable RES against forecast error. Synchronous compression and generation, flexible, fast ramping from very low minimum generation level. Provides up and down regulation in both compression and generation at lower cost than conventional thermal plant. Rapid change in power intake and output in response to changes in system frequency and voltage. Storage of up to 27 GWh, allowing “time shifting” of energy to enable dispatchable RES. Synchronous compression and generation, flexible, fast ramping and extremely low minimum generation level to support non-synchronised RES. Provides balancing services as a hedge for variable renewables against forecast error. Storage of up to 27 GWh, allowing “time shifting” of energy, reducing curtailment. Balancing ancillary services: aFRR, mFRR and RR. Synchronous compression and generation provide system inertia; fast ramping and rapid change in power intake/output addresses fluctuations in system frequency and voltage, thus supporting RES integration. | Denmark - Norway - 1000 Denmark - Sweden - 1700 | Denmark - - <1000 Denmark - Norway - 1000 - Denmark - Sweden - 2700 - Denmark - UK - 1400 - | 400 | 30 | 4.5 | +/- 10% | 320 | 16 | 220 | 60 | 35 | To be determined by EIA currently in progress. | NA | Substantial positive impacts deriving from local investment and employment (100 FTEs). EU-wide innovation value leading to roll-out of hydrogen-fuelled CAES at many sites across Europe.
1046 | Online Grid Controller “PSKW-Rio” | SWT PSKW Rio GmbH & Co. KG | Germany |  | HydroPumpedStorage | The realisation of the project is necessary because of the increasing expansion of RES and the shutdown of base load power plants (nuclear and coal power plants). The shutdown leads to a lack of rotating masses for stabilising the grid frequency, grid voltage etc. Without flexibility options (such as the online grid controller), an increasing share of the energy generated from wind and photovoltaics must be curtailed (feed-in management and redispatch). With the online grid controller PSKW Rio the fluctuating feed-in of RES can be balanced within a quarter of an hour. This leads to a baseload capacity of the fluctuating RES and the security of supply in the future energy system. The online grid controller PSKW Rio is an innovative and new technology that contributes to energy efficiency by increasing the regionally usable RES electricity and thus reduces carbon emissions in line with the European Union´s ambitious targets. The project will provide a significant benefit to the integration of RES and grid stability in the Greather Region of SaarLorLux. | 2030 | 1 | Project on time |  | New | False |  | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | More information on the project can be found under the following link: https://www.swt.de/swt/Integrale?MODULE=Frontend&ACTION=ViewPageView&PageView.PK=5&Document.PK=3584&_p_Menu.PK=0 * Homepage information only updated until the past spatial planning procedure (Raumordnungsverfahren) | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL-BE-LU-FR-DE Capability for Black Start & Islanding Operation Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | As the project is located in the Greater Region with many urban areas with less RES potential (Trier, Luxembourg etc.) and many rural areas with high RES potential, it will facilitate future scenarios with a high share of renewables. It will accommodate them into the completely Greater Region As the project is located in western Germany respectively in the middle of the Greater Region of SaarLorLux and close to the boarders of Luxembourg, Belgium and France, it will provide a significant benefit tot he integration of RES an a reduction of loop flows occurrence in this area. With ternary self-consumption machines, water can be permanently exchanged between the Moselle and the lower reservoir. The pipeline required for this is planned as a filling line for the lower reservoir. In the event of a power failure, a black start is possible at any time. The controllability of the pumped-storage power plant, which runs continuous in operation mode with maximum flexibility (-300 MW to +300 MW in ca. 45 seconds) via hydraulic bypass and electronic power control, enables a flexible, efficient and fast stabilization of the grid an the provision of reactive power | Germany - Luxemburg - 400 Germany - France - 1500 | Germany - - 5000 - 10000 Luxemburg - - <1000 France - - 1000 - 5000 Germany - Luxemburg - 400 - France - Germany - 1500 - | 635 | 0 | 2.6 | 10% | 300 | 3 | 300 | 80 | 80 | As necessary for any large infrastructure project, a spatial planning procedure (with public participation) was carried out. This involved a first assessment of the project's impact on the environment and included various reports such as an environmental impact study, spatial compatibility study, faunistic reports and various other investigations. The relevant participants issued statements concerning any potential impacts of the project, which must be taken into account in the course of the future approval procedure: The Nature Conservation Authority stated that it is highly possible that impacts for protected animal species, the loss of biotopes worthy of preservation and a strong interference in nature can be compensated. This includes early compensatory measures, smaller rescheduling requests and compensatory measures such as afforestation, renaturation of compensation areas and new creation of lean grassland etc. In the planning area, no FFH or bird protection areas according to “Natura 2000” have been designated and no fixed or delimited water protection areas have been identified. Since the pools are sealed on the inside with asphalt, this area will no longer be available for rainwater to seep away. The catchment areas of the springs on the upper pool will be reduced, which means that the spring discharges will decrease or dry up. This will be examined and evaluated in more detail as part of the planning approval procedure. | The studies conducted have comprehensively addressed potential social impacts. Accordingly, concepts for reducing and avoiding any negative impacts were integrated in the planning of the project. During the construction phase, there will be short-term negative effects in the form of dust, pollutant and noise pollution in the immediate surrounding areas. The construction also affects traces of a Roman villa and traces of a historical mining pit which will be lost through excavations and backfilling, when realizing the project. The relevant authorities have already issued a statement that this doesn’t give cause to general concerns against the project. Lasting effects relate primarily to visual changes in the landscape, the elimination of a small part of agriculturally usable areas and the redesign of the landscape-related recreation or tourism area. This will be compensated by measures that preserve the area for landscape-related recreation and tourism, counteracting any negative impairments on the recreational landscape and tourism. To this end, the project envisages various measures such as a visitor centre and various infrastructure measures in the vicinity of the building (viewpoints, circular routes). All temporarily impacted pedestrian pathways such as hiking routes will be restored by the end of the construction phase. The project will directly and indirectly secure jobs and create new ones. On the one hand, a stable, secure and competitive energy supply is an elementary prerequisite for production, growth and jobs. On the other hand, the project can make a direct contribution to safeguarding existing jobs and creating new jobs, both in the construction phase and in the operating phase. Ultimately, it contributes to an improved regional value chain. This is one of the reasons why the project is very popular in the surrounding local communities. | Currently there are no other significant residual impacts which where identified.
1048 | WSK PULS (PHES) | Vattenfall Wasserkraft PULS GmbH | Germany | Title: Netzentwicklungsplan 2035, Version 2021, 2. Entwurf; Country: Germany; Year: 2021; Project number: 50HzT-035; Page numbers: 161, 245-246; url: https://www.netzentwicklungsplan.de/sites/default/files/paragraphs-files/NEP_2035_V2021_2_Entwurf_Teil1.pdf and url: https://www.netzentwicklungsplan.de/sites/default/files/paragraphs-files/NEP_2035_V2021_2_Entwurf_Teil2.pdf and the confirmation of NDP in 2022 (Anhang zum Netzentwicklungsplan Strom 2035, Version 2021, zweiter Entwurf): url: https://www.netzentwicklungsplan.de/sites/default/files/2022-11/NEP_Anhang_Aktualisierung_Februar_2022_0.pdf; pages 246/247 | HydroPumpedStorage | PULS will be a pumped hydro electric storage plant located in the south of Thuringia in the middle of Germany. The plant will have an operating volume of about 4.1 million m³ and an electrical output of 402 MW. The storage plant will produce 838 GWh/a of CO2 free energy from volatile renewable energy sources, which will be enough to supply up to 270.000 households. As a result the regional carbon footprint could be signifcantly lowered. The topographical conditions on site suit the technical requirements of a pumped hydro energy storage plant very well, because of a given difference in height of 250 m between the upper and lower basin. Existing infrastructure (roads, powerlines,...) can be used to build and operate PULS, which results in an environmentally friendly construction and operating phase, because the construction of access roads is kept to a minimum. Also the connection to a 380 kV network is right on site of the planned location, which also minimizes the environmental impact. As a "green battery" PULS will play a huge part in the stabilisation of the network and therefore in a transition towards a carbon free energy system. | 2034 | 2 | Rescheduled | As part of the project purchase from STRABAG, time adjustments to the project were necessary. According to today's status and the experience as power plant operators, who themselves have already built and completed a power plant in the early 2000s (Goldisthal), we know that the old schedule was ambitious, so we have adjusted it/rescheduled. As soon as the hydrological report is completed in 2024, the current new schedule can be confirmed. | New | True | 1.17 | TYNDP 2022 ;TYNDP 2024 | False | False | https://group.vattenfall.com/de/newsroom/pressemitteilungen/2022/vattenfall-erwirbt-projektgesellschaft-fur-pumpspeicherkraftwerk-in-thuringen | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to address system adequacy deficiencies Capability for Black Start & Islanding Operation Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | Pumped storage power plants such as PULS act as a buffer and could counteract and control new flow patterns that the grid was not originally designed for. By enabling rapid and flexible control of electricity through the provision of all types of ancillary services, PULS is able to mitigate the risk of power outages and system deficiencies resulting from the growing market of volatile renewable energy sources. PULS is capable of black start and is available for island operation and grid restoration. PULS is located in an area with a potential shortage of reactive power suppliers. Through the possible provision of reactive power, PULS can make a decisive contribution to improving grid and voltage stability in the state of Thuringia. | Czech Republic - Germany - 1000 | Germany - - 5000 - 10000 Czech Republic - Germany - - 1000 | 470 | 200 | 7.05 | 15% | 402 | 3 | 400 | 80 | 99 | WSK Puls has performed environmental impact studies in the past and continue to do during this stage of development. The Project will have impact on habitats and the environment. WSK Puls is aware that some residual environmental impact in Biotops and natural protection areas will need to be mitigated. Therefor we plan to imply compensation measures that are species appropriate for plants and animals. In some cases, these measures will even be implied before the start of the operation. All mitigation costs are already planned and included in the CAPEX, but the final measures will be agreed with the relevant parties and authority as part of the building permit. Ongoing studies and impacts will be provided over time. | The support of the population of the surrounding communities is a key factor for the long-term success of our project. We are in intensive talks with residents, politicians and authorities to address the needs and concerns of the people. Thus, it is also intended and part of the project planning to improve the local infrastructure such as roads, sewage, water and telecoms. We strongly believe that our project will be beneficial for the local communities since we plan to employ local companies for parts of the construction of the plant. With an investment of 470 MEUR we will need to employ local professionals over the construction period. Therefor WSK Puls could bring substantial growth to the county of Saalfeld Rudolstadt and the land of Thuringia and will help to reduce unemployment. All mitigation costs are already planned in the CAPEX. Ongoing studies and impacts will be provided over time. | All mitigation costs are already planned in the CAPEX. Ongoing studies and impacts will be provided over time.
1050 | SE Integrator | Slovenske Elektrarne | Slovakia | yes, Title of the NDP: Desaťročný plán rozvoja prenosovej sústavy na roky 2024 – 2033, Publication year: April 2023 URL: 575_dprps.pdf (gov.sk) Pages: 59-61 | HydroPumpedStorage | The project consists of an upgrade of the existing pumped hydro energy storage (PHES) Cierny Vah, along with a hybridization of the pumped storage plant by adding electrochemical storage. Currently, the PHES, consisting of 6 generators and commissioned in 1982, has only limited flexibility (fixed 100 MW per TG in pump mode, 70 to 110 MW in generation mode) with grid regulation possible only in turbine mode. Due to increasing penetration of variable RES, industry decarbonization and retirement of the existing coal capacity, our region will likely face periods with insufficient ancillary services capacity. Major maintenance interventions need to be executed at the PHES by 2031 to prolong its lifetime. These maintenance windows can be used to execute an ambitious refurbishment to give the PHES state of the art technical parameters. The proposed upgrade of turbo generators will lead to increased turbine&pump efficiency and will be coupled with a minimum of 70 MW, 105 MWh (net) battery. This will result in a hybrid system, combining the advantages of pumped storage and electrochemical storage, capable of provision of fast flexibility in the range of approximately -670 MW and +730 MW. | 2030 | 2 | Project on time | a sligthly different timeline compared to the TYNDP 2022 timeline due to more time necessary to obtain final investment decision due to financing gap | MostlyUpgrade | True | 2.11 | TYNDP 2022 ;TYNDP 2024 | False | False | http://www.integrator-se.sk/ | Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Capability for Black Start & Islanding Operation | The project will bring additional ancillary services capacity, which will be needed due to the decommissioning of fossil fuel plants and increased RES penetration. The project will thus contribute to addressing the challenge of significant changes in the generation mix. Detailed simulations on a single bus model have shown that the project will lead to an improvement in both RoCoF and Frequency Nadir. In practical terms, the project may help to avoid major load shedding in case of a large production outage. The overall available balancing capacity after the refurbishment can range from -698 MW to 764.8 MW. Because of good interconnections between Slovakia and neighboring countries, this capacity will be shared through the MARI & PICASSO platforms. The project will provide an increase in the regional blackstart capacity and avoid additional investments. It will increase the dispatchable capacity to facilitate the start-up of the Slovak electricity system following a blackout and improve reliability of existing Blackstart capacity. | Czech Republic - Slovakia - 500 Hungary - Slovakia - 500 | Czech Republic - Slovakia - 500 - Hungary - Slovakia - 1000 - Poland - Slovakia - 500 - | 206 | 30 | 2.8 | +/- 30% | 730 | 4 | 670 | 77 | 50 | An Enviromental Impact Assesment study will be filled with the relevant authorities in October 2024. The environmental impact is will be likely very low as the project consists of modernizing existing turbines at an existing Pumped Hydro Energy Storage. The battery storage addition will necessitate up to 3000 m2 (depending on the supplier) of land adjacent to an existing switchyard. | The social impact will be likely neglible as the project consists of modernizing existing turbines at an existing Pumped Hydro Energy Storage. The battery storage addition will necessitate up to 3000 m2 (depending on the supplier) of land adjacent to an existing switchyard. | No residual impact as the project consists of a modernization of an existing site and addition of battery storage on an adjacent plot
1052 | Purifying -Pumped Hydroelectric Energy Storage Buseiro (P-PHES BUSEIRO) | CDR BUSEIRO, S.L. | Spain |  | HydroPumpedStorage | P-PHES BUSEIRO in Asturias, Spain, is a pure pumped plant (CLOSED LOOP) with an installed capacity of 153,18 Mw. (2 x 76,59 Mw.) in generating mode and 162,14 Mw in pumping mode and generate an annual capacity of 419 Gwh/year. The project consists of two reservoirs with a volume of 1,599 Mio m3. The total rated flow is 30 m3/s in generating mode and 24,6 m3/s in pumping mode. Normal static head is 316 m. The cycle efficiency is up to 95%. Moreover, the energy storage, the P-PHES BUSEIRO has another 3 IMPORTANT DIMENSIONS: ENVIRONMENTAL: The power plant is integrated into a purifying cycle of water flowing through abandoned mines that are currently being directly discharged to the rivers. SOCIAL: Located in the economically depressed region of Asturias with unemployment rates of 20% - 30%. P-PHES BUSEIRO will contribute to the reintegration of unemployed professionals and shift to a low carbon regional economy. INNOVATIVE: The Hybrid purification – generation – storage process was awarded a patent by the WIPO for the highest ratings to all claims for its novelty, inventiveness and industrial applicability" | 04-2028 | 3 | New Project |  | New | False |  | TYNDP 2022 ;TYNDP 2024 | False | False |  |  |  | France - Spain - 3000 | Spain - - > 10000 France - Spain - 4500 - Portugal - Spain - 1000 - | 87 | 0 | 2 | 15% | 153.18 | 1 | 162.14 | 79 | 75 | The Project is currently involved in the environmental impact assessment process (in Spain, Declaración de Impacto Ambiental “DIA”). No significant environmental impact was identified or informed by the competent authorities. | No significant social impact was identified or informed by the competent authorities and during the public consultations. | No other significant residual impact was identified or informed during the permitting process.
1054 | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | REPSOL GENERACIÓN SLU | Spain | Aguayo II project is integrated in the Spanish National Plan for the Development of the Electricity Transmission Grid 2015-2020. P. 199, Table 3.66. The link above. The extension of the REE substation where the Project's power evacuation line will be connected is included in the Electricity Transmission Grid Development Plan published for the period 2021-2026 (Pages 137, 384 and 386). | HydroPumpedStorage | Construction and commissioning of a Reversible Hydraulic Power Plant, called "AGUAYO II" with a capacity of 1000 MW. It will be located in the Alsa reservoir.The project will pump the water from this existing reservoir to a existing higher reservoir named Mediajo and will turbine it to generate electricity and restoring it back to the Alsa reservoir. It will be equipped with 4 reversible turbine-pump hydraulic groups. Daily Storage Capacity: 6.000 MWh (6 hours of operation in turbine mode). Equivalent annual energy production: approximately 2000 GWh. Maximum annual volume : 10 Hm3. ( upper reservoir capacity) Maximum turbine mode flow: 360 m3/s Maximum pump mode flow: 280 m3/s. Water destination: Electricity production under the Reversible Power Plant regime. Non consumptive use. | 2030 | 3 | Project on time |  | New | True | 1.18 | TYNDP 2022 ;TYNDP 2024 | False | False | The information contained in this report is confidential and may not be reproduced without the consent of Repsol. https://www.dropbox.com/s/6q0c679z8j4ewep/TYNDP_2021_Repsol_def_en.pdf?dl=0 | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Mitigate the risk of power failures Infrastructure to address system adequacy deficiencies | According to the updated CBA report following TYNDP 2024 guidelines, the introduction of Aguayo II allows a higher share of renewables, decreasing the curtailment/spillage from renewables 7.3%. Aguayo II PHS enables the reduction of RES energy spillage (curtailment) of 1438 GWh/yr in the Spanish Peninsular system. According to CBA following TYNDP 2024 guidelines, Aguayo II is able to make the system transient stable and to avoid the connection of 1 GT and the ST of a CCGT in Spain. Aguayo II impact to transient stability can be summarized in CCGT energy redispatched avoided: 582.97 GWh AGUAYO II is able to store electrical energy and it can be used to balance periods of excess renewable production by storing energy and periods of high demand by generating energy. This is especially relevant in Spain to compensate solar and wind power failures due to lack of resource periods According to CBA following TYNDP 2024 guidelines, Aguayo II contributes to system's firmness and balancing energy exchanges. See indicators B6 and B7 in updated CBA report | France - Spain - 3000 | Spain - - > 10000 France - Spain - 4500 - | 800 | 2.6 | 5.3 | +/-15% | 1000 | 2 | 1000 | 80 | 75 | Favourable Environmental Impact Statement granted in June 2020. The new hydro power plant will be built mostly in cavern reducing to the minimum the visual environmental impact. No actions in existing reservoirs will be carried out. There is no impact to areas protected by Natura 2000 Network, being ZEPA ES0000252 Embalse del Ebro the closest one at more than 5 km and with no ecologic connections which could be affected by the Project. The new high voltage line will be built using the existing path of a 220 kV one; therefore, the construction of this line has no additional impact to the Project. Additionally, the Project includes other preventive and remedial activities such as reforestation to ensure that the project is neutral or generates a negative carbon footprint during all the project cycle. | The municipalities affected by the Project are San Miguel de Aguayo (178 inhabitants), Bárcena de Pie de Concha (674 inhabitants) and Molledo (1476 inhabitants). The Project is supported by three municipalities, evidence of this are the three agreements signed in 2018 by each local Council appreciating the goodness of the Project to the area and the promotion of the local employment, as well as recognizing the conditions principally during the constructions works, including compensatory measures accepted as sufficient to compensate the troubles caused during the construction works. Among the agreed measures are the constructions of two variants of the existing roads to avoid the heavy vehicle traffic through the municipalities during the constructions works, the preparation of 45 hectares of pasture to compensate the temporary occupation of the used lands by the livestock of the area, the promotion of the local employment or the adaption of the paths and tourist trails of the zone, in particular: • the GR74: Eastern Corridor of Cantabria. Phase VII. San Miguel de Luena-San Miguel de Aguayo (Corredor Oriental de Cantabria. Etapa VII. San Miguel de Luena-San Miguel de Aguayo). • the PR S31: The Aguayo’s Route (Ruta de los Aguayos). • the Great Tit Tootpath (la Senda de los Carboneros), and • the way up to the Jano’s peak from the Royal Road of the Sickles (el camino de subida al pico Jano desde el Camino Real de las Hoces). The project also considers the realization of livestock improvements in the surroundings of the Alsa peat bog, such as the installation of feeding and drinking areas for the cattle, the reparation of the perimeter path of the Alsa peat bog and the improvement of the pens. The project will compensate the economic development of the area. The construction of the Project, especially the civil works, will produce an improvement in the employment, this is due to a labor dynamism because of local job creation direct and increased activity of companies in sectors such as construction, services and assembly that may be involved in the execution of the project. In addition, there will be an increase in indirect jobs generated by the project, which will not produce unwanted impacts by not negatively interfering with other economic activities. | The project has the official support of the municipal authorities and from Cantabria government (regional authority) since it would be the biggest industrial investment in the region of Cantabria ever. Additionally, there are agreements signed in 2018 by each local Council appreciating the goodness of the Project to the area and the promotion of the local employment, as well as recognizing the conditions principally during the constructions works, including compensatory measures accepted as sufficient to compensate the troubles caused during the construction works. Finally, during the public information phase when the Administrative Authorization was asked, the municipality of San Miguel de Aguayo, (the main municipality of the three that are affected) submitted an allegation in which certified the municipality’s approval to the Administrative Authorization of the Project, showing in that way an evident and explicit support to the Project, signed in a session of the Plenary Session of the Town Council.
1064 | CHR IRENE | ACCIONA ENERGÍA | Spain |  | HydroPumpedStorage | CHR IRENE is a new Pumped Storage Hydropower (PSH) promoted by ACCIONA ENERGÍA through the company Desarrollos Renovables del Norte. It is located between two energy axes of European Union countries: País Vasco/Navarra (Spain) and Landes (France)/Navarra (Spain), the latter being a PIC project promoted by the Spanish TSO. It is a closed-loop PSH with two new artificial reservoirs off-stream and with the power house located in a cavern. It is planned in two phases, with the same hydraulic circuit and the same cavern. The storable energy is 5,79 GWh. The first phase is designed with a power of 494,8MW and 12 hours of turbine operation. In a potential second phase, the power would increase to 733,5 MW with 8 hours of turbine operation. The design of CHR IRENE has been implemented using a hydraulic short circuit to provide the installation with enough flexibility to assist in controlling the electrical grid and the interconnection between France and Spain. | 31/12/2030 | 2 |  |  | New | False |  | TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Mitigate the risk of power failures Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | The CHR Irene storage is located next to the interconnections with France. Specifically, it is adjacent to the new PCI project that connects Navarra (Spain) and Las Landes (France) It enables the capacity to store energy transferred between countries for use when the interconnection is saturated The CHR Irene storage is located next to the interconnections with France. This fact means that in the event of a risk of failure in the vicinity of the border, CHR Irene can help prevent it. The CHR Irene is designed with flexible units (ternary groups or frequency converters and short-circuit) that allow for maximum flexibility. It will be able to start, stop, and change modes in just a few minutes. The capacity to increase or decrease load will also be flexible The CHR Irene will provide voltage stability through the reactive energy of the turbine/pump unit generators. |  |  | 479.36 | 24.75 | 3.1 | The main uncertainty is given by the terrain, that is, by the geotechnics. | 494.8 | 6 | -476.1 | 79 | 75 | No residual environmental impacts are expected since the entire project is located outside of protected natural áreas (RED NATURA 2000, LIC, ZEPA). Furthermore, the entire hydraulic circuit is designed underground to avoid visual impact, and there are no waste heaps or new access roads being opened. | No residual social impacts are expected as there is support from municipal authorities and the regional government. | Not identified
1066 | Kemijoki PSP | Kemijoki Oy | Finland | No | HydroPumpedStorage | Kemijoki Oy is planning to build a large pumped hydro storage power plant in Kemijärvi municipality in northern Finland. The pumping and electricity production capacity of the project is 550 MW, and the size of the electricity storage is 4400 MWh. The amount of energy produced in a year is around 420 GWh. The project would be the first large-scale pumped hydro storage power plant in Finland and it offers much-needed energy storage capacity and flexible power production to the Finnish power system. The Finnish electricity users would gain as the PSP reduces spot and balancing market prices as well as the need for system reserves. Kemijoki Oy is the largest producer of hydro power in Finland. Kemijoki's annual production is approximately 4750 GWh (2022), which accounts for one third of hydro power production in Finland. The company owns 20 hydropower plants (1166 MW). Kemijoki Oy's largest shareholder is the Finnish state, which owns a total of 50.10% of Kemijoki Oy's entire share capital. | 2032 | 1 |  |  | New | False |  | TYNDP 2024 | False | False | Kemijoki Oy published in April 2023 that the company is exploring the possibility of building pumped storage hydropower plants in Northern Finland: https://www.kemijoki.fi/viestinta/tiedotteet-ja-uutiset/kemijoki-oys-new-pumped-storage-hydropower-plants-are-the-key-to-a-safe-energy-transition.html?opened=2142 Kemijoki Oy will publish the site location in November 2023. Pumped storage project website will be published in Q1/2024. |  |  |  |  | 758 | 60 | 7.6 | The capex 758 M€ includes risk reservation for contingencies (15%, 110 M€). | 550 | 4 | 582 | 77 | 80 | Direct emissions savings estimated at 10 000t CO2 per year by replacing fossil-fired electricity generation, which is equivalent to the emissions of 5 000 vehicles. Indirect emissions savings by enabling more investments into renewable energy and electrification of industrial processes. Also, The PSP can ease the internal North-South transmission grid constraints in Finland, and thus reducing the need for new transmission line corridors. Locally, the PSP affects the water flows in lake Kemijärvi, which serves as a lower basin for the pumped storage. Also, the upper basin will be a new artificial lake formed by dams and natural surface shapes. | Direct positive benefits of the PSP to local municipal economy comes through employment and property taxes. From a technical standpoint, the PSP enables more renewable energy to be connected to the grid in the North of Finland and increased electricity consumption in the South of Finland. | PSP lowers and offers more stable electricity price in Finland, which improves the profitability and reduces cost uncertainty of new investments, making Finland more attractive as an investment environment. PSP reduces the electricity price differences between Finland and Sweden and unifies the Nordic electricity prices. This makes the Nordic common market more effective by reducing bottlenecks.
1067 | PSP CONSO II | IBERDROLA GENERACIÓN SAU | Spain | Yes. Title of the document: "Plan de desarrollo de la Red de Transporte de Energía Eléctrica. Período 2021-2026". Country: Spain. Year: Period 2021-2026. Project number: "Actuación GEN_ALM", and "ANEXO II: NUEVAS ACTUACIONES: POS50". Page number: 384-385-386, and 434. Url: https://www.planificacionelectrica.es/en/home | HydroPumpedStorage | PSP CONSO II is a new pumped-storage hydropower station to be built between the existing reservoirs of Cenza and Bao, in Orense, Galicia, Spain. It will include six 300 MW-rated reversible units totalling 1800 MW of maximum capacity, for both pump and turbine mode. Located in a rough and steep terrain of an environmentally protected area, PSP CONSO II is an underground facility, allowing minimum environmental impact, both during construction and operation periods. The power units, power transformers and ancillary equipment will be located in caverns, in addition to 6 km- and 2 km-long underground pipeline connections to the Cenza and Bao reservoirs, respectively. Moreover, PSP CONSO II is a double hydraulic circuit station, making it a safer, simpler and more reliable project. This provides added value benefits, by means of hydraulic short circuit operating configurations, thus offering flexibility to the grid in a very wide range of power. The station will be electrically connected to the new Viana 400 kV transmission substation to be built by REE, already included in the NDP 2021-2026. The Viana Substation will be connected to the existing Trives and Aparecida substations, by opening the current Trives-Aparecida 400 kV transmission line. | 2033 | 3 | New Project | N/A | MostlyNew | False |  | TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Capability for Black Start & Islanding Operation Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | CONSO II will reduce the use of more expensive CCGT plants and will increase the capacity of use of cross-border interconnections. This reduces the average cost of electricity. Further deployment in other EU countries will reduce price differentials among MS. Due to its large capacity (1800 MW) of stored energy, and fast response rate (inherent to pumped-storage technology), CONSO II is able to provide inertia, primary and transient stability, in addition to RR, aFRR and mFRR services. In case of blackout or other emergencies, CONSO II units will be capable of performing an autonomous black start sequence with emergency generator set and able to operate in islanding operation. CONSO II could therefore be added within the Iberian facilities designated to provide those capabilities. CONSO II reservoirs will be able to store large quantities of energy and avoid renewable energy curtailment when there are surpluses of energy production compared to the demand. The subsequent release of such energy at peak demand periods will also enable a cost-efficient supply, compared to CCGT generation |  |  | 1507 | 80 | 4.9 | 15% | 1800 | 54 | 1800 | 75 | 75 | The Cenza reservoir and most part of the area involved in the PSP CONSO II project are included within a Natura 2000 protected area, in particular the ZEC Macizo Central, Spain (ES1130002), protected under the Habitats Directive. The Bao reservoir, however, is not located within any protected area. The Environmental Impact Assessment (EIA) study was finished and submitted to the Administration in July 2024. The EIA includes an assessment of the residual environmental impact of the project on the Natura 2000 area. In this sense, it should be noted that the PSP CONSO II project will have two main parts: (i) The hydraulic part, to be installed underground. It involves a strip of land of about 8 km long and 0.5 km wide, under which the tunnels will be excavated, and the pipelines and equipment will be installed. About 7 km of the development will correspond to an underground area under the ZEC Macizo Central, while the rest, close to the Bao reservoir, also underground until the generation substation, will not run under a protected area. Only minimum elements will remain permanent civil works modifications on the surface, such as the water intakes both at the Cenza and Bao reservoirs, the water expansion chimneys, the entrance to the tunnels, as well as the access paths to the tunnels (which will mostly make use of the existing ones). In addition, the construction of the project and its operation will be executed in order to create a minimum environmental impact, so that the effect of the project on the surface and above the surface of protected areas is considered to be negligible. (ii) The electric evacuation part. Six underground circuits based on 400 kV isolated cables will connect the step-up underground power transformers of the reversible units to the Conso II 400 kV generation substation of Iberdrola, AIS type, and two 400 kV overhead lines, one double and one quadruple, will connect the 6 circuits to the new Viana 400 kV transmission substation of REE. Those overhead lines will be about 3 km long, but they will not be located in environmentally or socially sensible areas. In particular, the new overhead lines will run in parallel to another existing 220 kV one, creating minimum environmental and social impacts. Following the CBA methodology, the residual environmental impact is described using the following three descriptors: • Stage: In permitting. The final EIA is available and submitted to the Administration in July 2024. • Potential impact: Minimum. As it can be derived from the EIA, about 7 km of the PSP CONSO II project will run within a Natura 2000 site protected under the Habitats Directive, but it will be installed underground, with minimum impacts on the surface, as explained above. Then, about 1 km of electrical connections will run underground and under the Bao reservoir up to the generation substation within a non-protected, non-sensible area. And then, the project will include two 3 km overhead lines running in parallel to another existing line over non-protected, non-sensible areas. All these elements of the project are considered as not having a relevant environmental residual impact within environmentally sensitive areas. In particular, the study of specific damages to Natura 2000 areas included in the EIA identifies only 7 items during all phases of the project (construction, exploitation and dismantling), six of them qualified as “compatible” (lowest level) and the last one as “moderate”. As a result, ordinary compensation measures have been proposed. • Type of sensitivity: Habitats Directive (for the part of the project going underground the ZEC Macizo Central. In conclusion, due to the underground nature of most of the hydraulic part of the project and the little impact of the rest of the project, the impact on the environment identified in the EIA is considered minimum. There will be no harm to the coherence of the Natura 2000 network or to the integrity of the ZEC Macizo Central, and no significant impacts or effects on this area have been identified. The study on specific damages to Natura 2000 areas proposes preventive and corrective mitigation measures that will allow minimising the detected impacts during construction, exploitation and dismantling of the Conso II project. All measures have been budgeted and included in the budget; therefore, no other residual impacts are identified that are not already included in indicators C1 or C2. | As indicated in the “4th ENTSO-E Guideline for Cost Benefit Analysis of Grid Development Projects”, dated in April 2024, social impact characterises the project impact on the local population, as assessed through preliminary studies. This indicator only takes into account the residual impact of a project, i.e., the portion of impact that is not fully accounted for in C1 and C2. Based on the information indicated in the previous section “Residual Environmental Impact (S1)” and following the CBA methodology, the residual social impact is described using the following three descriptors: Stage: In permitting. The final EIA is available and submitted to the Administration in July 2024, including other feasibility studies. In particular, a study on the impact of PSP CONSO II on the population and human health. Potential impact: No. As indicated below, it is considered that the project has no residual social impact. Type of sensitivity: There are two types of social sensitivity items: (i) regarding population density. The PSP CONSO II project will be located in an uninhabited, rural and mountainous area, so that it will not have an impact on densely populated areas. In fact, the area is suffering a depopulation trend and its population is below the national mean. Moreover, the project will not be developed on land that is near to socially sensitive areas (such as schools, day-care centres, or similar facilities). The part of the project closest to inhabited areas is the hydraulic connection (underground) to the Bao reservoir and the generation substation, both of which to be located in the outskirts of the town of Villarino de Conso, having a population of 505 inhabitants (2022). (ii) regarding landscape. The project will not have impact on the landscape, because, although very close to or beneath them, the project will not affect land protected under Directives or International Laws on this matter, i.e: world heritage, land within national parks and areas of outstanding beauty, land with cultural significance and other areas protected by national law. From the landscape point of view, the project will be located in the landscape area of Trives, where the city hall of Villarino de Conso identifies the following main points of interest: • The Bao reservoir. It will not be affected, because the power connections will pass underground under it. • The glacial valley of Cenza. It will remain on the surface, not affected by the underground project. • The Cenza waterfall, one of the largest of Galicia with about 100m fall. It is currently affected by the already existing reservoir of Cenza and the also existing quarry upstream. • The moraine of Chaguazoso. It will remain on the surface, not affected by the underground project. • The mountain range of Invernadero- Natural park of Invernadero. This is a protected natural park, very close to the project area, but not affected by the PSP CONSO II project. It includes several ranges representative of the typical landscape of Galicia, with rounded summits and covered with endemic vegetal species, associated to a rich wild fauna (roe deers, mountain goats, wolves, boars, etc). It was declared natural park in 1997 and it is currently proposed to be included into the ZEC Macizo Central of the Natura 2000 network. • Rivers of landscape relevance: among other ones, the Conso and the Cenza rivers are outstanding. The project will not affect them, insofar as the Cenza and Bao reservoirs are already existing and the project will make use of them without affecting the course of the rivers. As mentioned before, the project will not have a relevant impact on the landscape, because it will be located underground. Only a few elements will keep on the surface (inlet at Cenza reservoir, expansion chimneys, and outlet at Bao reservoir, entrance to tunnels, and access paths, in addition to the generation substation and the overhead lines towards the connection point to the high voltage grid), and all of which will be developed with the maximum care and minimum visual effect to the landscape. Nonetheless, during the time of the execution of the works, nature-based leisure activities carried out in the area, such as fishing in the reservoirs or hiking along the paths, may be temporarily affected but considered negligible. On the other hand, the overhead lines connecting the generation substation to the new 400 kV Viana transmission substation of REE will run in parallel to another existing 220 kV overhead line, therefore minimising its impact, and not running over sensible areas. Therefore, it is considered that the project has been especially conceived to be underground and with such a care in the execution of the works and final restitution of the surface environment, so that it will not have a relevant social and landscape impact during its operating lifetime. | As indicated in the “4th ENTSO-E Guideline for Cost Benefit Analysis of Grid Development Projects”, dated in April 2024, the Other Residual Impact (S3) indicator lists the impact(s) of a project that are not covered by indicators S1 and S2. These impacts may be positive or negative. The following other residual impacts are considered: • Job creation, mostly during the design and construction of the plant, but also during the operation. It is considered that about 3,600 employees will participate along all the project execution period, most of them covered by local people of Galicia. This will help to retain active labour workforce in the area and reduce the depopulation trend of the area. • Driving force in the local economy. During all the project phases (construction, exploitation and dismantling), large efforts will be made, as far as possible, to contract local and regional companies or entities to provide services, components or equipment for the project, therefore stimulating the growth of the local economy. • Skills and knowledge gained by the employees involved in the project. The PSP CONSO II project is an outstanding project, due to its size and to its technical unusual conception. Many not-so-standard and uncommon interdisciplinary design and construction techniques will need to be applied, some of which will not be already mastered in advance by the employees. Iberdrola will establish training programmes in all the needed technical fields, health and safety, etc, in cooperation with the local and regional Administrations, in order to guarantee the success of the project. • Demographic challenge. The municipality of Villarino de Conso where the project will be executed has a population below 1,000 inhabitants with a reduction trend, and it is considered as one of the municipalities of the Demographic Challenge established by the Ministry of Ecologic Transition and Demographic Challenge. The execution of the project will contribute to the objectives of the Agenda 2030 related to the Demographic Challenge Strategy, in particular SDG 1 No Poverty; SDG 5 Gender Equality; SDG 8 Decent Work and Economic Growth; SDG 9 Industry, Innovation and Infrastructure; SDG 10 Reduced Inequality; SDG 11 Sustainable Cities and Communities; and SDG 17 Partnerships to achieve the Goal. • Cultural heritage. According to desk work and archaeological prospections that has been carried out, several elements of cultural heritage have been documented in the project area. In general terms, the impacts generated by the project will be compatible to them or inexistent. In case of a more direct effect on elements of traditional architecture (walls, paths or ponds), the protection, mitigation and restoration measures will allow considering such impacts as moderate. The excavation and earth levelling works will include a previous intensive archaeologic control, according to the usual practice of Iberdrola, that will not only protect but also identify and highlight such elements for the benefit of the population, so that CONSO II project will make a contribution and added value to the cultural heritage elements around the works area. As a general social conclusion, it is expected that the PSP CONSO II will have an excellent social acceptance, not only due to the economic and demographic growth creation in the area, but also due to the large environmental care of the project, with the use of existing infrastructures (the Cenza and Bao reservoirs), its underground character beneath the Natura 2000 protected area, the establishment of the evacuation electric overhead lines in parallel with an existing one, and the great care to be applied in the restoration of the surface natural environment after the execution of the civil works. In summary, the population is already used to the existing infrastructures, and the project will not significantly increase the land use, while enhancing the local economy and trying to improve the demographic trend.
1068 | Hydro-pumped electricity storage GIRONÉS & RAÏMATS | EBERGY 2011 S.L. | Spain | a) October 2015: The National electrical development plan 2015 (H2020 planification) was approved by Minister Council. It contains actions to the develop the grid for storage projects. Specifically, SE MEQUINENZA 1100Mw is included in the National Electrical Development Plan 2015. b) February 2016: The SE NUEVA MEQUINENZA is mentioned in the REE report of February 2016 as a binding action for storage projects c) March 2022: “Planificación Energética. Plan de Desarrollo de la Red de Transporte de Energía Eléctrica 2021-2026” available in the web page of the Secretary of Energy from the Ministry of Ecological Transition. https://energia.gob.es/planificacion/Planificacionelectricidadygas/plan-desarrollo-red-transporte-energia-electrica-2021-2026/Paginas/2021-2026.aspx. Inside the document you can find:  Figure (page 385) shows renewable energy integration action included in the current Planning 2021-2026 that also was included in the previous Planning of the electricity transport network 2015-2020 as a “binding storage action”. “NUEVA ALMENDRALES-MEQUINENZA” (1100 Mw) is a new sub-station in the area supporting exclusively the PHES needs, which commissioning date is Q2 2024.  Figure (page 378) shows a renewable energy integration action included in the current Planning 2021-2026 that also was included in the previous Planning of the electricity transport network 2015-2020 as “non-binding Storage Action”. Two new/expanded substations are considered in the area supporting the PHES plant: “ELS AUBALS” (1592 Mw) with axis development 400/220 kV “Escatrón-Els Aubals-La Secuita” and MEQUINENZA-ASCO (3438 Mw) under investigation. As explained before, the implementation plan of Gironés-Raïmats considers the operation of the PHES facility in two phases. Firstly, the plant will be connected to NEW ALMENDRALES-MEQUINENZA substation in 2027 (already included in the planning period 2021-2026). The second connection point is planned for 2030, predictably ELS AUBALS substation but beyond the planning period 2021-2026. | HydroPumpedStorage | Gironés-Raïmats is a big capacity energy storage project included in the 4th List of Project of Common Interest. Base load power stations in Spain (e.g. coal-fired or nuclear) are being increasingly substituted by fluctuating renewables (mainly wind or photovoltaic). Gironés Raïmats aims to provide a quick response for peak-load energy supply, becoming a useful tool for ancillary services such as provision of contingency reserve, provision of regulation reserve, load following, load shifting (energy arbitrage), black start and voltage support. Gironés-Raïmats uses the pumped hydro energy storage technology (PHES). This facility comprises two new water reservoirs operating in a closed-loop, a 7 km-long steel-lined waterway connecting both the reservoirs, and eight reversible pump-turbines in the powerhouse. With an investment over 2600 million euros, this PHES scheme has 3076 Mw of average installed capacity and 75.4 Gwh of maximum stored energy. The two-phase construction design enables a cost-effectively solution without requiring significant upgrades of the existing transmission system. | 2030 | 1 | New Project |  | New | False |  | TYNDP 2024 | False | False | www.girones-raimats.com https://youtu.be/tpmpPrSxZL8 (in this link yo can see the 3D model video of the building design) | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Capability for Black Start & Islanding Operation Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | The continuous power generation for large electro-intensive consumers, to compensate for the excess pumping hours, allows providing ROTATING INERTIA to the system. The development of a technology park is planned within the G&R perimeter, dedicated to hosting hyperscale data centers. We have proposed a PLI to ensure a constant water (energy) reserve in the upper reservoir to address potential issues in the electrical system. Girones and Raimats (G&R) is located at the center of gravity of renewable generation in Aragon and Catalonia. Its high-capacity design will allow capturing a large portion of those surpluses efficiently, significantly offloading the grid. The Tarragona petrochemical complex is only 60 km from G&R. Its major industries plan to switch from oil to green hydrogen for their heat processes by 2030. G&R can be the source of renewable energy through a dedicated line. |  |  | 2600 | 0 | 30 | ± 15% | 2728 | 75 | 3424 | 79 | 100 | Through careful design and planning, combined with prudent application of proven mitigation measures, Gironés-Raïmats has identified and addressed all potential adverse environmental effects, and reduced the predicted adverse impacts to a low level of significance. No residual environmental impacts have been identified as hydro pumped facilities are not located in potentially sensitive environmental areas (i.e. Habitats Directive, Birds Directive, etcetera). With respect to the grid connection, the publication of Ministerial Order TEC/212/2019 on 25 February kicked off the process of preparing the next electricity transmission grid infrastructure planning for the period 2021-2026. The connection points of the project to the grid have not been yet defined, so an environmental assessment is not yet available. | The Project is close to the two Asco’s nuclear reactors (10km) which closure is expected in 2032 and to the FLIX town where is placed the Ercros industrial complex whose closure is planned in the medium term. Therefore, the populations surrounding the Project are immersed in a process of de-nuclearization (within a 10km radius) and de-industrialization of the Ercros complex. As a result, the social impact of a reversible pumped hydroelectric power plant will be very positive in terms of economic stabilization for these regions. The government considers this area a designated just transition zone due to the denuclearization process. | No additional residual impacts have been identified
1070 | Hydro-Pumped Electricity Storage in Estonia Mine | Eesti Energia AS | Estonia | Estonia’s 2030 National Energy and Climate Plan; Estonia ; 2019 ; pages 78 , 83-84 , 163-164,; https://www.mkm.ee/en/energy-sector-and-mineral-resources/energy-economy/national-energy-and-climate-plan | HydroPumpedStorage | The project will build a 325 MW pumped storage hydro power (PSHP) plant in the abandoned part of Estonia mine which is located in North-Eastern part of Republic of Estonia. Electricity will be stored mechanically by circulating water between two reservoirs at different height level. During electricity oversupply in the grid, water will be pumped into the upper reservoir, and when demand is high, electricity will be generated by releasing water back into the underground lower reservoir. Innovatively, as Estonia does not have mountains, the height difference between two reservoirs will be created from utilizing mining by-products - waste rock and old tunnels. The upper reservoir substructure will be built from more than 5 million tons of limestone mining tailings, and 18,8 km worth of waterproofed and reinforced old mining tunnels will form the lower reservoir. This reuse-based approach enables to build pumped hydro as a brownfield project, with minimal additional environmental impact. Currently there is a 2 – 5 MW nominal capacity pilot hydro-pumped electricity storage plant project being developed as a proof of concept by the same developer in the same location which would be scaled up by 2034. | 2034 | 3 | New Project |  | New | False |  | TYNDP 2024 | False | False | [5 empty] | 1134 | 0 | 23 | +/- 20% | 325 | 858 | 332 | 80 | 40 | Due to the circular economic nature of the project, the overall residual impact (including residual environmental impact) is positive. The PSHP is located on the post-industrial territory and in old, un-used tunnels of a mine. | Due to the circular economic nature of the project, the overall residual impact (including residual social impact) is positive. The PSHP is located on the post-industrial territory and in old, un-used tunnels of a mine. | Due to the circular economic nature of the project, the overall residual impact is positive. The PSHP is located on the post-industrial territory and in old, un-used tunnels of a mine.
1071 | Villarosa | Edison S.p.A. | Italy |  | HydroPumpedStorage | The Villarosa Pumped Storage project consists in a hydroelectric storage system classified as ‘pure pumping’, meaning that the natural inflows in the upper basin are less than 5% of the volume of water annually turbined. The plant will be in Sicily, in the municipalities of Villarosa, Calascibetta and Enna. The project foresees the construction of a new upper reservoir with capacity of approx. 3 mln m3, an underground powerhouse equipped with two reversible pump-turbine and a Full Size Converter, and a waterways system connecting the new reservoir with the existing Villarosa reservoir (Morello Dam). The selected E&M configuration will balance the grid fluctuations thanks to high operational flexibility, allowing the integration of intermittent renewable energies such as solar and wind power. Villarosa PSP can be assimilated to a closed cycle in which the volume of water pumped from the downstream reservoir is then entirely returned to the reservoir itself passing through the plant turbines generating energy. | 2029 | 3 |  |  | New | False |  | TYNDP 2024 | False | False |  | Mitigate the risk of power failures Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | Avoiding grid failures of any kind, improving storage capacity of the electrical system. Future scenarios describe a high diffusion of RES, the Pumped Storage will have a fundamental role for the integration of renewables, as they will provide a series of useful services to the electrical system, including balancing and dispatching services, functional to guarantee the safety and adequacy of the electrical system The Pumped Storage will allow to store part of the generation of Non-Programmable Renewable Sources from the hours of high availability to the hours of low or no availability, managing their overgeneration efficiently, avoiding curtailment and therefore ensuring the achievement of the decarbonization targets. The Pumped Storage will allow to store part of the generation of Non-Programmable Renewable Sources from the hours of high availability to the hours of low or no availability, managing their overgeneration efficiently, avoiding curtailment and therefore ensuring the achievement of the decarbonization targets. |  |  | 550 | 0 | 8 |  | 270 | 1.91 | 290 | 88 |  | EIA positively concluded | EIA positively concluded | EIA positively concluded
1072 | HPS VROCHONERA | TERNA ENERGY S.A. | Greece |  | HydroPumpedStorage | The Hydro Pumped Storage Complex “Vrochonera” consists of two independent Hydro Pump Storage Projects “Vrochonera I” (installed production capacity 424 MW - installed pumping capacity 377 MW) and “Vrochonera II” (installed production capacity 351 MW - installed pumping capacity 344 MW).Total net volume of Upper Reservoir 3.44 million m^3. As Lower Reservoir of the Complex, is considered the existing artificial lake “Agia Varvara” (Owner Public Power Corporation). The purpose of the Project is energy storing to assist renewable sources integration. The excess wind and photovoltaic energy will be stored, through water pumping from the lower to the upper reservoirs, during the low load consumption or in renewable overproduction periods. Subsequently, energy will be recovered via turbine mode, during the peak load hours. The electromechanical equipment will be installed in one common underground Power House. The total installed capacity is 775 MW for production and 721 MW for pumping. | 2031 | 3 |  |  | New | False |  | TYNDP 2024 | False | False | [5 empty] | 1100 | 197 | 31 | 20 | 775 | 8 | 721 | 73 | 50 | The Promoter submitted the Preliminary Environmental Impact Assessment (PEIA) Study in 2022. The relevant authorities approved the PEIA Study in August 2024, under the condition that the archaeological authorities’ term will be applied. Specifically, the archaeological authorities in order to issue a positive assessment for the PEIA, imposed the construction of one common underground Powerstation with one common Lower intake, downstream of the tailrace channel. Consequently, the Promoter revised the design of the Project, based on the archaeological authorities’ recommendations. The Project’s final design consists of an underground common Powerstation, which houses the 7 units, two independent Upper Reservoirs, two independent Waterway systems and one common Lower Intake. The above-mentioned modifications of the Project’s design led to a significant increase of the total budget and a reduction of the environmental footprint. The Promoter submitted the Environmental Impact Assessment Study of the Project on September 11th 2024, with the aim of obtaining the final environmental permit for the Project. Based on the Project’s revised design for the installation of the Project an area of 0,63 km2 will be permanently occupied. It mainly concerns forestry land. The overall environmental impacts from the project (waterbodies, air, noise, landscape etc) have been assessed in detail in the Preliminary Environmental Impact Assessment Study (which has been approved by the relevant authorities) and the Environmental Impact Assessment Study. Part of the Ultra High Voltage Overhead transmission line, the High Voltage Center and the Lower Intake, are located within Habitats Directive Site/Natura 2000 (GR1210002). For the Forestry land occupation, a right of use will be paid. For the private areas, the Company will come to an agreement with the Owners and will buy the areas. The Project does not create movement of population and does not affect cultural heritage. It does not change significantly the waterbodies. The landscape is affecting by the two Upper Reservoirs, of 1,82 million m3 and 1.62 million m3. All the other components of the Project are mainly underground works. | Based on the Project’s revised design during the construction peak are expected 1100 employees and 110 in operation. Many of them will come from the local people, so, they will support their family incomes. Additionally, the engineers and technicians will enhance their technical experience. Apart from constructing powerhouses and reservoirs, the Project’s implementation also includes the maintenance, improvement and extension of the infrastructure network in the area (roads, etc.), which will also have a positive impact on the region. Besides all the above, this Project has a high Added European Value. The Project Owner will carry out a communication and visibility Plan, including website, information leaflets, newsletters, presentations, reports & internal project deliverables etc, in order to inform the local community about the Project. | All impacts expected due to the Project’s implantation have been assessed in the Preliminary Environmental Impact Assessment (PEIA) Study, which has been approved by the relevant authorities in August 2024 and the Environmental Impact Assessment Study, which has been submitted on September 11th 2024.
1073 | Taccu Sa Pruna | Edison S.p.A. | Italy |  | HydroPumpedStorage | Taccu Sa Pruna Storage project consists in a hydroelectric storage system classified as ‘pure pumping’, meaning that the natural inflows in the upper basin are less than 5% of the volume of water annually turbined. The plant will be located between the existing reservoir of Nuraghe Arrubiu and a newly built basin with a volume of approximately 3,000,000 cubic meters in the locality of Taccu Sa Pruna, in the municipality of Esterzili (SU). The planned underground powerhouse is equipped with two ternary group, and a waterways system connecting the new reservoir with the existing one. The selected E&M configuration will balance the grid fluctuations thanks to high operational flexibility, allowing the integration of intermittent renewable energies such as solar and wind power. Taccu Sa Pruna PSP can be assimilated to a closed cycle in which the volume of water pumped from the downstream reservoir is then entirely returned to the reservoir itself passing through the plant turbines generating energy. | 2031 | 3 |  |  | New | False |  | TYNDP 2024 | False | False |  | Mitigate the risk of power failures Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | Avoiding grid failures of any kind, improving storage capacity of the electrical system. Future scenarios describe a high diffusion of RES, the Pumped Storage will have a fundamental role for the integration of renewables, as they will provide a series of useful services to the electrical system, including balancing and dispatching services, functional to guarantee the safety and adequacy of the electrical system The Pumped Storage will allow to store part of the generation of Non-Programmable Renewable Sources from the hours of high availability to the hours of low or no availability, managing their overgeneration efficiently, avoiding curtailment and therefore ensuring the achievement of the decarbonization targets. The Pumped Storage will allow to store part of the generation of Non-Programmable Renewable Sources from the hours of high availability to the hours of low or no availability, managing their overgeneration efficiently, avoiding curtailment and therefore ensuring the achievement of the decarbonization targets. |  |  | 650 | 0 | 8 |  | 340 | 3.04 | 390 | 87 |  | Not applicable - EIA not already obtained, evaluation ongoing | Not applicable - EIA not already obtained, evaluation ongoing | Not applicable - EIA not already obtained, evaluation ongoing
1074 | Construction of pumped-storage hydropower plant “Batak”, which utilizes the pre-existing dams of the “Batashki hydroelectric cascade” - (PSHPP “Batak”) | NATSIONALNA ELEKTRICHESKA KOMPANIA EAD | Bulgaria |  | HydroPumpedStorage | The project PSHPP “Batak” is strategically located to leverage the Batashki hydroelectric cascade dams. It provides both an addition and an alternative to PSHPP “Chaira” with its newly installed generating and pumping mode storage capacity of approximately 800 MW, achieved by connecting and utilizing as an upper reservoir the "Golyam Beglik" dam and as a lower reservoir the "Batak" dam. The implemented project will enhance the energy infrastructure and improve its resilience by integrating new renewable energy generation within the European power grid. In addition, the integration of modern pump-hydro storage technologies will optimize the operation of base power plants, thereby increasing the reliability and flexibility of the Bulgarian electricity system. This will enhance its balancing capabilities, enable flexible 24-hour and weekly management, rapid capacity replacement during emergencies and additional balancing services. Additionally, it will optimize energy pricing in Southeast Europe as it will provide real-time price signals for all regionally coupled market segments. Its implementation has a key role toward achieving the goals and priorities defined in the Integrated National "Energy and Climate" Plan, promoting low-carbon technologies, while preserving energy security. | 2030 | 1 |  |  | New | False |  | TYNDP 2024 | False | False |  | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | PSHPP “Batak” will reduce the price differences by storing energy during periods of low prices and releasing them during high demand. It will support the integration of RES by increasing the use of existing transmission capacities and facilitating the management of peak loads, thus improving grid efficiency. PSHPP “Batak” is planned to be connected to cross-border flows, which will help improve the flexibility and resilience of the power system by ensuring a balance between countries with different energy profiles. In case of energy deficit/surplus in one country, PSHPP “Batak” can store and redistribute energy according to needs, easing cross-border flows and the exchange of energy reserves between countries, enabling the coordinated use of reserve capacity and providing short term and seasonal flexibility. RES often generate surpluses simultaneously. PSHPP “Batak” can store excess renewable energy, thereby facilitating the investment in and enabling the deployment of larger RES quantities; allowing renewable energy to be used when it is most needed; reducing losses and optimizing its use in the grid. |  |  | 911.5 | 0 | 16.41 | 20% | 800 | 14 | 728 | 70 | 100 | No information. Subject to upcoming studies. | No information. Subject to upcoming studies. | No information. Subject to upcoming studies.
1075 | Construction of pumped-storage hydropower plant “Dospat” - (PSHPP "Dospat") | NATSIONALNA ELEKTRICHESKA KOMPANIA EAD | Bulgaria |  | HydroPumpedStorage | The project "PSHPP “Dospat” will serve as both a strategic addition and an alternative to PSHPP “Chaira” with its newly installed generating and pumping mode storage capacity of approximately 800 MW. This will be achieved by connecting and utilizing as an upper reservoir the "Golyam Beglik" and “Shiroka polyana” dams and as lower reservoir the "Dospat" dam. The implemented project will strengthen the European energy grid infrastructure and enhance its resilience through the integration of new renewable energy generation. By leveraging advanced pumped-hydro storage technologies, there will be a marked optimization in the operational efficiency of base-load power plants, thereby strengthening the stability and flexibility of the Bulgarian power grid. The implementation of the project delivers a sustainable energy solution, which will allow for flexible 24-hour and weekly management, rapid capacity replacement during emergencies, and additional balancing services. Its implementation will ensure long-term energy security and is of key importance toward achieving the goals and priorities defined in the Integrated National "Energy and Climate" Plan, promoting low-carbon technologies. | 2032 | 1 |  |  | New | False |  | TYNDP 2024 | False | False |  | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | PSHPP “Dospat” will reduce the price differences by storing energy during periods of low prices and releasing them during high demand. It will support the integration of RES by increasing the use of existing transmission capacities and facilitating the management of peak loads, thus improving grid efficiency. PSHPP “Dospat” is planned to be connected to cross-border flows, which will help improve the flexibility and resilience of the power system by ensuring a balance between countries with different energy profiles. In case of energy deficit/surplus in one country, PSHPP “Dospat” can store and redistribute energy according to needs, easing cross-border flows and the exchange of energy reserves between EU countries, enabling the coordinated use of reserve capacity and providing short term and seasonal flexibility. RES often generate surpluses simultaneously. PSHPP “Dospat” can store excess renewable energy, thereby facilitating the investment in and enabling the deployment of larger RES quantities; allowing renewable energy to be used when it is most needed; reducing losses and optimizing its use in the grid. |  |  | 911.5 | 0 | 16.41 | 20% | 800 | 14 | 728 | 70 | 100 | No information. Subject to upcoming studies. | No information. Subject to upcoming studies. | No information. Subject to upcoming studies.
1076 | Favazzina | Edison S.p.A. | Italy |  | HydroPumpedStorage | The Favazzina Pumped Storage project consists in a hydroelectric storage system classified as ‘pure pumping’, meaning that the natural inflows in the upper basin are less than 5% of the volume of water annually turbined. The plant will be in Calabria, in the municipalities of Scilla and Bagnara Calabra. The project foresees the construction of a new upper reservoir with capacity of approx. 1 mln m3, an underground powerhouse equipped with two ternary groups, a surge tank, and a waterways system connecting the new reservoir with the lower basin (Tyrrhenian Sea). Pumped storage plants, such as Favazzina PSP, will balance the grid fluctuations thanks to high operational flexibility, allowing the integration of intermittent renewable energies such as solar and wind power. The Favazzina PSP can be assimilated to a closed cycle in which the volume of water pumped from the downstream reservoir is then entirely returned to the reservoir itself passing through the plant turbines generating energy. | 2032 | 3 |  |  | New | False |  | TYNDP 2024 | False | False |  | Mitigate the risk of power failures Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | Avoiding grid failures of any kind, improving storage capacity of the electrical system. Future scenarios describe a high diffusion of RES, the Pumped Storage will have a fundamental role for the integration of renewables, as they will provide a series of useful services to the electrical system, including balancing and dispatching services, functional to guarantee the safety and adequacy of the electrical system The Pumped Storage will allow to store part of the generation of Non-Programmable Renewable Sources from the hours of high availability to the hours of low or no availability, managing their overgeneration efficiently, avoiding curtailment and therefore ensuring the achievement of the decarbonization targets. The Pumped Storage will allow to store part of the generation of Non-Programmable Renewable Sources from the hours of high availability to the hours of low or no availability, managing their overgeneration efficiently, avoiding curtailment and therefore ensuring the achievement of the decarbonization targets. |  |  | 600 | 0 | 8 |  | 255 | 1.68 | 325 | 83 | 0 | Not applicable - EIA not already obtained, evaluation ongoing | Not applicable - EIA not already obtained, evaluation ongoing | Not applicable - EIA not already obtained, evaluation ongoing
1077 | Serra Del Corvo | Edison S.p.A. | Italy |  | HydroPumpedStorage | The Serra del Corvo Pumped Storage project consists in a hydroelectric storage system classified as ‘pure pumping’, meaning that the natural inflows in the upper basin are less than 5% of the volume of water annually turbined. The plant will be in Puglia, in the municipality of Gravina in Puglia. The project foresees the construction of a new upper reservoir with capacity of approx. 5 mln m3, an underground powerhouse equipped with two reversible pump-turbine, and a waterways system connecting the new reservoir with the existing Serra del Corvo reservoir (Basentello Dam). Pumped storage plants, such as Serra del Corvo PSP, will balance the grid fluctuations thanks to operational flexibility, allowing the integration of intermittent renewable energies such as solar and wind power. The Serra del Corvo PSP can be assimilated to a closed cycle in which the volume of water pumped from the downstream reservoir is then entirely returned to the reservoir itself passing through the plant turbines generating energy. | 2030 | 3 |  |  | New | False |  | TYNDP 2024 | False | False |  | Mitigate the risk of power failures Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | Avoiding grid failures of any kind, improving storage capacity of the electrical system. Future scenarios describe a high diffusion of RES, the Pumped Storage will have a fundamental role for the integration of renewables, as they will provide a series of useful services to the electrical system, including balancing and dispatching services, functional to guarantee the safety and adequacy of the electrical system The Pumped Storage will allow to store part of the generation of Non-Programmable Renewable Sources from the hours of high availability to the hours of low or no availability, managing their overgeneration efficiently, avoiding curtailment and therefore ensuring the achievement of the decarbonization targets. The Pumped Storage will allow to store part of the generation of Non-Programmable Renewable Sources from the hours of high availability to the hours of low or no availability, managing their overgeneration efficiently, avoiding curtailment and therefore ensuring the achievement of the decarbonization targets. |  |  | 600 | 0 | 8 |  | 300 | 2.78 | 400 | 86 |  | Not applicable - EIA not already obtained, evaluation ongoing | Not applicable - EIA not already obtained, evaluation ongoing | Not applicable - EIA not already obtained, evaluation ongoing
1078 | HPS LADONAS | PPC Renewables - TERNA Energy S.A. (special purpose vehicle of TERNA ENERGY S.A) | Greece |  | HydroPumpedStorage | The Hydro Pumped Storage “Ladonas” consists of the Upper Reservoir, the Water Conveyance Systems and the Powerhouse. The net volume is 1,95 million m^3. As Lower Reservoir of the Project, is considered the existing artificial lake “Ladonas” (Owner Public Power Corporation). The purpose of the Project is energy storing to assist renewable sources integration. The excess wind and photovoltaic energy will be stored, through water pumping from the lower to the upper reservoir, during the low load consumption or in renewable overproduction periods. Subsequently, energy will be recovered via turbine mode, during the peak load hours. The electromechanical equipment will be installed in the Power House. The total installed capacity is 225* MW for production and 230.7 MW for pumping. *The Promoter increased the diameter of the waterway system of the Project, resulting the increase of the installed capacity to 225 MW in production mode and the reduction of the installed capacity to 230,7MW in pumping mode. Furthermore, the above-mentioned modification increased the total CAPEX of the Project. | 2031 | 3 |  |  | New | False |  | TYNDP 2024 | False | False | [5 empty] | 300 | 50.8 | 8.4 | 20 | 220 | 2 | 231 | 75 | 50 | For the installation of the Project an area of 0,64 km2 will be permanently occupied. It mainly concerns forestry land, without any environmental "sensitivity". The Environmental Impact Assessment Study was carried out and submitted to the relevant authorities in September 2023. The overall environmental impacts from the project (waterbodies, air, noise, landscape etc) have been assessed in detail in the Environmental Impact Assessment Study. For the Forestry land occupation, a right of use will be paid. For the private areas, the Company will come to an agreement with the Owners and will buy the areas. The Project does not create movement of population and does not affect cultural heritage. The roads to be constructed will improve the access to the remote villages, at the Project area. It does not change significantly the waterbodies. The landscape is affecting by the upper reservoirs, of 1,95 million m3. All the other components of the Project are mainly underground works. | The project is located in remoted, economically poor and degraded region of Peloponnese. The main occupations of the residents are small-scale land cultivation and livestock farming. During construction peak 500 employees are expected and 30 in operation. Many of them will come from the local people, so, they will support their family incomes. Additionally, the engineers and technicians will enhance their technical experience. Apart from constructing dam, powerhouse and reservoir, the Project’s implementation also includes the maintenance, improvement and extension of the infrastructure network in the area (roads, etc.), which will also have a positive impact on the region. Besides all the above, this Project has a high Added European Value. The Project Owner will carry out a communication and visibility Plan, including website, information leaflets, newsletters, presentations, reports & internal project deliverables etc. The Project has been positively expected by local population, in terms of social acceptance. | All impacts expected due to the Project’s implantation have been thoroughly assessed in the (2023) Environmental Impact Assessment Study, which has been submitted for approval to the relevant authorities.
1081 | CAES Ahaus, Germany | Corre Energy BV | Germany | N/a in Germany | CompressedAirEnergyStorage | This project will deploy advanced compressed air energy storage (CAES) technology using air storage caverns to be developed in salt deposits. In particular the project will facilitate increased integration of onshore and offshore wind by providing balancing services and system services. The project is configured as two generation (expansion) trains, each of 160 MW capacity, and two compression trains, each of 110 MW capacity. The project will deploy hydrogen-fuelled CAES technology to provide a 100% renewable, highly flexible and cost effective long duration energy storage solution that can be rolled out across Europe to facilitate increased integration of RES. 100% H2 fuelling is anticipated from 2030, after which the project will have zero CO2 emissions. As a substantial customer for green hydrogen, the project will act as a key catalyst in the transition to the hydrogen economy in the Netherlands and across Europe. | 2029 | 1 | New Project |  | New | False |  | TYNDP 2024 | False | False | https://corre.energy/ | Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Storage of up to 27 GWh, providing “time shifting” of energy, added generation capacity, avoided investment in conventional thermal generation. Synchronous compression and generation, flexible, fast ramping and extremely low minimum generation level. Provides balancing services as a hedge for variable RES against forecast error. Synchronous compression and generation, flexible, fast ramping from very low minimum generation level. Provides up and down regulation in both compression and generation at lower cost than conventional thermal plant. Rapid change in power intake and output in response to changes in system frequency and voltage. Storage of up to 27 GWh, allowing “time shifting” of energy to enable dispatchable RES. Synchronous compression and generation, flexible, fast ramping and extremely low minimum generation level to support non-synchronised RES. Provides balancing services as a hedge for variable renewables against forecast error. Storage of up to 27 GWh, allowing “time shifting” of energy, reducing curtailment. Balancing ancillary services: aFRR, mFRR and RR. Synchronous compression and generation provide system inertia; fast ramping and rapid change in power intake/output addresses fluctuations in system frequency and voltage, thus supporting RES integration. |  |  | 450 | 0 | 4.5 | +/- 10% | 320 | 27 | 220 | 60 | 35 | Not known at present (under consideration) | Not known at present (under consideration) | Not known at present (under consideration)

## 2030NT
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1001st | Kaunertal Extension Project | PINT | 51 | 61 | 36 |  | 26 | 33 | 19 | 14 | 14 | 14 | -230 | -167 | -291 | 2 | 3 | 29 | 46 | 0 | 0 | 0 | 213 | 217 | 208 |  | -88 | -22 | -26 | -1 | -2 | -8 | -3 | 0 | 394 | 394 | 394 | 7 | 7 | 7
1003st | Hydro-pumped storage in Bulgaria - Yadenitsa | PINT | 10 | 12 | 8 |  | 11 | 21 | 2 | 9 | 26 | -4 | -93 | -18 | -186 | -122 | 1 | 12 | 19 | -2 | -15 | -25 | 137 | 405 | -57 |  | -13 | -4 | -7 | 0 | 0 | -1 | -132 | -46 | 404 | 404 | 404 | 7 | 7 | 7
1004st | Estonian PHES (pumped-hydro energy storage) | PINT | 18 | 23 | 14 |  | 9 | 13 | 4 | 15 | 19 | 14 | -80 | -34 | -115 | 1 | 1 | 10 | 16 | 0 | 0 | 0 | 237 | 290 | 207 |  | -178 | -6 | -111 | -4 | -6 | -4 | 12 | 0 | 330 | 330 | 330 | 3 | 3 | 3
1006st | HPS AMFILOCHIA | PINT | 4 | 6 | 1 |  | 2 | 4 | 1 | 1 | 3 | -1 | -20 | -8 | -35 | -68 | 0 | 3 | 4 | -1 | -8 | -14 | 14 | 45 | -16 |  | 0 | 0 | -8 | 0 | 0 | 0 | -70 | -24 | 354 | 354 | 354 | 4 | 4 | 4
1012st | Purifying -Pumped Hydroelectric Energy Storage Navaleo (P-PHES Navaleo) | TOOT | 49 | 57 | 43 |  | 21 | 23 | 19 | 55 | 57 | 52 | -185 | -171 | -199 | 28 | 2 | 23 | 37 | 0 | 4 | 6 | 838 | 864 | 810 |  | -34 | -14 | -10 | 0 | 0 | -5 | 81 | 6 | 530 | 530 | 530 | 4 | 4 | 4
1013st | CAES Zuidwending, NL | PINT | 24 | 32 | 17 |  | 17 | 23 | 11 | 18 | 19 | 17 | -149 | -93 | -205 | -2 | 2 | 19 | 30 | 0 | 0 | 0 | 276 | 290 | 263 |  | -69 | -15 | -27 | -1 | -2 | -5 | 13 | 0 | 169 | 169 | 169 | 5 | 5 | 5
1025st | Silvermines Hydroelectric Power Station | PINT | 18 | 20 | 14 |  | 9 | 12 | 7 | 21 | 29 | 13 | -81 | -66 | -105 | 1 | 1 | 10 | 16 | 0 | 0 | 0 | 326 | 446 | 205 |  | -20 | -7 | -1 | 0 | 0 | -2 | 33 | 0 | 157 | 157 | 157 | 2 | 2 | 2
1026st | Hydro pumped storage Riedl | PINT | 31 | 38 | 26 |  | 14 | 21 | 9 | 19 | 22 | 16 | -122 | -82 | -186 | 82 | 2 | 15 | 25 | 1 | 10 | 16 | 288 | 338 | 241 |  | -45 | -12 | -10 | -1 | -1 | -4 | 389 | 26 | 365 | 365 | 365 | 5 | 5 | 5
1027st | Purifying -Pumped Hydroelectric Energy Storage CUA (P-PHES CUA) | PINT | 38 | 40 | 36 |  | 18 | 20 | 14 | 38 | 40 | 35 | -156 | -119 | -179 | 15 | 2 | 19 | 31 | 0 | 2 | 3 | 590 | 620 | 541 |  | -39 | -7 | -24 | -1 | -1 | -2 | 61 | 4 | 742 | 742 | 742 | 6 | 6 | 6
1029st | PSPP Kozjak | PINT | 11 | 14 | 8 |  | 6 | 9 | 3 | 5 | 10 | 0 | -49 | -29 | -75 | 7 | 1 | 6 | 10 | 0 | 1 | 1 | 78 | 160 | 7 |  | -15 | -6 | -1 | 0 | 0 | -2 | 28 | 2 | 388 | 388 | 388 | 6 | 6 | 6
1035st | Ptolemaida Battery Energy Storage System | PINT | 5 | 6 | 1 |  | 1 | 3 | 1 | 3 | 4 | 2 | -13 | -5 | -25 | -1 | 0 | 2 | 3 | 0 | 0 | 0 | 40 | 62 | 24 |  | -6 | -1 | -13 | 0 | -1 | 0 | -7 | 0 | 166 | 166 | 166 | 2 | 2 | 2
1038st | CAES Zuidwending Extension | PINT | 25 | 32 | 18 |  | 17 | 24 | 11 | 19 | 20 | 17 | -152 | -93 | -211 | -2 | 2 | 19 | 31 | 0 | 0 | 0 | 286 | 309 | 263 |  | -69 | -16 | -24 | -1 | -2 | -6 | 13 | 0 | 167 | 167 | 167 | 5 | 5 | 5
1041st | Purifying-Pumped Hydroelectric Energy Storage "Velilla del Río Carrión" (P-PHES VELILLA) | PINT | 18 | 19 | 17 |  | 8 | 10 | 5 | 16 | 21 | 11 | -70 | -45 | -92 | 6 | 1 | 9 | 14 | 0 | 1 | 1 | 249 | 317 | 162 |  | -19 | -4 | -10 | 0 | -1 | -1 | 29 | 2 | 513 | 513 | 513 | 4 | 4 | 4
1044st | Green Hydrogen Hub CAES | PINT | 27 | 31 | 24 |  | 17 | 25 | 9 | 19 | 22 | 16 | -152 | -84 | -221 | 9 | 2 | 19 | 31 | 0 | 1 | 2 | 289 | 340 | 238 |  | -69 | -16 | -25 | -1 | -2 | -6 | 23 | 2 | 157 | 157 | 157 | 2 | 2 | 2
1046st | Online Grid Controller “PSKW-Rio” | PINT | 31 | 38 | 27 |  | 14 | 21 | 11 | 18 | 21 | 16 | -127 | -97 | -186 | 36 | 2 | 16 | 26 | 0 | 5 | 7 | 281 | 324 | 241 |  | -49 | -12 | -15 | -1 | -1 | -4 | 12 | 8 | 368 | 368 | 368 | 5 | 5 | 5
1048st | WSK PULS (PHES) | PINT | 38 | 39 | 36 |  | 18 | 21 | 14 | 27 | 30 | 23 | -160 | -126 | -187 | 62 | 2 | 20 | 32 | 1 | 8 | 13 | 415 | 461 | 344 |  | -55 | -11 | -25 | -1 | -2 | -4 | 238 | 18 | 490 | 490 | 490 | 6 | 6 | 6
1050st | SE Integrator | PINT | 19 | 27 | 13 |  | 11 | 17 | 7 | 7 | 13 | 3 | -94 | -58 | -149 | -1 | 1 | 12 | 19 | 0 | 0 | 0 | 112 | 201 | 51 |  | -37 | -11 | -4 | 0 | 0 | -4 | -1 | 0 | 441 | 441 | 441 | 7 | 7 | 7
1052st | Purifying -Pumped Hydroelectric Energy Storage Buseiro (P-PHES BUSEIRO) | PINT | 20 | 21 | 18 |  | 10 | 13 | 6 | 18 | 22 | 14 | -85 | -52 | -119 | 4 | 1 | 11 | 17 | 0 | 0 | 1 | 274 | 335 | 216 |  | -37 | -4 | -27 | -1 | -2 | -2 | 25 | 1 | 528 | 528 | 528 | 4 | 4 | 4
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 92 | 103 | 83 |  | 40 | 44 | 36 | 97 | 101 | 92 | -356 | -314 | -391 | 32 | 4 | 44 | 72 | 0 | 4 | 6 | 1492 | 1541 | 1410 |  | -71 | -17 | -22 | -1 | -2 | -6 | 250 | 9 | 1181 | 1181 | 1181 | 9 | 9 | 9
1064st | CHR IRENE | PINT | 50 | 51 | 48 |  | 24 | 29 | 18 | 50 | 52 | 48 | -216 | -156 | -258 | 13 | 3 | 27 | 43 | 0 | 2 | 3 | 763 | 792 | 730 |  | -47 | -12 | -15 | -1 | -1 | -4 | 87 | 3 | 842 | 842 | 842 | 6 | 6 | 6
1066st | Kemijoki PSP | PINT | 17 | 19 | 16 |  | 5 | 8 | 3 | 20 | 22 | 18 | -45 | -28 | -72 | 0 | 1 | 6 | 9 | 0 | 0 | 0 | 311 | 334 | 278 |  | -42 | -2 | -33 | -1 | -2 | -1 | 68 | 2 | 489 | 489 | 489 | 6 | 6 | 6
1067st | PSP CONSO II | PINT | 164 | 169 | 160 |  | 96 | 100 | 93 | 183 | 203 | 169 | -845 | -824 | -878 | 110 | 11 | 105 | 170 | 1 | 14 | 22 | 2814 | 3087 | 2583 |  | -153 | -46 | -13 | -2 | -2 | -16 | 431 | 26 | 1519 | 1519 | 1519 | 12 | 12 | 12
1068st | Hydro-pumped electricity storage GIRONÉS & RAÏMATS | PINT | 296 | 306 | 285 |  | 138 | 164 | 103 | 319 | 324 | 314 | -1216 | -906 | -1448 | 78 | 15 | 152 | 245 | 1 | 10 | 16 | 4904 | 5034 | 4802 |  | -243 | -71 | -27 | -3 | -3 | -25 | 1663 | 41 | 1896 | 1896 | 1896 | 17 | 17 | 17
1070st | Hydro-Pumped Electricity Storage in Estonia Mine | PINT | 13 | 15 | 11 |  | 7 | 9 | 3 | 10 | 14 | 8 | -61 | -28 | -83 | 0 | 1 | 8 | 12 | 0 | 0 | 0 | 151 | 214 | 120 |  | -40 | -4 | -25 | -1 | -1 | -2 | -5 | 0 | 259 | 259 | 259 | 3 | 3 | 3
1071st | Villarosa | PINT | 21 | 27 | 17 |  | 10 | 16 | 7 | 7 | 9 | 5 | -88 | -58 | -140 | 43 | 1 | 11 | 18 | 1 | 5 | 9 | 113 | 140 | 72 |  | -43 | -9 | -18 | -1 | -1 | -3 | 137 | 11 | 396 | 396 | 396 | 7 | 7 | 7
1072st | HPS VROCHONERA | PINT | 6 | 9 | 5 |  | 4 | 6 | 1 | 2 | 7 | -4 | -32 | -9 | -56 | 0 | 0 | 4 | 7 | 0 | 0 | 0 | 31 | 107 | -54 |  | -6 | -2 | -4 | 0 | 0 | -1 | -2 | 0 | 367 | 367 | 367 | 4 | 4 | 4
1073st | Taccu Sa Pruna | PINT | 21 | 28 | 15 |  | 11 | 17 | 8 | 10 | 12 | 9 | -100 | -69 | -152 | 48 | 1 | 12 | 20 | 1 | 6 | 10 | 162 | 183 | 135 |  | -37 | -12 | -4 | 0 | 0 | -4 | 202 | 13 | 293 | 293 | 293 | 5 | 5 | 5
1074st | Construction of pumped-storage hydropower plant “Batak”, which utilizes the pre-existing dams of the “Batashki hydroelectric cascade” - (PSHPP “Batak”) | PINT | 21 | 23 | 18 |  | 11 | 14 | 8 | 7 | 14 | 1 | -101 | -69 | -122 | 5 | 1 | 13 | 20 | 0 | 1 | 1 | 116 | 214 | 18 |  | -34 | -9 | -12 | -1 | -1 | -3 | 18 | 1 | 393 | 393 | 393 | 7 | 7 | 7
1075st | Construction of pumped-storage hydropower plant “Dospat” - (PSHPP "Dospat") | PINT | 40 | 44 | 38 |  | 19 | 24 | 16 | 12 | 26 | -1 | -165 | -139 | -208 | 11 | 2 | 21 | 33 | 0 | 1 | 2 | 186 | 406 | -8 |  | -62 | -18 | -11 | -1 | -1 | -6 | 34 | 3 | 394 | 394 | 394 | 7 | 7 | 7
1076st | Favazzina | PINT | 19 | 23 | 17 |  | 11 | 14 | 8 | 13 | 17 | 11 | -95 | -67 | -128 | 40 | 1 | 12 | 19 | 0 | 5 | 8 | 204 | 269 | 170 |  | -32 | -8 | -13 | -1 | -1 | -3 | 138 | 10 | 269 | 269 | 269 | 5 | 5 | 5
1077st | Serra Del Corvo | PINT | 26 | 33 | 21 |  | 14 | 19 | 10 | 12 | 13 | 11 | -126 | -86 | -171 | 43 | 2 | 16 | 25 | 1 | 5 | 9 | 186 | 198 | 173 |  | -47 | -11 | -20 | -1 | -1 | -4 | 144 | 11 | 314 | 314 | 314 | 6 | 6 | 6
1078st | HPS LADONAS | PINT | 6 | 10 | 4 |  | 4 | 8 | 1 | 5 | 11 | 1 | -38 | -1 | -66 | -2 | 0 | 5 | 8 | 0 | 0 | 0 | 82 | 164 | 9 |  | -23 | -3 | -17 | -1 | -1 | -1 | -3 | 0 | 149 | 149 | 149 | 2 | 2 | 2
1081st | CAES Ahaus, Germany | PINT | 28 | 31 | 25 |  | 18 | 27 | 10 | 16 | 16 | 16 | -161 | -87 | -235 | 31 | 2 | 20 | 32 | 0 | 4 | 6 | 244 | 246 | 242 |  | -63 | -18 | -10 | -1 | -1 | -6 | -67 | 5 | 148 | 148 | 148 | 2 | 2 | 2

## 2040NT
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1001st | Kaunertal Extension Project | PINT | 60 | 65 | 51 |  | 1 | 6 | -4 | 16 | 18 | 13 | -9 | 27 | -42 | 8 | 2 | 4 | 5 | 1 | 4 | 4 | 241 | 277 | 206 |  | -35 | -2 | -23 | -1 | -1 | -1 | 20 | 4 | 1391 | 1391 | 1391 | 14 | 14 | 14
1003st | Hydro-pumped storage in Bulgaria - Yadenitsa | PINT | 48 | 52 | 44 |  | 32 | 33 | 31 | 16 | 17 | 14 | -219 | -210 | -228 | 0 | 42 | 105 | 113 | 0 | 0 | 0 | 244 | 271 | 217 |  | -111 | -37 | 0 | -1 | -1 | -13 | -114 | -5 | 909 | 909 | 909 | 11 | 11 | 11
1004st | Estonian PHES (pumped-hydro energy storage) | PINT | 25 | 33 | 20 |  | 3 | 6 | 0 | 31 | 47 | 15 | -22 | 1 | -43 | 0 | 4 | 11 | 12 | 0 | 0 | 0 | 484 | 741 | 245 |  | -84 | -3 | -49 | -2 | -3 | -2 | 105 | 2 | 239 | 239 | 239 | 3 | 3 | 3
1006st | HPS AMFILOCHIA | PINT | 23 | 32 | 12 |  | 10 | 14 | 6 | 8 | 17 | -4 | -71 | -42 | -97 | -1 | 14 | 34 | 37 | 0 | 0 | 0 | 232 | 257 | 206 |  | -16 | -5 | 0 | 0 | 0 | -2 | -42 | -1 | 561 | 561 | 561 | 6 | 6 | 6
1012st | Purifying -Pumped Hydroelectric Energy Storage Navaleo (P-PHES Navaleo) | TOOT | 54 | 60 | 48 |  | 15 | 19 | 13 | 90 | 92 | 85 | -104 | -90 | -130 | 5 | 20 | 50 | 54 | 1 | 2 | 3 | 1393 | 1452 | 1301 |  | -21 | -5 | -4 | 0 | 0 | -2 | 280 | 7 | 722 | 722 | 722 | 5 | 5 | 5
1013st | CAES Zuidwending, NL | PINT | 25 | 31 | 19 |  | -7 | -4 | -9 | 3 | 13 | -6 | 44 | 61 | 27 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 195 | -104 |  | -43 | -4 | -24 | -1 | -1 | -2 | -81 | 0 | 208 | 208 | 208 | 12 | 12 | 12
1025st | Silvermines Hydroelectric Power Station | PINT | 7 | 10 | 5 |  | 0 | 3 | -1 | 19 | 33 | 3 | -1 | 8 | -18 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 295 | 527 | 46 |  | -11 | -1 | -10 | 0 | 0 | 0 | 35 | 0 | 310 | 310 | 310 | 5 | 5 | 5
1026st | Hydro pumped storage Riedl | PINT | 11 | 11 | 11 |  | -2 | 5 | -10 | 16 | 29 | 7 | 11 | 66 | -31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 456 | 109 |  | -18 | -2 | -10 | 0 | -1 | -1 | -17 | 0 | 1039 | 1039 | 1039 | 13 | 13 | 13
1027st | Purifying -Pumped Hydroelectric Energy Storage CUA (P-PHES CUA) | PINT | 24 | 34 | 13 |  | 6 | 9 | 3 | 55 | 59 | 52 | -40 | -19 | -63 | 2 | 8 | 19 | 20 | 0 | 1 | 1 | 871 | 916 | 826 |  | -16 | -4 | -3 | 0 | 0 | -1 | 176 | 4 | 1164 | 1164 | 1164 | 8 | 8 | 8
1029st | PSPP Kozjak | PINT | 19 | 22 | 17 |  | 11 | 15 | 8 | 8 | 12 | 4 | -77 | -53 | -100 | 1 | 15 | 37 | 40 | 0 | 0 | 1 | 129 | 188 | 70 |  | -22 | -10 | -5 | 0 | 0 | -3 | 43 | 1 | 478 | 478 | 478 | 6 | 6 | 6
1035st | Ptolemaida Battery Energy Storage System | PINT | 6 | 13 | 2 |  | 0 | 4 | -3 | -5 | 6 | -14 | 2 | 17 | -29 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -73 | 95 | -210 |  | 0 | -2 | -5 | 0 | 0 | -1 | -5 | 1 | 258 | 258 | 258 | 3 | 3 | 3
1038st | CAES Zuidwending Extension | PINT | 28 | 31 | 25 |  | -2 | 5 | -9 | 13 | 13 | 13 | 13 | 61 | -36 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 200 | 206 | 195 |  | -42 | -3 | -24 | -1 | -1 | -1 | -81 | 0 | 206 | 206 | 206 | 11 | 11 | 11
1041st | Purifying-Pumped Hydroelectric Energy Storage "Velilla del Río Carrión" (P-PHES VELILLA) | PINT | 9 | 13 | 5 |  | 0 | 1 | 0 | 14 | 23 | 7 | -3 | 1 | -5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 220 | 364 | 104 |  | -11 | 0 | -8 | 0 | 0 | 0 | 63 | 1 | 752 | 752 | 752 | 6 | 6 | 6
1044st | Green Hydrogen Hub CAES | PINT | 27 | 31 | 23 |  | -1 | 5 | -7 | 22 | 25 | 19 | 4 | 45 | -37 | 3 | 0 | 0 | 0 | 1 | 2 | 2 | 343 | 403 | 283 |  | -38 | -1 | -27 | -1 | -1 | -1 | -182 | 0 | 250 | 250 | 250 | 4 | 4 | 4
1046st | Online Grid Controller “PSKW-Rio” | PINT | 20 | 29 | 11 |  | -1 | 0 | -3 | 16 | 19 | 13 | 8 | 22 | -2 | 13 | 0 | 0 | 0 | 3 | 6 | 7 | 108 | 293 | -169 |  | -13 | 0 | -12 | 0 | -1 | 0 | 247 | 10 | 1039 | 1039 | 1039 | 13 | 13 | 13
1048st | WSK PULS (PHES) | PINT | 15 | 21 | 10 |  | -2 | 1 | -4 | 15 | 17 | 14 | 14 | 27 | -4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 253 | 222 |  | -7 | -1 | -6 | 0 | 0 | 0 | 3 | 0 | 1389 | 1389 | 1389 | 17 | 17 | 17
1050st | SE Integrator | PINT | 24 | 32 | 20 |  | 11 | 14 | 9 | 6 | 19 | -10 | -73 | -61 | -95 | -1 | 14 | 35 | 38 | 0 | -1 | -1 | 84 | 291 | -165 |  | -28 | -10 | -2 | 0 | 0 | -4 | 22 | 2 | 895 | 895 | 895 | 9 | 9 | 9
1052st | Purifying -Pumped Hydroelectric Energy Storage Buseiro (P-PHES BUSEIRO) | PINT | 6 | 9 | 3 |  | -1 | 1 | -5 | 11 | 21 | 3 | 9 | 31 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 324 | 49 |  | -2 | 0 | 0 | 0 | 0 | 0 | 100 | 1 | 781 | 781 | 781 | 6 | 6 | 6
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 58 | 60 | 55 |  | 8 | 12 | 4 | 124 | 124 | 123 | -56 | -29 | -84 | 6 | 11 | 27 | 29 | 1 | 3 | 3 | 1932 | 1934 | 1930 |  | -35 | -5 | -13 | -1 | -1 | -2 | 630 | 9 | 2021 | 2021 | 2021 | 15 | 15 | 15
1064st | CHR IRENE | PINT | 46 | 49 | 43 |  | 10 | 11 | 9 | 70 | 70 | 70 | -66 | -60 | -72 | 1 | 13 | 32 | 34 | 0 | 0 | 0 | 1098 | 1101 | 1095 |  | -16 | -4 | -4 | 0 | 0 | -1 | 267 | 3 | 1336 | 1336 | 1336 | 10 | 10 | 10
1066st | Kemijoki PSP | PINT | 14 | 23 | 8 |  | -1 | 1 | -3 | 22 | 24 | 19 | 7 | 19 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 380 | 303 |  | -5 | -1 | 0 | 0 | 0 | -1 | 47 | 2 | 644 | 644 | 644 | 7 | 7 | 7
1067st | PSP CONSO II | PINT | 201 | 203 | 199 |  | 51 | 52 | 50 | 307 | 310 | 304 | -348 | -343 | -353 | 15 | 67 | 167 | 179 | 3 | 7 | 8 | 4807 | 4838 | 4776 |  | -83 | -19 | -18 | -1 | -1 | -7 | 1200 | 30 | 2634 | 2634 | 2634 | 21 | 21 | 21
1068st | Hydro-pumped electricity storage GIRONÉS & RAÏMATS | PINT | 333 | 367 | 296 |  | 81 | 90 | 76 | 527 | 534 | 520 | -548 | -515 | -614 | -5 | 105 | 264 | 282 | -1 | -2 | -3 | 8120 | 8128 | 8111 |  | -112 | -28 | -20 | -1 | -2 | -10 | 2779 | 1 | 3251 | 3251 | 3251 | 27 | 27 | 27
1070st | Hydro-Pumped Electricity Storage in Estonia Mine | PINT | 7 | 9 | 4 |  | -2 | 1 | -6 | 8 | 16 | -4 | 11 | 42 | -9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 245 | -59 |  | -25 | -1 | -15 | -1 | -1 | 0 | 40 | 1 | 224 | 224 | 224 | 3 | 3 | 3
1071st | Villarosa | PINT | 15 | 20 | 11 |  | 0 | 5 | -7 | 13 | 14 | 12 | -2 | 45 | -37 | -1 | 0 | 1 | 1 | 0 | 0 | 0 | 206 | 223 | 189 |  | -6 | -5 | -6 | 0 | 0 | -2 | 8 | 1 | 375 | 375 | 375 | 5 | 5 | 5
1072st | HPS VROCHONERA | PINT | 17 | 20 | 14 |  | 8 | 10 | 6 | 1 | 2 | 1 | -51 | -43 | -68 | 0 | 10 | 25 | 26 | 0 | 0 | 0 | 24 | 24 | 23 |  | -29 | -9 | -1 | 0 | 0 | -3 | 61 | 0 | 582 | 582 | 582 | 7 | 7 | 7
1073st | Taccu Sa Pruna | PINT | 11 | 11 | 10 |  | 5 | 10 | 2 | 17 | 32 | 3 | -31 | -11 | -66 | -1 | 6 | 15 | 16 | 0 | -1 | -1 | 270 | 502 | 51 |  | -25 | -8 | 0 | 0 | 0 | -3 | 16 | 1 | 410 | 410 | 410 | 6 | 6 | 6
1074st | Construction of pumped-storage hydropower plant “Batak”, which utilizes the pre-existing dams of the “Batashki hydroelectric cascade” - (PSHPP “Batak”) | PINT | 50 | 59 | 44 |  | 22 | 23 | 22 | 13 | 16 | 10 | -153 | -149 | -158 | 85 | 29 | 74 | 79 | 16 | 41 | 44 | 210 | 250 | 155 |  | -64 | -22 | -1 | 0 | 0 | -8 | -169 | 47 | 900 | 900 | 900 | 11 | 11 | 11
1075st | Construction of pumped-storage hydropower plant “Dospat” - (PSHPP "Dospat") | PINT | 69 | 79 | 57 |  | 29 | 31 | 27 | 11 | 24 | -6 | -199 | -184 | -211 | 0 | 38 | 96 | 102 | 0 | 0 | 0 | 175 | 383 | -83 |  | -93 | -29 | -4 | -1 | -1 | -10 | -7 | -1 | 887 | 887 | 887 | 11 | 11 | 11
1076st | Favazzina | PINT | 15 | 18 | 12 |  | 6 | 8 | 3 | 13 | 14 | 13 | -38 | -23 | -53 | 0 | 7 | 18 | 20 | 0 | 0 | 0 | 212 | 228 | 196 |  | -6 | -5 | -5 | 0 | 0 | -2 | 1 | 1 | 378 | 378 | 378 | 6 | 6 | 6
1077st | Serra Del Corvo | PINT | 15 | 20 | 11 |  | 5 | 7 | 2 | 9 | 12 | 7 | -36 | -15 | -50 | 0 | 7 | 17 | 18 | 0 | 0 | 0 | 147 | 190 | 115 |  | -30 | -9 | -2 | 0 | 0 | -3 | 27 | 1 | 446 | 446 | 446 | 7 | 7 | 7
1078st | HPS LADONAS | PINT | 7 | 9 | 4 |  | 2 | 3 | 1 | 2 | 7 | -1 | -14 | -10 | -20 | 0 | 3 | 7 | 7 | 0 | 0 | 0 | 35 | 102 | 0 |  | -7 | -3 | -2 | 0 | 0 | -1 | 3 | 0 | 234 | 234 | 234 | 3 | 3 | 3
1081st | CAES Ahaus, Germany | PINT | 43 | 44 | 42 |  | -1 | 7 | -10 | 12 | 14 | 9 | 7 | 65 | -51 | 17 | 0 | 0 | 0 | 3 | 8 | 9 | 180 | 218 | 143 |  | -55 | -5 | -32 | -1 | -2 | -2 | 198 | 11 | 411 | 411 | 411 | 5 | 5 | 5

## 2040DE
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1001st | Kaunertal Extension Project | PINT | 78 | 87 | 67 |  | 12 | 15 | 7 | 51 | 64 | 41 | -80 | -49 | -105 | 6 | 15 | 39 | 41 | 1 | 3 | 3 | 722 | 917 | 582 |  | -35 | -4 | -24 | -1 | -1 | -1 | 20 | 4 | 665 | 665 | 665 | 8 | 8 | 8
1003st | Hydro-pumped storage in Bulgaria - Yadenitsa | PINT | 83 | 104 | 63 |  | 31 | 34 | 30 | 21 | 26 | 12 | -212 | -201 | -229 | -7 | 41 | 102 | 109 | -1 | -3 | -3 | 301 | 366 | 173 |  | -100 | -29 | -33 | -1 | -2 | -10 | -114 | -6 | 534 | 534 | 534 | 5 | 5 | 5
1004st | Estonian PHES (pumped-hydro energy storage) | PINT | 38 | 46 | 31 |  | 8 | 11 | 6 | 33 | 39 | 28 | -52 | -39 | -77 | 1 | 10 | 25 | 27 | 0 | 0 | 0 | 469 | 544 | 397 |  | -57 | -2 | -37 | -1 | -2 | -1 | 105 | 4 | 723 | 723 | 723 | 10 | 10 | 10
1006st | HPS AMFILOCHIA | PINT | 34 | 56 | 6 |  | 14 | 30 | 0 | 29 | 31 | 26 | -95 | 0 | -204 | -2 | 18 | 46 | 49 | 0 | -1 | -1 | 406 | 443 | 369 |  | -10 | -3 | -1 | 0 | 0 | -1 | -42 | -2 | 1148 | 1148 | 1148 | 11 | 11 | 11
1012st | Purifying -Pumped Hydroelectric Energy Storage Navaleo (P-PHES Navaleo) | TOOT | 76 | 79 | 73 |  | 18 | 19 | 16 | 76 | 77 | 76 | -122 | -111 | -132 | 9 | 23 | 59 | 63 | 2 | 4 | 5 | 1085 | 1095 | 1066 |  | -35 | -6 | -12 | -1 | -1 | -2 | 280 | 13 | 689 | 689 | 689 | 6 | 6 | 6
1013st | CAES Zuidwending, NL | PINT | 39 | 49 | 29 |  | -1 | 2 | -5 | 18 | 28 | 8 | 10 | 35 | -15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 401 | 115 |  | -16 | 0 | -13 | 0 | -1 | 0 | -81 | -1 | 291 | 291 | 291 | 19 | 19 | 19
1025st | Silvermines Hydroelectric Power Station | PINT | 13 | 24 | 2 |  | 1 | 3 | 0 | 19 | 21 | 18 | -10 | -3 | -17 | 1 | 2 | 5 | 5 | 0 | 0 | 0 | 271 | 294 | 249 |  | -1 | 0 | 1 | 0 | 0 | 0 | 35 | 1 | 927 | 927 | 927 | 9 | 9 | 9
1026st | Hydro pumped storage Riedl | PINT | 31 | 35 | 25 |  | 4 | 5 | 2 | 22 | 26 | 18 | -27 | -17 | -35 | 1 | 5 | 13 | 14 | 0 | 0 | 0 | 318 | 375 | 262 |  | 5 | 0 | 4 | 0 | 0 | 0 | -17 | 0 | 1002 | 1002 | 1002 | 12 | 12 | 12
1027st | Purifying -Pumped Hydroelectric Energy Storage CUA (P-PHES CUA) | PINT | 53 | 61 | 45 |  | 14 | 16 | 13 | 51 | 56 | 46 | -95 | -86 | -106 | 5 | 18 | 45 | 49 | 1 | 2 | 3 | 723 | 788 | 653 |  | -12 | -1 | -11 | 0 | -1 | 0 | 176 | 9 | 705 | 705 | 705 | 6 | 6 | 6
1029st | PSPP Kozjak | PINT | 29 | 32 | 24 |  | 9 | 11 | 7 | 15 | 20 | 9 | -62 | -50 | -73 | 1 | 12 | 30 | 32 | 0 | 1 | 1 | 210 | 288 | 129 |  | -33 | -6 | -29 | -1 | -1 | -2 | 43 | 2 | 380 | 380 | 380 | 4 | 4 | 4
1035st | Ptolemaida Battery Energy Storage System | PINT | 5 | 7 | 2 |  | 3 | 5 | 0 | 0 | 1 | -1 | -17 | 1 | -35 | 1 | 3 | 8 | 9 | 0 | 0 | 0 | 1 | 10 | -11 |  | 0 | 1 | -5 | 0 | 0 | 0 | -5 | 0 | 449 | 449 | 449 | 4 | 4 | 4
1038st | CAES Zuidwending Extension | PINT | 37 | 49 | 25 |  | -1 | 3 | -5 | 17 | 28 | 6 | 7 | 35 | -21 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 243 | 401 | 86 |  | -18 | -2 | -12 | 0 | -1 | -1 | -81 | -1 | 290 | 290 | 290 | 19 | 19 | 19
1041st | Purifying-Pumped Hydroelectric Energy Storage "Velilla del Río Carrión" (P-PHES VELILLA) | PINT | 22 | 30 | 14 |  | 5 | 7 | 4 | 18 | 23 | 12 | -36 | -28 | -47 | 2 | 7 | 17 | 18 | 0 | 1 | 1 | 256 | 329 | 175 |  | -6 | 0 | -7 | 0 | 0 | 0 | 63 | 2 | 519 | 519 | 519 | 4 | 4 | 4
1044st | Green Hydrogen Hub CAES | PINT | 36 | 38 | 34 |  | 6 | 12 | -1 | 33 | 34 | 32 | -38 | 4 | -81 | 34 | 7 | 18 | 19 | 7 | 17 | 18 | 471 | 485 | 456 |  | -26 | -3 | -14 | -1 | -1 | -1 | -182 | 3 | 186 | 186 | 186 | 5 | 5 | 5
1046st | Online Grid Controller “PSKW-Rio” | PINT | 29 | 31 | 25 |  | 4 | 6 | 2 | 20 | 22 | 17 | -30 | -15 | -40 | -4 | 6 | 14 | 15 | -1 | -2 | -2 | 287 | 313 | 239 |  | 1 | -1 | -1 | 0 | 0 | 0 | 247 | 17 | 1004 | 1004 | 1004 | 12 | 12 | 12
1048st | WSK PULS (PHES) | PINT | 26 | 27 | 25 |  | 5 | 6 | 3 | 24 | 26 | 23 | -31 | -22 | -41 | 0 | 6 | 15 | 16 | 0 | 0 | 0 | 347 | 358 | 337 |  | 4 | 0 | 4 | 0 | 0 | 0 | 3 | 0 | 1339 | 1339 | 1339 | 16 | 16 | 16
1050st | SE Integrator | PINT | 36 | 53 | 23 |  | 15 | 16 | 14 | 7 | 13 | 3 | -102 | -92 | -112 | 3 | 20 | 49 | 52 | 1 | 1 | 2 | 94 | 181 | 49 |  | -56 | -14 | -15 | -1 | -1 | -5 | 22 | 2 | 1104 | 1104 | 1104 | 7 | 7 | 7
1052st | Purifying -Pumped Hydroelectric Energy Storage Buseiro (P-PHES BUSEIRO) | PINT | 22 | 28 | 15 |  | 5 | 6 | 4 | 20 | 24 | 16 | -34 | -24 | -42 | 2 | 7 | 17 | 18 | 0 | 1 | 1 | 291 | 346 | 232 |  | 4 | 0 | 0 | 0 | 0 | 0 | 100 | 3 | 536 | 536 | 536 | 5 | 5 | 5
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 123 | 126 | 120 |  | 30 | 32 | 28 | 120 | 120 | 119 | -205 | -191 | -219 | 12 | 39 | 99 | 106 | 2 | 6 | 6 | 1696 | 1705 | 1687 |  | -27 | -4 | -15 | -1 | -1 | -1 | 630 | 23 | 858 | 858 | 858 | 8 | 8 | 8
1064st | CHR IRENE | PINT | 70 | 72 | 68 |  | 18 | 20 | 16 | 65 | 66 | 64 | -123 | -110 | -139 | 3 | 24 | 59 | 64 | 1 | 1 | 1 | 923 | 929 | 913 |  | -13 | -3 | -7 | 0 | 0 | -1 | 267 | 7 | 745 | 745 | 745 | 6 | 6 | 6
1066st | Kemijoki PSP | PINT | 36 | 49 | 24 |  | 6 | 9 | 3 | 32 | 42 | 21 | -43 | -23 | -63 | 1 | 8 | 21 | 22 | 0 | 0 | 0 | 457 | 595 | 308 |  | -41 | 0 | -28 | -1 | -2 | -1 | 47 | 2 | 800 | 800 | 800 | 6 | 6 | 6
1067st | PSP CONSO II | PINT | 266 | 276 | 256 |  | 66 | 73 | 58 | 240 | 242 | 238 | -446 | -394 | -498 | 38 | 86 | 215 | 230 | 7 | 18 | 19 | 3401 | 3462 | 3340 |  | -71 | -18 | -15 | -1 | -1 | -6 | 1200 | 61 | 884 | 884 | 884 | 8 | 8 | 8
1068st | Hydro-pumped electricity storage GIRONÉS & RAÏMATS | PINT | 471 | 482 | 460 |  | 105 | 108 | 102 | 450 | 452 | 448 | -716 | -696 | -737 | -5 | 137 | 344 | 369 | -1 | -2 | -2 | 6444 | 6462 | 6426 |  | -193 | -35 | -73 | -3 | -5 | -13 | 2779 | 44 | 874 | 874 | 874 | 8 | 8 | 8
1070st | Hydro-Pumped Electricity Storage in Estonia Mine | PINT | 15 | 28 | 5 |  | 4 | 4 | 3 | 13 | 23 | 8 | -26 | -22 | -30 | 0 | 5 | 12 | 13 | 0 | 0 | 0 | 193 | 331 | 121 |  | -5 | 0 | -2 | 0 | 0 | 0 | 40 | 2 | 580 | 580 | 580 | 8 | 8 | 8
1071st | Villarosa | PINT | 20 | 34 | 10 |  | 6 | 7 | 5 | 13 | 19 | 10 | -38 | -32 | -47 | 1 | 7 | 18 | 20 | 0 | 1 | 1 | 191 | 278 | 142 |  | -8 | -1 | -5 | 0 | 0 | 0 | 8 | 0 | 376 | 376 | 376 | 7 | 7 | 7
1072st | HPS VROCHONERA | PINT | 38 | 42 | 35 |  | 11 | 13 | 9 | 28 | 32 | 26 | -76 | -61 | -85 | 2 | 15 | 37 | 39 | 0 | 1 | 1 | 401 | 461 | 369 |  | -6 | -5 | 10 | 0 | 1 | -2 | 61 | 0 | 1199 | 1199 | 1199 | 12 | 12 | 12
1073st | Taccu Sa Pruna | PINT | 23 | 35 | 10 |  | 6 | 7 | 6 | 26 | 34 | 16 | -42 | -38 | -50 | 1 | 8 | 20 | 22 | 0 | 0 | 0 | 369 | 486 | 233 |  | -8 | -3 | 3 | 0 | 0 | -1 | 16 | 1 | 384 | 384 | 384 | 2 | 2 | 2
1074st | Construction of pumped-storage hydropower plant “Batak”, which utilizes the pre-existing dams of the “Batashki hydroelectric cascade” - (PSHPP “Batak”) | PINT | 58 | 63 | 51 |  | 24 | 28 | 15 | 16 | 24 | 10 | -160 | -100 | -192 | 159 | 31 | 77 | 82 | 30 | 76 | 82 | 235 | 341 | 138 |  | -100 | -28 | -30 | -1 | -2 | -10 | -169 | 95 | 539 | 539 | 539 | 5 | 5 | 5
1075st | Construction of pumped-storage hydropower plant “Dospat” - (PSHPP "Dospat") | PINT | 70 | 78 | 61 |  | 33 | 35 | 31 | 24 | 30 | 18 | -225 | -212 | -239 | -2 | 43 | 108 | 116 | 0 | -1 | -1 | 338 | 428 | 246 |  | -113 | -33 | -30 | -2 | -2 | -11 | -7 | -1 | 525 | 525 | 525 | 5 | 5 | 5
1076st | Favazzina | PINT | 10 | 12 | 9 |  | 6 | 7 | 5 | 10 | 11 | 10 | -39 | -31 | -48 | 1 | 8 | 19 | 20 | 0 | 0 | 0 | 147 | 154 | 141 |  | -7 | -2 | -4 | 0 | 0 | -1 | 1 | 0 | 350 | 350 | 350 | 2 | 2 | 2
1077st | Serra Del Corvo | PINT | 27 | 39 | 18 |  | 9 | 10 | 6 | 21 | 27 | 16 | -58 | -42 | -66 | 2 | 11 | 28 | 30 | 0 | 1 | 1 | 297 | 384 | 228 |  | -17 | -4 | -7 | 0 | 0 | -1 | 27 | 1 | 414 | 414 | 414 | 2 | 2 | 2
1078st | HPS LADONAS | PINT | 13 | 22 | 6 |  | 4 | 6 | 3 | 8 | 10 | 6 | -30 | -21 | -40 | 3 | 6 | 14 | 15 | 1 | 1 | 1 | 116 | 143 | 94 |  | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 402 | 402 | 402 | 4 | 4 | 4
1081st | CAES Ahaus, Germany | PINT | 44 | 55 | 33 |  | -3 | 0 | -5 | 15 | 23 | 7 | 18 | 35 | 1 | -6 | 0 | 0 | 0 | -1 | -3 | -3 | 209 | 328 | 91 |  | -7 | -1 | -2 | 0 | 0 | 0 | 198 | 18 | 401 | 401 | 401 | 5 | 5 | 5

## 2030NT-ENTSO-E
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1001st | Kaunertal Extension Project | PINT | 52 | 61 | 39 |  | 23 | 26 | 17 | 14 | 15 | 13 | -201 | -154 | -232 | 2 | 3 | 25 | 40 | 0 | 0 | 0 | 217 | 230 | 204 |  | -78 | -21 | -21 | -1 | -1 | -7 | 3 | 0 | 391 | 391 | 391 | 7 | 7 | 7
1003st | Hydro-pumped storage in Bulgaria - Yadenitsa | PINT | 10 | 12 | 9 |  | 2 | 2 | 1 | -1 | 2 | -4 | -13 | -6 | -20 | -122 | 0 | 2 | 3 | -2 | -15 | -25 | -12 | 30 | -54 |  | -6 | -1 | -4 | 0 | 0 | 0 | -131 | -46 | 392 | 392 | 392 | 7 | 7 | 7
1004st | Estonian PHES (pumped-hydro energy storage) | PINT | 16 | 19 | 14 |  | 7 | 10 | 4 | 15 | 17 | 14 | -64 | -33 | -88 | 1 | 1 | 8 | 13 | 0 | 0 | 0 | 231 | 261 | 210 |  | -170 | -7 | -102 | -4 | -6 | -4 | 12 | 0 | 331 | 331 | 331 | 3 | 3 | 3
1006st | HPS AMFILOCHIA | PINT | 3 | 5 | 0 |  | 1 | 2 | 1 | 0 | 3 | -3 | -11 | -6 | -14 | -68 | 0 | 1 | 2 | -1 | -8 | -14 | 3 | 43 | -39 |  | -5 | -1 | 0 | 0 | 0 | 0 | -70 | -24 | 264 | 264 | 264 | 3 | 3 | 3
1012st | Purifying -Pumped Hydroelectric Energy Storage Navaleo (P-PHES Navaleo) | TOOT | 51 | 59 | 44 |  | 19 | 20 | 16 | 54 | 56 | 53 | -166 | -140 | -180 | 28 | 2 | 21 | 33 | 0 | 4 | 6 | 833 | 858 | 816 |  | -41 | -11 | -6 | 0 | -1 | -4 | 81 | 6 | 520 | 520 | 520 | 4 | 4 | 4
1013st | CAES Zuidwending, NL | PINT | 34 | 57 | 11 |  | 13 | 18 | 8 | 16 | 17 | 15 | -116 | -71 | -161 | -2 | 1 | 14 | 23 | 0 | 0 | 0 | 244 | 254 | 234 |  | -56 | -15 | -15 | -1 | -1 | -5 | 13 | 0 | 168 | 168 | 168 | 5 | 5 | 5
1025st | Silvermines Hydroelectric Power Station | PINT | 14 | 18 | 11 |  | 5 | 6 | 4 | 21 | 27 | 13 | -46 | -35 | -57 | 1 | 1 | 6 | 9 | 0 | 0 | 0 | 315 | 417 | 195 |  | -19 | -6 | -4 | 0 | 0 | -2 | 33 | 0 | 152 | 152 | 152 | 2 | 2 | 2
1026st | Hydro pumped storage Riedl | PINT | 30 | 35 | 27 |  | 11 | 14 | 9 | 19 | 21 | 15 | -96 | -79 | -128 | 82 | 1 | 12 | 19 | 1 | 10 | 16 | 293 | 327 | 232 |  | -42 | -11 | -10 | -1 | -1 | -4 | 389 | 26 | 365 | 365 | 365 | 5 | 5 | 5
1027st | Purifying -Pumped Hydroelectric Energy Storage CUA (P-PHES CUA) | PINT | 35 | 41 | 28 |  | 14 | 16 | 11 | 37 | 39 | 35 | -121 | -94 | -140 | 15 | 2 | 15 | 24 | 0 | 2 | 3 | 561 | 609 | 533 |  | -29 | -7 | -12 | 0 | -1 | -3 | 61 | 4 | 716 | 716 | 716 | 5 | 5 | 5
1029st | PSPP Kozjak | PINT | 8 | 11 | 3 |  | 3 | 5 | 2 | 3 | 4 | 1 | -28 | -17 | -43 | 7 | 0 | 3 | 6 | 0 | 1 | 1 | 39 | 54 | 14 |  | -13 | -5 | -3 | 0 | 0 | -2 | 28 | 2 | 380 | 380 | 380 | 6 | 6 | 6
1035st | Ptolemaida Battery Energy Storage System | PINT | 3 | 6 | 0 |  | 1 | 1 | 0 | 1 | 2 | -1 | -5 | -1 | -9 | -1 | 0 | 1 | 1 | 0 | 0 | 0 | 11 | 27 | -16 |  | -2 | 0 | -6 | 0 | 0 | 0 | -6 | 0 | 124 | 124 | 124 | 2 | 2 | 2
1038st | CAES Zuidwending Extension | PINT | 35 | 57 | 14 |  | 14 | 19 | 8 | 17 | 17 | 17 | -119 | -71 | -167 | -2 | 2 | 15 | 24 | 0 | 0 | 0 | 258 | 261 | 254 |  | -56 | -15 | -13 | -1 | -1 | -5 | 13 | 0 | 166 | 166 | 166 | 5 | 5 | 5
1041st | Purifying-Pumped Hydroelectric Energy Storage "Velilla del Río Carrión" (P-PHES VELILLA) | PINT | 16 | 20 | 13 |  | 6 | 8 | 4 | 15 | 17 | 11 | -52 | -34 | -70 | 6 | 1 | 6 | 10 | 0 | 1 | 1 | 231 | 266 | 163 |  | -13 | -3 | -6 | 0 | 0 | -1 | 29 | 2 | 495 | 495 | 495 | 4 | 4 | 4
1044st | Green Hydrogen Hub CAES | PINT | 25 | 31 | 19 |  | 12 | 18 | 6 | 14 | 14 | 14 | -110 | -57 | -162 | 9 | 1 | 14 | 22 | 0 | 1 | 2 | 214 | 219 | 209 |  | -58 | -15 | -17 | -1 | -1 | -5 | 23 | 2 | 156 | 156 | 156 | 2 | 2 | 2
1046st | Online Grid Controller “PSKW-Rio” | PINT | 29 | 30 | 27 |  | 11 | 14 | 9 | 17 | 19 | 15 | -95 | -81 | -123 | 36 | 1 | 12 | 19 | 0 | 5 | 7 | 263 | 297 | 232 |  | -39 | -11 | -9 | 0 | -1 | -4 | 12 | 8 | 368 | 368 | 368 | 5 | 5 | 5
1048st | WSK PULS (PHES) | PINT | 36 | 40 | 29 |  | 14 | 16 | 12 | 25 | 27 | 22 | -128 | -107 | -139 | 62 | 2 | 16 | 26 | 1 | 8 | 13 | 378 | 420 | 339 |  | -44 | -11 | -13 | -1 | -1 | -4 | 238 | 18 | 490 | 490 | 490 | 6 | 6 | 6
1050st | SE Integrator | PINT | 16 | 18 | 14 |  | 8 | 10 | 6 | 4 | 5 | 3 | -70 | -53 | -91 | -1 | 1 | 9 | 14 | 0 | 0 | 0 | 63 | 79 | 49 |  | -29 | -9 | -2 | 0 | 0 | -3 | -2 | 0 | 425 | 425 | 425 | 6 | 6 | 6
1052st | Purifying -Pumped Hydroelectric Energy Storage Buseiro (P-PHES BUSEIRO) | PINT | 16 | 19 | 13 |  | 7 | 8 | 5 | 16 | 18 | 14 | -59 | -41 | -70 | 4 | 1 | 7 | 12 | 0 | 0 | 1 | 251 | 271 | 214 |  | -22 | -4 | -10 | 0 | 0 | -2 | 25 | 1 | 511 | 511 | 511 | 4 | 4 | 4
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 90 | 101 | 78 |  | 32 | 35 | 29 | 96 | 99 | 91 | -280 | -253 | -307 | 32 | 4 | 35 | 56 | 0 | 4 | 6 | 1475 | 1517 | 1394 |  | -56 | -16 | -10 | -1 | -1 | -6 | 250 | 9 | 1139 | 1139 | 1139 | 9 | 9 | 9
1064st | CHR IRENE | PINT | 47 | 49 | 43 |  | 19 | 22 | 14 | 47 | 48 | 46 | -167 | -124 | -190 | 13 | 2 | 21 | 34 | 0 | 2 | 3 | 724 | 749 | 699 |  | -35 | -12 | -3 | 0 | 0 | -4 | 87 | 3 | 811 | 811 | 811 | 6 | 6 | 6
1066st | Kemijoki PSP | PINT | 16 | 18 | 14 |  | 4 | 5 | 3 | 19 | 22 | 17 | -32 | -27 | -40 | 0 | 0 | 4 | 7 | 0 | 0 | 0 | 297 | 336 | 270 |  | -30 | -2 | -18 | -1 | -1 | -1 | 68 | 2 | 488 | 488 | 488 | 6 | 6 | 6
1067st | PSP CONSO II | PINT | 183 | 219 | 158 |  | 78 | 83 | 74 | 182 | 200 | 167 | -687 | -655 | -728 | 110 | 9 | 86 | 139 | 1 | 14 | 22 | 2795 | 3053 | 2554 |  | -128 | -39 | -11 | -1 | -1 | -14 | 431 | 26 | 1467 | 1467 | 1467 | 11 | 11 | 11
1068st | Hydro-pumped electricity storage GIRONÉS & RAÏMATS | PINT | 298 | 313 | 287 |  | 111 | 132 | 82 | 314 | 321 | 305 | -980 | -727 | -1166 | 78 | 12 | 122 | 198 | 1 | 10 | 16 | 4830 | 4995 | 4671 |  | -197 | -60 | -14 | -2 | -2 | -21 | 1663 | 41 | 1842 | 1842 | 1842 | 17 | 17 | 17
1070st | Hydro-Pumped Electricity Storage in Estonia Mine | PINT | 10 | 12 | 8 |  | 5 | 6 | 3 | 8 | 9 | 7 | -42 | -25 | -56 | 0 | 1 | 5 | 8 | 0 | 0 | 0 | 127 | 140 | 112 |  | -30 | -3 | -16 | -1 | -1 | -1 | -5 | 0 | 259 | 259 | 259 | 3 | 3 | 3
1071st | Villarosa | PINT | 19 | 20 | 17 |  | 7 | 10 | 5 | 7 | 9 | 5 | -62 | -47 | -87 | 43 | 1 | 8 | 13 | 1 | 5 | 9 | 102 | 136 | 85 |  | -28 | -9 | -4 | 0 | 0 | -3 | 137 | 11 | 363 | 363 | 363 | 7 | 7 | 7
1072st | HPS VROCHONERA | PINT | 5 | 5 | 4 |  | 2 | 3 | 0 | 0 | 2 | -3 | -14 | -4 | -22 | -1 | 0 | 2 | 3 | 0 | 0 | 0 | -4 | 28 | -49 |  | -2 | -2 | -4 | 0 | 0 | -1 | -2 | 0 | 276 | 276 | 276 | 4 | 4 | 4
1073st | Taccu Sa Pruna | PINT | 18 | 20 | 15 |  | 8 | 12 | 6 | 10 | 11 | 9 | -71 | -56 | -102 | 48 | 1 | 9 | 14 | 1 | 6 | 10 | 158 | 175 | 142 |  | -32 | -10 | -5 | 0 | 0 | -3 | 201 | 13 | 267 | 267 | 267 | 5 | 5 | 5
1074st | Construction of pumped-storage hydropower plant “Batak”, which utilizes the pre-existing dams of the “Batashki hydroelectric cascade” - (PSHPP “Batak”) | PINT | 20 | 22 | 17 |  | 8 | 10 | 6 | 6 | 13 | 1 | -73 | -52 | -90 | 5 | 1 | 9 | 15 | 0 | 1 | 1 | 89 | 200 | 15 |  | -20 | -8 | -1 | 0 | 0 | -3 | 18 | 1 | 381 | 381 | 381 | 7 | 7 | 7
1075st | Construction of pumped-storage hydropower plant “Dospat” - (PSHPP "Dospat") | PINT | 38 | 39 | 38 |  | 14 | 16 | 11 | 10 | 25 | 0 | -121 | -100 | -142 | 11 | 2 | 15 | 24 | 0 | 1 | 2 | 162 | 395 | -4 |  | -42 | -15 | -1 | 0 | 0 | -5 | 34 | 3 | 383 | 383 | 383 | 7 | 7 | 7
1076st | Favazzina | PINT | 17 | 21 | 14 |  | 8 | 10 | 7 | 10 | 11 | 8 | -71 | -60 | -86 | 39 | 1 | 9 | 14 | 0 | 5 | 8 | 153 | 168 | 125 |  | -17 | -8 | -2 | 0 | 0 | -3 | 138 | 10 | 244 | 244 | 244 | 5 | 5 | 5
1077st | Serra Del Corvo | PINT | 22 | 23 | 21 |  | 9 | 12 | 8 | 11 | 12 | 7 | -83 | -72 | -102 | 43 | 1 | 10 | 17 | 1 | 5 | 9 | 163 | 193 | 111 |  | -27 | -10 | -2 | 0 | 0 | -4 | 144 | 11 | 285 | 285 | 285 | 5 | 5 | 5
1078st | HPS LADONAS | PINT | 4 | 6 | 3 |  | 2 | 3 | 1 | 3 | 5 | 0 | -20 | -4 | -30 | -2 | 0 | 3 | 4 | 0 | 0 | 0 | 47 | 73 | 1 |  | -12 | -3 | -4 | 0 | 0 | -1 | -3 | 0 | 108 | 108 | 108 | 1 | 1 | 1
1081st | CAES Ahaus, Germany | PINT | 36 | 54 | 17 |  | 14 | 20 | 7 | 13 | 15 | 12 | -123 | -66 | -180 | 31 | 2 | 15 | 25 | 0 | 4 | 6 | 205 | 223 | 186 |  | -59 | -16 | -13 | -1 | -1 | -6 | -67 | 5 | 147 | 147 | 147 | 2 | 2 | 2

## 2040NT-ENTSO-E
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1001st | Kaunertal Extension Project | PINT | 80 | 81 | 79 |  | 2 | 5 | -1 | 13 | 15 | 12 | -12 | 3 | -32 | 8 | 2 | 6 | 6 | 1 | 4 | 4 | 208 | 244 | 188 |  | -35 | -2 | -23 | -1 | -1 | -1 | 20 | 4 | 1391 | 1391 | 1391 | 14 | 14 | 14
1003st | Hydro-pumped storage in Bulgaria - Yadenitsa | PINT | 51 | 51 | 50 |  | 19 | 28 | 12 | 10 | 17 | 0 | -131 | -80 | -187 | 0 | 25 | 63 | 67 | 0 | 0 | 0 | 152 | 264 | 4 |  | -75 | -25 | -1 | -1 | 0 | -9 | -113 | -5 | 859 | 859 | 859 | 11 | 11 | 11
1004st | Estonian PHES (pumped-hydro energy storage) | PINT | 28 | 36 | 22 |  | 5 | 6 | 4 | 32 | 47 | 18 | -34 | -24 | -43 | 0 | 6 | 16 | 17 | 0 | 0 | 0 | 492 | 743 | 280 |  | -83 | -3 | -49 | -2 | -3 | -2 | 105 | 2 | 239 | 239 | 239 | 3 | 3 | 3
1006st | HPS AMFILOCHIA | PINT | 44 | 44 | 43 |  | 7 | 9 | 2 | 7 | 15 | -5 | -47 | -17 | -63 | -1 | 9 | 22 | 24 | 0 | 0 | 0 | 102 | 229 | -83 |  | -3 | -1 | -1 | 0 | 0 | 0 | -42 | -1 | 353 | 353 | 353 | 4 | 4 | 4
1012st | Purifying -Pumped Hydroelectric Energy Storage Navaleo (P-PHES Navaleo) | TOOT | 55 | 55 | 55 |  | 10 | 12 | 9 | 83 | 94 | 70 | -71 | -59 | -82 | 5 | 14 | 34 | 36 | 1 | 2 | 3 | 1287 | 1464 | 1104 |  | -20 | -5 | -4 | 0 | 0 | -2 | 280 | 7 | 702 | 702 | 702 | 5 | 5 | 5
1013st | CAES Zuidwending, NL | PINT | 34 | 37 | 32 |  | -4 | 3 | -10 | 15 | 19 | 11 | 25 | 68 | -19 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 293 | 160 |  | -38 | -2 | -24 | -1 | -1 | -1 | -78 | 0 | 206 | 206 | 206 | 12 | 12 | 12
1025st | Silvermines Hydroelectric Power Station | PINT | 11 | 15 | 7 |  | 0 | 1 | -1 | 16 | 27 | 1 | 0 | 8 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 426 | 16 |  | -13 | -1 | -10 | 0 | -1 | 0 | 35 | 0 | 290 | 290 | 290 | 5 | 5 | 5
1026st | Hydro pumped storage Riedl | PINT | 16 | 17 | 14 |  | 0 | 1 | -1 | 11 | 13 | 10 | 2 | 6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 196 | 155 |  | -15 | -2 | -10 | 0 | -1 | -1 | -17 | 0 | 1039 | 1039 | 1039 | 13 | 13 | 13
1027st | Purifying -Pumped Hydroelectric Energy Storage CUA (P-PHES CUA) | PINT | 35 | 35 | 34 |  | 7 | 9 | 5 | 55 | 55 | 54 | -48 | -36 | -59 | 2 | 9 | 23 | 24 | 0 | 1 | 1 | 856 | 871 | 841 |  | -12 | -3 | -2 | 0 | 0 | -1 | 176 | 4 | 1106 | 1106 | 1106 | 8 | 8 | 8
1029st | PSPP Kozjak | PINT | 21 | 23 | 19 |  | 10 | 11 | 7 | 10 | 12 | 8 | -66 | -47 | -76 | 1 | 13 | 32 | 34 | 0 | 0 | 0 | 162 | 191 | 125 |  | -15 | -8 | -6 | 0 | 0 | -3 | 42 | 1 | 467 | 467 | 467 | 6 | 6 | 6
1035st | Ptolemaida Battery Energy Storage System | PINT | 10 | 16 | 3 |  | 1 | 3 | -2 | 6 | 7 | 5 | -9 | 16 | -23 | 1 | 2 | 5 | 5 | 0 | 0 | 0 | 97 | 113 | 80 |  | -6 | 0 | -5 | 0 | 0 | 0 | -5 | 1 | 164 | 164 | 164 | 2 | 2 | 2
1038st | CAES Zuidwending Extension | PINT | 36 | 37 | 35 |  | -3 | 4 | -10 | 13 | 15 | 11 | 22 | 68 | -24 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 201 | 242 | 160 |  | -38 | -2 | -24 | -1 | -1 | -1 | -78 | 0 | 198 | 198 | 198 | 11 | 11 | 11
1041st | Purifying-Pumped Hydroelectric Energy Storage "Velilla del Río Carrión" (P-PHES VELILLA) | PINT | 11 | 14 | 7 |  | 1 | 2 | 1 | 13 | 19 | 7 | -10 | -4 | -15 | 1 | 2 | 5 | 5 | 0 | 0 | 0 | 203 | 301 | 111 |  | -13 | 0 | -8 | 0 | 0 | 0 | 63 | 1 | 721 | 721 | 721 | 5 | 5 | 5
1044st | Green Hydrogen Hub CAES | PINT | 35 | 38 | 33 |  | -3 | 3 | -8 | 18 | 20 | 16 | 17 | 57 | -23 | 3 | 0 | 0 | 0 | 1 | 2 | 2 | 285 | 323 | 247 |  | -37 | -1 | -27 | -1 | -1 | -1 | -184 | 0 | 241 | 241 | 241 | 3 | 3 | 3
1046st | Online Grid Controller “PSKW-Rio” | PINT | 24 | 34 | 14 |  | 0 | 1 | -2 | 15 | 18 | 13 | 3 | 14 | -3 | 13 | 0 | 0 | 0 | 3 | 6 | 7 | 232 | 282 | 196 |  | -13 | 0 | -12 | 0 | -1 | 0 | 248 | 10 | 1039 | 1039 | 1039 | 13 | 13 | 13
1048st | WSK PULS (PHES) | PINT | 27 | 32 | 17 |  | 1 | 3 | 0 | 18 | 26 | 11 | -8 | -3 | -17 | 1 | 2 | 4 | 4 | 0 | 0 | 0 | 282 | 412 | 182 |  | -5 | 0 | -6 | 0 | 0 | 0 | 3 | 0 | 1389 | 1389 | 1389 | 17 | 17 | 17
1050st | SE Integrator | PINT | 28 | 35 | 24 |  | 12 | 14 | 8 | 11 | 20 | 4 | -82 | -57 | -97 | -1 | 16 | 39 | 42 | 0 | -1 | -1 | 174 | 311 | 66 |  | -35 | -12 | -2 | 0 | 0 | -4 | 22 | 2 | 889 | 889 | 889 | 9 | 9 | 9
1052st | Purifying -Pumped Hydroelectric Energy Storage Buseiro (P-PHES BUSEIRO) | PINT | 8 | 10 | 4 |  | 1 | 2 | 0 | 10 | 21 | 1 | -7 | 0 | -16 | 0 | 1 | 3 | 4 | 0 | 0 | 0 | 160 | 328 | 15 |  | -1 | 0 | 0 | 0 | 0 | 0 | 100 | 1 | 746 | 746 | 746 | 5 | 5 | 5
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 68 | 71 | 66 |  | 11 | 12 | 9 | 126 | 129 | 123 | -72 | -63 | -80 | 6 | 14 | 34 | 37 | 1 | 3 | 3 | 1967 | 2017 | 1916 |  | -33 | -5 | -13 | -1 | -1 | -2 | 630 | 9 | 1872 | 1872 | 1872 | 14 | 14 | 14
1064st | CHR IRENE | PINT | 37 | 52 | 19 |  | 6 | 9 | 3 | 69 | 73 | 64 | -41 | -18 | -63 | 1 | 8 | 20 | 21 | 0 | 0 | 0 | 1073 | 1142 | 1004 |  | -14 | -3 | -4 | 0 | 0 | -1 | 267 | 3 | 1266 | 1266 | 1266 | 9 | 9 | 9
1066st | Kemijoki PSP | PINT | 19 | 25 | 12 |  | 0 | 1 | 0 | 21 | 25 | 17 | -2 | 2 | -4 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 332 | 382 | 273 |  | -7 | -2 | 0 | 0 | 0 | -1 | 47 | 2 | 643 | 643 | 643 | 7 | 7 | 7
1067st | PSP CONSO II | PINT | 202 | 208 | 195 |  | 40 | 41 | 38 | 307 | 311 | 304 | -270 | -262 | -278 | 15 | 52 | 130 | 139 | 3 | 7 | 8 | 4807 | 4869 | 4746 |  | -73 | -16 | -18 | -1 | -1 | -6 | 1200 | 30 | 2428 | 2428 | 2428 | 19 | 19 | 19
1068st | Hydro-pumped electricity storage GIRONÉS & RAÏMATS | PINT | 337 | 373 | 309 |  | 66 | 72 | 62 | 526 | 531 | 521 | -449 | -419 | -488 | -5 | 86 | 216 | 231 | -1 | -2 | -3 | 8102 | 8121 | 8082 |  | -100 | -24 | -20 | -1 | -2 | -9 | 2779 | 1 | 3040 | 3040 | 3040 | 25 | 25 | 25
1070st | Hydro-Pumped Electricity Storage in Estonia Mine | PINT | 11 | 17 | 5 |  | 1 | 3 | -2 | 11 | 23 | -6 | -7 | 13 | -23 | 0 | 1 | 3 | 3 | 0 | 0 | 0 | 178 | 365 | -91 |  | -28 | -1 | -15 | -1 | -1 | -1 | 40 | 1 | 224 | 224 | 224 | 3 | 3 | 3
1071st | Villarosa | PINT | 18 | 24 | 10 |  | 3 | 5 | 2 | 15 | 21 | 10 | -20 | -13 | -34 | -1 | 4 | 10 | 11 | 0 | 0 | 0 | 228 | 333 | 163 |  | -2 | -3 | -6 | 0 | 0 | -1 | 10 | 1 | 299 | 299 | 299 | 5 | 5 | 5
1072st | HPS VROCHONERA | PINT | 22 | 24 | 21 |  | 5 | 6 | 4 | 12 | 27 | -2 | -32 | -24 | -40 | 0 | 6 | 15 | 16 | 0 | 0 | 0 | 185 | 418 | -29 |  | -17 | -5 | -1 | 0 | 0 | -2 | 62 | 0 | 373 | 373 | 373 | 5 | 5 | 5
1073st | Taccu Sa Pruna | PINT | 20 | 29 | 14 |  | 6 | 9 | 2 | 16 | 31 | 2 | -40 | -14 | -60 | -1 | 8 | 19 | 21 | 0 | -1 | -1 | 254 | 487 | 34 |  | -17 | -5 | -1 | 0 | 0 | -2 | 17 | 1 | 375 | 375 | 375 | 5 | 5 | 5
1074st | Construction of pumped-storage hydropower plant “Batak”, which utilizes the pre-existing dams of the “Batashki hydroelectric cascade” - (PSHPP “Batak”) | PINT | 59 | 70 | 49 |  | 18 | 21 | 16 | 9 | 14 | 7 | -123 | -107 | -141 | 85 | 24 | 59 | 63 | 16 | 41 | 44 | 146 | 214 | 110 |  | -44 | -15 | -1 | 0 | 0 | -5 | -187 | 47 | 851 | 851 | 851 | 11 | 11 | 11
1075st | Construction of pumped-storage hydropower plant “Dospat” - (PSHPP "Dospat") | PINT | 79 | 90 | 69 |  | 24 | 26 | 22 | 12 | 22 | 2 | -162 | -150 | -174 | 0 | 31 | 78 | 83 | 0 | 0 | 0 | 194 | 339 | 37 |  | -70 | -22 | -3 | -1 | -1 | -8 | -7 | -1 | 841 | 841 | 841 | 11 | 11 | 11
1076st | Favazzina | PINT | 18 | 22 | 15 |  | 5 | 7 | 3 | 13 | 15 | 10 | -33 | -18 | -47 | 0 | 6 | 16 | 17 | 0 | 0 | 0 | 196 | 232 | 161 |  | -2 | -3 | -5 | 0 | 0 | -1 | 2 | 1 | 345 | 345 | 345 | 5 | 5 | 5
1077st | Serra Del Corvo | PINT | 21 | 27 | 12 |  | 5 | 8 | 2 | 14 | 22 | 6 | -36 | -13 | -54 | 0 | 7 | 17 | 18 | 0 | 0 | 0 | 211 | 351 | 91 |  | -21 | -6 | -1 | 0 | 0 | -2 | 27 | 1 | 411 | 411 | 411 | 7 | 7 | 7
1078st | HPS LADONAS | PINT | 10 | 12 | 6 |  | 1 | 2 | 1 | 2 | 8 | -2 | -10 | -8 | -12 | 0 | 2 | 5 | 5 | 0 | 0 | 0 | 32 | 126 | -25 |  | -3 | -2 | -2 | 0 | 0 | -1 | 4 | 0 | 144 | 144 | 144 | 2 | 2 | 2
1081st | CAES Ahaus, Germany | PINT | 51 | 54 | 48 |  | -1 | 8 | -10 | 15 | 16 | 13 | 9 | 70 | -52 | 17 | 0 | 0 | 0 | 3 | 8 | 9 | 227 | 255 | 200 |  | -55 | -5 | -32 | -1 | -2 | -2 | 198 | 11 | 411 | 411 | 411 | 5 | 5 | 5

## 2040DE-ENTSO-E
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1001st | Kaunertal Extension Project | PINT | 84 | 84 | 83 |  | 8 | 10 | 5 | 48 | 62 | 34 | -56 | -33 | -70 | 6 | 11 | 27 | 29 | 1 | 3 | 3 | 680 | 899 | 482 |  | -35 | -4 | -23 | -1 | -1 | -1 | 20 | 4 | 739 | 739 | 739 | 8 | 8 | 8
1003st | Hydro-pumped storage in Bulgaria - Yadenitsa | PINT | 101 | 105 | 98 |  | 31 | 35 | 27 | 25 | 26 | 25 | -211 | -182 | -240 | -6 | 41 | 102 | 109 | -1 | -3 | -3 | 364 | 374 | 355 |  | -95 | -28 | -31 | -1 | -2 | -10 | -113 | -6 | 593 | 593 | 593 | 6 | 6 | 6
1004st | Estonian PHES (pumped-hydro energy storage) | PINT | 38 | 42 | 31 |  | 5 | 8 | 4 | 32 | 36 | 27 | -36 | -24 | -52 | 1 | 7 | 17 | 18 | 0 | 0 | 0 | 453 | 503 | 393 |  | -57 | -2 | -37 | -1 | -2 | -1 | 105 | 4 | 803 | 803 | 803 | 11 | 11 | 11
1006st | HPS AMFILOCHIA | PINT | 46 | 87 | 2 |  | 11 | 22 | 0 | 20 | 31 | 4 | -72 | 1 | -153 | -1 | 14 | 35 | 37 | 0 | -1 | -1 | 280 | 445 | 56 |  | -4 | -1 | -2 | 0 | 0 | 0 | -42 | -2 | 345 | 345 | 345 | 3 | 3 | 3
1012st | Purifying -Pumped Hydroelectric Energy Storage Navaleo (P-PHES Navaleo) | TOOT | 77 | 80 | 73 |  | 12 | 13 | 12 | 76 | 77 | 75 | -84 | -80 | -87 | 9 | 16 | 40 | 43 | 2 | 4 | 5 | 1076 | 1093 | 1061 |  | -31 | -5 | -12 | -1 | -1 | -2 | 280 | 13 | 410 | 410 | 410 | 3 | 3 | 3
1013st | CAES Zuidwending, NL | PINT | 46 | 60 | 33 |  | -3 | 1 | -8 | 17 | 27 | 8 | 21 | 52 | -9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 385 | 105 |  | -20 | -1 | -12 | 0 | -1 | -1 | -78 | -1 | 323 | 323 | 323 | 21 | 21 | 21
1025st | Silvermines Hydroelectric Power Station | PINT | 13 | 16 | 8 |  | 2 | 5 | 1 | 14 | 21 | 5 | -17 | -9 | -33 | 1 | 3 | 8 | 9 | 0 | 0 | 0 | 204 | 305 | 79 |  | -1 | 0 | 1 | 0 | 0 | 0 | 35 | 1 | 1030 | 1030 | 1030 | 10 | 10 | 10
1026st | Hydro pumped storage Riedl | PINT | 28 | 29 | 27 |  | 4 | 5 | 1 | 20 | 24 | 18 | -24 | -7 | -36 | 1 | 5 | 12 | 13 | 0 | 0 | 0 | 290 | 343 | 256 |  | 3 | -1 | 4 | 0 | 0 | 0 | -17 | 0 | 1113 | 1113 | 1113 | 14 | 14 | 14
1027st | Purifying -Pumped Hydroelectric Energy Storage CUA (P-PHES CUA) | PINT | 51 | 54 | 48 |  | 10 | 12 | 9 | 50 | 53 | 46 | -70 | -63 | -82 | 5 | 14 | 34 | 36 | 1 | 2 | 3 | 714 | 747 | 660 |  | -10 | 0 | -10 | 0 | -1 | 0 | 176 | 9 | 443 | 443 | 443 | 3 | 3 | 3
1029st | PSPP Kozjak | PINT | 31 | 34 | 25 |  | 9 | 10 | 7 | 15 | 21 | 12 | -61 | -49 | -68 | 1 | 12 | 29 | 32 | 0 | 1 | 1 | 219 | 300 | 161 |  | -29 | -5 | -28 | -1 | -1 | -2 | 42 | 1 | 421 | 421 | 421 | 5 | 5 | 5
1035st | Ptolemaida Battery Energy Storage System | PINT | 6 | 9 | 1 |  | 3 | 4 | 1 | 1 | 4 | -1 | -17 | -4 | -29 | -67 | 3 | 8 | 9 | -13 | -32 | -35 | 13 | 52 | -12 |  | 0 | 1 | -4 | 0 | 0 | 0 | -1330 | -55 | 166 | 166 | 166 | 2 | 2 | 2
1038st | CAES Zuidwending Extension | PINT | 54 | 60 | 48 |  | -1 | 5 | -8 | 22 | 27 | 17 | 8 | 52 | -35 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 385 | 241 |  | -18 | -2 | -12 | 0 | -1 | -1 | -78 | -1 | 323 | 323 | 323 | 21 | 21 | 21
1041st | Purifying-Pumped Hydroelectric Energy Storage "Velilla del Río Carrión" (P-PHES VELILLA) | PINT | 19 | 24 | 15 |  | 4 | 6 | 4 | 18 | 25 | 13 | -30 | -26 | -38 | 2 | 6 | 15 | 16 | 0 | 1 | 1 | 254 | 352 | 186 |  | -3 | 1 | -5 | 0 | 0 | 0 | 63 | 2 | 314 | 314 | 314 | 2 | 2 | 2
1044st | Green Hydrogen Hub CAES | PINT | 41 | 51 | 31 |  | 1 | 6 | -4 | 30 | 33 | 28 | -6 | 30 | -42 | 33 | 1 | 3 | 3 | 6 | 16 | 17 | 431 | 469 | 393 |  | -23 | -3 | -13 | -1 | -1 | -1 | -184 | 3 | 203 | 203 | 203 | 5 | 5 | 5
1046st | Online Grid Controller “PSKW-Rio” | PINT | 26 | 29 | 24 |  | 3 | 5 | 1 | 19 | 21 | 16 | -23 | -5 | -37 | -4 | 4 | 11 | 12 | -1 | -2 | -2 | 268 | 296 | 231 |  | 2 | 0 | 0 | 0 | 0 | 0 | 248 | 17 | 1115 | 1115 | 1115 | 14 | 14 | 14
1048st | WSK PULS (PHES) | PINT | 30 | 38 | 23 |  | 3 | 4 | 1 | 23 | 24 | 22 | -19 | -9 | -25 | 0 | 4 | 9 | 10 | 0 | 0 | 0 | 325 | 339 | 317 |  | 5 | 0 | 4 | 0 | 0 | 0 | 3 | 0 | 1487 | 1487 | 1487 | 18 | 18 | 18
1050st | SE Integrator | PINT | 29 | 30 | 28 |  | 15 | 17 | 15 | 6 | 11 | 3 | -105 | -101 | -113 | 3 | 20 | 50 | 54 | 1 | 1 | 1 | 80 | 162 | 40 |  | -55 | -14 | -15 | -1 | -1 | -5 | 22 | 2 | 1226 | 1226 | 1226 | 8 | 8 | 8
1052st | Purifying -Pumped Hydroelectric Energy Storage Buseiro (P-PHES BUSEIRO) | PINT | 22 | 24 | 20 |  | 4 | 5 | 4 | 20 | 23 | 18 | -30 | -29 | -31 | 2 | 6 | 14 | 16 | 0 | 1 | 1 | 285 | 333 | 253 |  | 3 | 0 | 0 | 0 | 0 | 0 | 100 | 3 | 325 | 325 | 325 | 2 | 2 | 2
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 124 | 126 | 123 |  | 22 | 24 | 20 | 119 | 120 | 119 | -149 | -134 | -163 | 12 | 29 | 72 | 77 | 2 | 6 | 6 | 1694 | 1722 | 1665 |  | -23 | -3 | -15 | -1 | -1 | -1 | 630 | 23 | 598 | 598 | 598 | 5 | 5 | 5
1064st | CHR IRENE | PINT | 69 | 73 | 64 |  | 14 | 16 | 12 | 65 | 65 | 64 | -94 | -85 | -111 | 3 | 18 | 45 | 49 | 1 | 1 | 1 | 919 | 928 | 901 |  | -13 | -3 | -7 | 0 | 0 | -1 | 267 | 7 | 480 | 480 | 480 | 4 | 4 | 4
1066st | Kemijoki PSP | PINT | 36 | 40 | 33 |  | 4 | 6 | 3 | 32 | 42 | 23 | -29 | -20 | -41 | 1 | 6 | 14 | 15 | 0 | 0 | 0 | 462 | 607 | 327 |  | -41 | 0 | -28 | -1 | -2 | -1 | 47 | 2 | 888 | 888 | 888 | 7 | 7 | 7
1067st | PSP CONSO II | PINT | 271 | 279 | 263 |  | 45 | 48 | 43 | 239 | 241 | 236 | -309 | -293 | -326 | 38 | 59 | 149 | 159 | 7 | 18 | 19 | 3384 | 3455 | 3314 |  | -56 | -14 | -14 | -1 | -1 | -5 | 1200 | 61 | 623 | 623 | 623 | 5 | 5 | 5
1068st | Hydro-pumped electricity storage GIRONÉS & RAÏMATS | PINT | 482 | 509 | 450 |  | 81 | 82 | 80 | 445 | 451 | 437 | -554 | -543 | -560 | -5 | 106 | 267 | 285 | -1 | -2 | -2 | 6418 | 6442 | 6393 |  | -152 | -22 | -70 | -3 | -5 | -8 | 2779 | 44 | 620 | 620 | 620 | 5 | 5 | 5
1070st | Hydro-Pumped Electricity Storage in Estonia Mine | PINT | 13 | 23 | 7 |  | 3 | 4 | 2 | 13 | 23 | 7 | -17 | -12 | -24 | 0 | 3 | 8 | 9 | 0 | 0 | 0 | 189 | 329 | 101 |  | -6 | 0 | -2 | 0 | 0 | 0 | 40 | 2 | 644 | 644 | 644 | 9 | 9 | 9
1071st | Villarosa | PINT | 18 | 28 | 13 |  | 6 | 7 | 5 | 12 | 18 | 9 | -38 | -31 | -51 | 2 | 7 | 18 | 20 | 0 | 1 | 1 | 178 | 262 | 124 |  | -5 | -1 | -4 | 0 | 0 | 0 | 10 | 1 | 418 | 418 | 418 | 8 | 8 | 8
1072st | HPS VROCHONERA | PINT | 50 | 53 | 44 |  | 10 | 12 | 9 | 28 | 33 | 25 | -68 | -58 | -81 | 2 | 13 | 33 | 35 | 0 | 1 | 1 | 405 | 475 | 356 |  | 4 | -2 | 10 | 0 | 1 | -1 | 62 | 0 | 354 | 354 | 354 | 4 | 4 | 4
1073st | Taccu Sa Pruna | PINT | 22 | 29 | 17 |  | 6 | 6 | 5 | 26 | 33 | 19 | -38 | -35 | -41 | 1 | 7 | 18 | 20 | 0 | 0 | 1 | 371 | 476 | 271 |  | -6 | -3 | 2 | 0 | 0 | -1 | 17 | 1 | 426 | 426 | 426 | 2 | 2 | 2
1074st | Construction of pumped-storage hydropower plant “Batak”, which utilizes the pre-existing dams of the “Batashki hydroelectric cascade” - (PSHPP “Batak”) | PINT | 64 | 68 | 60 |  | 24 | 29 | 15 | 17 | 25 | 10 | -160 | -103 | -196 | 158 | 31 | 77 | 83 | 30 | 76 | 81 | 244 | 360 | 133 |  | -96 | -27 | -29 | -1 | -2 | -9 | -187 | 94 | 599 | 599 | 599 | 5 | 5 | 5
1075st | Construction of pumped-storage hydropower plant “Dospat” - (PSHPP "Dospat") | PINT | 85 | 85 | 85 |  | 32 | 33 | 30 | 29 | 29 | 29 | -215 | -206 | -224 | -1 | 41 | 103 | 111 | 0 | -1 | -1 | 420 | 420 | 420 |  | -108 | -31 | -30 | -1 | -2 | -11 | -7 | -1 | 583 | 583 | 583 | 5 | 5 | 5
1076st | Favazzina | PINT | 17 | 28 | 7 |  | 5 | 6 | 4 | 11 | 11 | 10 | -31 | -25 | -38 | 1 | 6 | 15 | 16 | 0 | 1 | 1 | 153 | 153 | 152 |  | -6 | -1 | -4 | 0 | 0 | 0 | 2 | 0 | 380 | 380 | 380 | 2 | 2 | 2
1077st | Serra Del Corvo | PINT | 25 | 34 | 21 |  | 6 | 7 | 5 | 20 | 26 | 17 | -44 | -37 | -51 | 2 | 8 | 21 | 22 | 0 | 1 | 1 | 291 | 370 | 240 |  | -10 | -2 | -6 | 0 | 0 | -1 | 27 | 1 | 450 | 450 | 450 | 2 | 2 | 2
1078st | HPS LADONAS | PINT | 15 | 19 | 12 |  | 5 | 8 | 3 | 8 | 11 | 5 | -32 | -21 | -52 | 3 | 6 | 15 | 17 | 1 | 1 | 2 | 113 | 152 | 77 |  | 2 | 0 | 2 | 0 | 0 | 0 | 4 | 0 | 162 | 162 | 162 | 2 | 2 | 2
1081st | CAES Ahaus, Germany | PINT | 59 | 69 | 49 |  | -2 | 3 | -7 | 20 | 22 | 19 | 13 | 47 | -21 | -5 | 0 | 0 | 0 | -1 | -2 | -3 | 290 | 315 | 264 |  | -7 | -1 | -2 | 0 | 0 | 0 | 198 | 18 | 446 | 446 | 446 | 5 | 5 | 5

## 2030NT-EU27
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1001st | Kaunertal Extension Project | PINT | 60 | 69 | 46 |  | 23 | 26 | 18 | 14 | 15 | 13 | -200 | -156 | -232 | 2 | 3 | 25 | 40 | 0 | 0 | 0 | 211 | 223 | 200 |  | -77 | -20 | -21 | -1 | -1 | -7 | -3 | 0 | 391 | 391 | 391 | 7 | 7 | 7
1003st | Hydro-pumped storage in Bulgaria - Yadenitsa | PINT | 11 | 11 | 11 |  | 1 | 2 | 0 | -1 | 2 | -4 | -6 | 2 | -14 | -121 | 0 | 1 | 2 | -2 | -15 | -24 | -10 | 34 | -54 |  | -10 | 0 | -5 | 0 | 0 | 0 | -127 | -46 | 387 | 387 | 387 | 7 | 7 | 7
1004st | Estonian PHES (pumped-hydro energy storage) | PINT | 19 | 21 | 15 |  | 7 | 10 | 4 | 15 | 17 | 13 | -62 | -33 | -87 | 1 | 1 | 8 | 12 | 0 | 0 | 0 | 227 | 258 | 205 |  | -170 | -7 | -102 | -4 | -6 | -4 | 12 | 0 | 331 | 331 | 331 | 3 | 3 | 3
1006st | HPS AMFILOCHIA | PINT | 3 | 6 | 1 |  | 1 | 1 | 1 | 0 | 3 | -3 | -12 | -10 | -13 | -68 | 0 | 1 | 2 | -1 | -8 | -14 | 3 | 42 | -39 |  | -5 | -1 | -1 | 0 | 0 | 0 | -70 | -23 | 232 | 232 | 232 | 3 | 3 | 3
1012st | Purifying -Pumped Hydroelectric Energy Storage Navaleo (P-PHES Navaleo) | TOOT | 51 | 60 | 43 |  | 19 | 20 | 16 | 54 | 56 | 53 | -166 | -138 | -181 | 28 | 2 | 21 | 33 | 0 | 4 | 6 | 834 | 855 | 821 |  | -39 | -11 | -6 | 0 | -1 | -4 | 81 | 6 | 509 | 509 | 509 | 3 | 3 | 3
1013st | CAES Zuidwending, NL | PINT | 42 | 70 | 15 |  | 13 | 18 | 8 | 16 | 17 | 15 | -116 | -71 | -161 | -2 | 1 | 14 | 23 | 0 | 0 | 0 | 245 | 253 | 238 |  | -55 | -15 | -15 | -1 | -1 | -5 | 14 | 0 | 165 | 165 | 165 | 5 | 5 | 5
1025st | Silvermines Hydroelectric Power Station | PINT | 15 | 16 | 13 |  | 5 | 6 | 3 | 20 | 27 | 12 | -40 | -26 | -51 | 1 | 1 | 5 | 8 | 0 | 0 | 0 | 309 | 414 | 190 |  | -18 | -5 | -4 | 0 | 0 | -2 | 33 | 0 | 150 | 150 | 150 | 2 | 2 | 2
1026st | Hydro pumped storage Riedl | PINT | 35 | 39 | 32 |  | 11 | 14 | 9 | 19 | 21 | 15 | -95 | -76 | -126 | 79 | 1 | 12 | 19 | 1 | 10 | 16 | 292 | 327 | 230 |  | -41 | -11 | -10 | -1 | -1 | -4 | 374 | 25 | 366 | 366 | 366 | 5 | 5 | 5
1027st | Purifying -Pumped Hydroelectric Energy Storage CUA (P-PHES CUA) | PINT | 37 | 42 | 30 |  | 14 | 16 | 11 | 37 | 39 | 35 | -122 | -96 | -143 | 15 | 2 | 15 | 25 | 0 | 2 | 3 | 562 | 607 | 532 |  | -27 | -7 | -11 | 0 | -1 | -2 | 61 | 4 | 699 | 699 | 699 | 5 | 5 | 5
1029st | PSPP Kozjak | PINT | 12 | 17 | 7 |  | 3 | 5 | 2 | 3 | 4 | 1 | -26 | -18 | -42 | 7 | 0 | 3 | 5 | 0 | 1 | 1 | 40 | 58 | 13 |  | -8 | -3 | -2 | 0 | 0 | -1 | 26 | 2 | 380 | 380 | 380 | 6 | 6 | 6
1035st | Ptolemaida Battery Energy Storage System | PINT | 4 | 10 | 0 |  | 1 | 1 | 0 | 1 | 2 | -1 | -7 | -4 | -10 | -1 | 0 | 1 | 1 | 0 | 0 | 0 | 13 | 29 | -14 |  | -3 | -1 | -5 | 0 | 0 | 0 | -7 | 0 | 111 | 111 | 111 | 2 | 2 | 2
1038st | CAES Zuidwending Extension | PINT | 43 | 70 | 17 |  | 14 | 19 | 8 | 17 | 17 | 17 | -119 | -71 | -168 | -2 | 2 | 15 | 24 | 0 | 0 | 0 | 258 | 263 | 253 |  | -56 | -15 | -13 | -1 | -1 | -5 | 14 | 0 | 161 | 161 | 161 | 5 | 5 | 5
1041st | Purifying-Pumped Hydroelectric Energy Storage "Velilla del Río Carrión" (P-PHES VELILLA) | PINT | 18 | 24 | 15 |  | 6 | 8 | 4 | 15 | 17 | 11 | -51 | -35 | -68 | 6 | 1 | 6 | 10 | 0 | 1 | 1 | 229 | 266 | 162 |  | -14 | -3 | -6 | 0 | 0 | -1 | 28 | 2 | 483 | 483 | 483 | 3 | 3 | 3
1044st | Green Hydrogen Hub CAES | PINT | 31 | 36 | 25 |  | 12 | 18 | 6 | 14 | 14 | 14 | -109 | -56 | -162 | 9 | 1 | 14 | 22 | 0 | 1 | 2 | 211 | 215 | 206 |  | -58 | -15 | -17 | -1 | -1 | -5 | 24 | 2 | 153 | 153 | 153 | 2 | 2 | 2
1046st | Online Grid Controller “PSKW-Rio” | PINT | 33 | 34 | 32 |  | 11 | 14 | 9 | 17 | 19 | 15 | -94 | -78 | -121 | 35 | 1 | 12 | 19 | 0 | 4 | 7 | 260 | 292 | 230 |  | -39 | -11 | -9 | 0 | -1 | -4 | 6 | 8 | 368 | 368 | 368 | 5 | 5 | 5
1048st | WSK PULS (PHES) | PINT | 40 | 44 | 34 |  | 14 | 16 | 12 | 24 | 27 | 22 | -127 | -105 | -140 | 54 | 2 | 16 | 26 | 1 | 7 | 11 | 375 | 413 | 335 |  | -43 | -11 | -13 | -1 | -1 | -4 | 207 | 16 | 489 | 489 | 489 | 6 | 6 | 6
1050st | SE Integrator | PINT | 23 | 25 | 21 |  | 7 | 10 | 5 | 4 | 5 | 3 | -65 | -47 | -88 | 0 | 1 | 8 | 13 | 0 | 0 | 0 | 60 | 80 | 48 |  | -24 | -8 | -2 | 0 | 0 | -3 | 4 | 0 | 424 | 424 | 424 | 6 | 6 | 6
1052st | Purifying -Pumped Hydroelectric Energy Storage Buseiro (P-PHES BUSEIRO) | PINT | 18 | 22 | 14 |  | 7 | 8 | 4 | 16 | 18 | 14 | -60 | -40 | -71 | 4 | 1 | 7 | 12 | 0 | 0 | 1 | 252 | 272 | 214 |  | -22 | -5 | -10 | 0 | 0 | -2 | 25 | 1 | 497 | 497 | 497 | 4 | 4 | 4
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 93 | 102 | 80 |  | 32 | 35 | 28 | 96 | 99 | 91 | -279 | -250 | -305 | 31 | 4 | 35 | 56 | 0 | 4 | 6 | 1475 | 1520 | 1394 |  | -52 | -15 | -10 | -1 | -1 | -5 | 249 | 9 | 1110 | 1110 | 1110 | 8 | 8 | 8
1064st | CHR IRENE | PINT | 47 | 51 | 45 |  | 19 | 21 | 13 | 47 | 49 | 46 | -164 | -119 | -189 | 13 | 2 | 20 | 33 | 0 | 2 | 3 | 726 | 756 | 698 |  | -31 | -10 | -3 | 0 | 0 | -4 | 86 | 3 | 790 | 790 | 790 | 6 | 6 | 6
1066st | Kemijoki PSP | PINT | 17 | 20 | 15 |  | 4 | 5 | 3 | 19 | 21 | 18 | -33 | -28 | -42 | 1 | 0 | 4 | 7 | 0 | 0 | 0 | 294 | 326 | 276 |  | -29 | -2 | -18 | -1 | -1 | -1 | 68 | 2 | 487 | 487 | 487 | 6 | 6 | 6
1067st | PSP CONSO II | PINT | 188 | 223 | 163 |  | 78 | 82 | 74 | 182 | 200 | 167 | -685 | -651 | -723 | 110 | 9 | 85 | 138 | 1 | 14 | 22 | 2791 | 3042 | 2552 |  | -117 | -35 | -10 | -1 | -1 | -12 | 430 | 26 | 1430 | 1430 | 1430 | 11 | 11 | 11
1068st | Hydro-pumped electricity storage GIRONÉS & RAÏMATS | PINT | 304 | 321 | 290 |  | 110 | 131 | 82 | 314 | 322 | 305 | -972 | -726 | -1156 | 78 | 12 | 121 | 196 | 1 | 10 | 16 | 4827 | 5002 | 4663 |  | -183 | -56 | -14 | -2 | -2 | -19 | 1661 | 41 | 1798 | 1798 | 1798 | 16 | 16 | 16
1070st | Hydro-Pumped Electricity Storage in Estonia Mine | PINT | 11 | 12 | 10 |  | 5 | 7 | 3 | 8 | 9 | 7 | -42 | -24 | -59 | 0 | 1 | 5 | 8 | 0 | 0 | 0 | 123 | 136 | 109 |  | -30 | -3 | -16 | -1 | -1 | -1 | -5 | 0 | 259 | 259 | 259 | 3 | 3 | 3
1071st | Villarosa | PINT | 21 | 22 | 19 |  | 7 | 10 | 5 | 7 | 9 | 5 | -61 | -46 | -85 | 35 | 1 | 8 | 12 | 0 | 4 | 7 | 101 | 133 | 82 |  | -26 | -8 | -4 | 0 | 0 | -3 | 107 | 8 | 344 | 344 | 344 | 7 | 7 | 7
1072st | HPS VROCHONERA | PINT | 6 | 8 | 5 |  | 2 | 3 | 0 | 0 | 2 | -3 | -14 | -4 | -22 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | -2 | 38 | -49 |  | -2 | -2 | -3 | 0 | 0 | -1 | -1 | 0 | 244 | 244 | 244 | 3 | 3 | 3
1073st | Taccu Sa Pruna | PINT | 19 | 22 | 14 |  | 8 | 11 | 6 | 10 | 11 | 9 | -69 | -51 | -101 | 39 | 1 | 9 | 14 | 0 | 5 | 8 | 157 | 174 | 140 |  | -29 | -9 | -5 | 0 | 0 | -3 | 168 | 11 | 255 | 255 | 255 | 5 | 5 | 5
1074st | Construction of pumped-storage hydropower plant “Batak”, which utilizes the pre-existing dams of the “Batashki hydroelectric cascade” - (PSHPP “Batak”) | PINT | 22 | 28 | 20 |  | 8 | 10 | 6 | 6 | 13 | 1 | -69 | -51 | -85 | 6 | 1 | 9 | 14 | 0 | 1 | 1 | 89 | 203 | 14 |  | -15 | -7 | -2 | 0 | 0 | -2 | 23 | 1 | 376 | 376 | 376 | 7 | 7 | 7
1075st | Construction of pumped-storage hydropower plant “Dospat” - (PSHPP "Dospat") | PINT | 40 | 41 | 38 |  | 13 | 15 | 11 | 10 | 26 | 0 | -114 | -95 | -134 | 12 | 1 | 14 | 23 | 0 | 1 | 2 | 162 | 396 | -5 |  | -37 | -13 | -1 | 0 | 0 | -5 | 37 | 3 | 379 | 379 | 379 | 7 | 7 | 7
1076st | Favazzina | PINT | 18 | 19 | 17 |  | 8 | 10 | 7 | 10 | 11 | 8 | -70 | -63 | -85 | 32 | 1 | 9 | 14 | 0 | 4 | 6 | 154 | 168 | 127 |  | -16 | -7 | -2 | 0 | 0 | -2 | 109 | 8 | 240 | 240 | 240 | 5 | 5 | 5
1077st | Serra Del Corvo | PINT | 24 | 26 | 22 |  | 9 | 11 | 8 | 11 | 12 | 7 | -80 | -67 | -100 | 35 | 1 | 10 | 16 | 0 | 4 | 7 | 164 | 194 | 116 |  | -24 | -9 | -1 | 0 | 0 | -3 | 114 | 9 | 281 | 281 | 281 | 5 | 5 | 5
1078st | HPS LADONAS | PINT | 4 | 6 | 3 |  | 2 | 3 | 0 | 3 | 5 | 0 | -18 | -3 | -27 | -1 | 0 | 2 | 4 | 0 | 0 | 0 | 47 | 73 | 2 |  | -11 | -3 | -4 | 0 | 0 | -1 | -3 | 0 | 99 | 99 | 99 | 1 | 1 | 1
1081st | CAES Ahaus, Germany | PINT | 44 | 68 | 21 |  | 14 | 20 | 7 | 13 | 15 | 12 | -121 | -64 | -179 | 30 | 2 | 15 | 24 | 0 | 4 | 6 | 204 | 222 | 186 |  | -56 | -15 | -14 | -1 | -1 | -5 | -71 | 5 | 148 | 148 | 148 | 2 | 2 | 2

## 2040NT-EU27
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1001st | Kaunertal Extension Project | PINT | 90 | 109 | 64 |  | 2 | 5 | -1 | 15 | 19 | 12 | -13 | 4 | -35 | 8 | 3 | 6 | 7 | 1 | 4 | 4 | 234 | 301 | 177 |  | -35 | -2 | -23 | -1 | -1 | -1 | 20 | 4 | 1391 | 1391 | 1391 | 14 | 14 | 14
1003st | Hydro-pumped storage in Bulgaria - Yadenitsa | PINT | 63 | 73 | 58 |  | 17 | 26 | 11 | 11 | 18 | 2 | -117 | -76 | -174 | 0 | 23 | 56 | 60 | 0 | 0 | 0 | 170 | 289 | 39 |  | -61 | -21 | -2 | 0 | 0 | -7 | -103 | -4 | 824 | 824 | 824 | 11 | 11 | 11
1004st | Estonian PHES (pumped-hydro energy storage) | PINT | 29 | 37 | 24 |  | 5 | 6 | 4 | 34 | 50 | 22 | -33 | -24 | -42 | 0 | 6 | 16 | 17 | 0 | 0 | 0 | 527 | 791 | 344 |  | -81 | -2 | -49 | -2 | -3 | -2 | 105 | 2 | 239 | 239 | 239 | 3 | 3 | 3
1006st | HPS AMFILOCHIA | PINT | 44 | 44 | 43 |  | 6 | 8 | 3 | 14 | 14 | 13 | -44 | -18 | -58 | -1 | 8 | 21 | 23 | 0 | 0 | 0 | 213 | 218 | 207 |  | -3 | -1 | -1 | 0 | 0 | 0 | -42 | -1 | 268 | 268 | 268 | 4 | 4 | 4
1012st | Purifying -Pumped Hydroelectric Energy Storage Navaleo (P-PHES Navaleo) | TOOT | 57 | 57 | 57 |  | 11 | 12 | 10 | 86 | 86 | 85 | -74 | -69 | -78 | 5 | 14 | 35 | 38 | 1 | 2 | 3 | 1318 | 1342 | 1295 |  | -18 | -4 | -5 | 0 | 0 | -1 | 281 | 7 | 699 | 699 | 699 | 5 | 5 | 5
1013st | CAES Zuidwending, NL | PINT | 39 | 42 | 37 |  | -3 | 3 | -10 | 14 | 17 | 10 | 23 | 69 | -22 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 212 | 274 | 149 |  | -39 | -3 | -24 | -1 | -1 | -1 | -78 | 0 | 206 | 206 | 206 | 12 | 12 | 12
1025st | Silvermines Hydroelectric Power Station | PINT | 12 | 18 | 7 |  | 0 | 1 | -1 | 17 | 27 | 5 | 0 | 8 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 433 | 76 |  | -14 | 0 | -10 | 0 | -1 | 0 | 35 | 0 | 290 | 290 | 290 | 5 | 5 | 5
1026st | Hydro pumped storage Riedl | PINT | 27 | 45 | 14 |  | 1 | 4 | 0 | 19 | 29 | 13 | -10 | 0 | -25 | 1 | 2 | 5 | 5 | 0 | 0 | 0 | 216 | 233 | 199 |  | -16 | -2 | -9 | 0 | -1 | -1 | -16 | 0 | 1039 | 1039 | 1039 | 13 | 13 | 13
1027st | Purifying -Pumped Hydroelectric Energy Storage CUA (P-PHES CUA) | PINT | 38 | 38 | 38 |  | 7 | 9 | 6 | 57 | 57 | 57 | -50 | -40 | -60 | 2 | 10 | 24 | 26 | 0 | 1 | 1 | 889 | 895 | 884 |  | -14 | -3 | -3 | 0 | 0 | -1 | 177 | 4 | 1074 | 1074 | 1074 | 8 | 8 | 8
1029st | PSPP Kozjak | PINT | 23 | 27 | 19 |  | 8 | 10 | 6 | 7 | 10 | 3 | -56 | -43 | -67 | 1 | 11 | 27 | 29 | 0 | 1 | 1 | 103 | 158 | 42 |  | -7 | -5 | -6 | 0 | 0 | -2 | 46 | 1 | 467 | 467 | 467 | 6 | 6 | 6
1035st | Ptolemaida Battery Energy Storage System | PINT | 12 | 17 | 6 |  | 1 | 3 | -2 | 3 | 12 | -9 | -9 | 14 | -23 | 1 | 2 | 5 | 5 | 0 | 0 | 0 | 44 | 186 | -136 |  | -6 | 0 | -5 | 0 | 0 | 0 | -6 | 0 | 125 | 125 | 125 | 2 | 2 | 2
1038st | CAES Zuidwending Extension | PINT | 42 | 42 | 42 |  | -3 | 4 | -10 | 13 | 17 | 10 | 21 | 69 | -28 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 205 | 261 | 149 |  | -39 | -2 | -24 | -1 | -1 | -1 | -78 | 0 | 198 | 198 | 198 | 11 | 11 | 11
1041st | Purifying-Pumped Hydroelectric Energy Storage "Velilla del Río Carrión" (P-PHES VELILLA) | PINT | 13 | 18 | 7 |  | 2 | 2 | 1 | 14 | 20 | 8 | -12 | -6 | -16 | 1 | 2 | 6 | 6 | 0 | 0 | 0 | 222 | 305 | 115 |  | -16 | -1 | -8 | 0 | 0 | -1 | 63 | 1 | 687 | 687 | 687 | 5 | 5 | 5
1044st | Green Hydrogen Hub CAES | PINT | 45 | 45 | 44 |  | -2 | 4 | -8 | 18 | 22 | 15 | 15 | 57 | -26 | 3 | 0 | 0 | 0 | 1 | 1 | 1 | 288 | 346 | 229 |  | -38 | -1 | -27 | -1 | -1 | -1 | -332 | -11 | 241 | 241 | 241 | 3 | 3 | 3
1046st | Online Grid Controller “PSKW-Rio” | PINT | 28 | 38 | 14 |  | 0 | 1 | -2 | 16 | 18 | 13 | 1 | 11 | -5 | 11 | 0 | 0 | 0 | 2 | 5 | 6 | 252 | 286 | 199 |  | -13 | 0 | -11 | 0 | -1 | 0 | 260 | 12 | 1039 | 1039 | 1039 | 13 | 13 | 13
1048st | WSK PULS (PHES) | PINT | 30 | 39 | 18 |  | 1 | 2 | 1 | 19 | 31 | 9 | -8 | -4 | -13 | 1 | 2 | 4 | 4 | 0 | 0 | 0 | 295 | 483 | 150 |  | -6 | 0 | -6 | 0 | 0 | 0 | 3 | 0 | 1389 | 1389 | 1389 | 17 | 17 | 17
1050st | SE Integrator | PINT | 35 | 42 | 28 |  | 12 | 14 | 8 | 14 | 20 | 10 | -82 | -57 | -96 | -1 | 16 | 39 | 42 | 0 | 0 | 0 | 222 | 311 | 159 |  | -35 | -13 | -2 | 0 | 0 | -4 | 27 | 2 | 889 | 889 | 889 | 9 | 9 | 9
1052st | Purifying -Pumped Hydroelectric Energy Storage Buseiro (P-PHES BUSEIRO) | PINT | 10 | 17 | 4 |  | 1 | 2 | 0 | 12 | 23 | 5 | -7 | 0 | -14 | 0 | 1 | 4 | 4 | 0 | 0 | 0 | 194 | 366 | 77 |  | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 1 | 743 | 743 | 743 | 5 | 5 | 5
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 74 | 77 | 70 |  | 11 | 12 | 10 | 130 | 134 | 126 | -73 | -65 | -81 | 6 | 14 | 35 | 38 | 1 | 3 | 3 | 2033 | 2100 | 1965 |  | -33 | -5 | -13 | -1 | -1 | -2 | 630 | 9 | 1798 | 1798 | 1798 | 13 | 13 | 13
1064st | CHR IRENE | PINT | 41 | 59 | 19 |  | 6 | 9 | 3 | 74 | 78 | 69 | -43 | -21 | -64 | 1 | 8 | 21 | 22 | 0 | 0 | 0 | 1150 | 1222 | 1079 |  | -15 | -3 | -4 | 0 | 0 | -1 | 268 | 3 | 1237 | 1237 | 1237 | 9 | 9 | 9
1066st | Kemijoki PSP | PINT | 21 | 31 | 14 |  | 1 | 1 | 0 | 23 | 25 | 22 | -5 | -3 | -6 | 0 | 1 | 2 | 2 | 0 | 0 | 0 | 361 | 397 | 342 |  | -4 | -1 | 0 | 0 | 0 | 0 | 37 | 2 | 643 | 643 | 643 | 7 | 7 | 7
1067st | PSP CONSO II | PINT | 211 | 219 | 203 |  | 40 | 41 | 38 | 312 | 317 | 308 | -270 | -261 | -278 | 15 | 52 | 130 | 139 | 3 | 7 | 8 | 4880 | 4965 | 4796 |  | -71 | -16 | -18 | -1 | -1 | -6 | 1202 | 30 | 2303 | 2303 | 2303 | 17 | 17 | 17
1068st | Hydro-pumped electricity storage GIRONÉS & RAÏMATS | PINT | 349 | 388 | 323 |  | 66 | 71 | 62 | 525 | 530 | 520 | -449 | -422 | -484 | -5 | 86 | 216 | 231 | -1 | -2 | -3 | 8092 | 8118 | 8067 |  | -98 | -24 | -20 | -1 | -2 | -9 | 2785 | 1 | 2881 | 2881 | 2881 | 23 | 23 | 23
1070st | Hydro-Pumped Electricity Storage in Estonia Mine | PINT | 13 | 20 | 7 |  | 1 | 4 | -1 | 15 | 27 | 1 | -10 | 7 | -26 | 0 | 2 | 5 | 5 | 0 | 0 | 0 | 237 | 432 | 22 |  | -29 | -2 | -15 | -1 | -1 | -1 | 40 | 1 | 224 | 224 | 224 | 3 | 3 | 3
1071st | Villarosa | PINT | 21 | 28 | 11 |  | 3 | 5 | 2 | 16 | 21 | 12 | -21 | -14 | -33 | -1 | 4 | 10 | 11 | 0 | 0 | 0 | 245 | 327 | 185 |  | -2 | -3 | -6 | 0 | 0 | -1 | 8 | 1 | 293 | 293 | 293 | 4 | 4 | 4
1072st | HPS VROCHONERA | PINT | 26 | 32 | 21 |  | 5 | 6 | 3 | 14 | 28 | 2 | -31 | -21 | -41 | 0 | 6 | 15 | 16 | 0 | 0 | 0 | 223 | 419 | 36 |  | -16 | -4 | -1 | 0 | 0 | -2 | 60 | 0 | 288 | 288 | 288 | 4 | 4 | 4
1073st | Taccu Sa Pruna | PINT | 24 | 34 | 15 |  | 6 | 8 | 2 | 17 | 32 | 4 | -40 | -17 | -58 | -2 | 8 | 19 | 20 | 0 | -1 | -1 | 269 | 497 | 70 |  | -15 | -5 | -1 | 0 | 0 | -2 | 15 | 0 | 346 | 346 | 346 | 5 | 5 | 5
1074st | Construction of pumped-storage hydropower plant “Batak”, which utilizes the pre-existing dams of the “Batashki hydroelectric cascade” - (PSHPP “Batak”) | PINT | 57 | 58 | 57 |  | 17 | 20 | 13 | 9 | 13 | 5 | -115 | -91 | -138 | 87 | 22 | 55 | 59 | 17 | 42 | 45 | 142 | 199 | 81 |  | -34 | -12 | -2 | 0 | 0 | -4 | -184 | 47 | 817 | 817 | 817 | 11 | 11 | 11
1075st | Construction of pumped-storage hydropower plant “Dospat” - (PSHPP "Dospat") | PINT | 84 | 96 | 75 |  | 22 | 24 | 21 | 14 | 26 | 4 | -151 | -143 | -166 | 0 | 29 | 73 | 78 | 0 | 0 | 0 | 225 | 411 | 71 |  | -60 | -19 | -2 | -1 | -1 | -7 | -5 | -1 | 805 | 805 | 805 | 10 | 10 | 10
1076st | Favazzina | PINT | 23 | 27 | 18 |  | 5 | 7 | 3 | 16 | 17 | 14 | -32 | -18 | -46 | 0 | 6 | 15 | 17 | 0 | 0 | 0 | 243 | 266 | 221 |  | -2 | -3 | -5 | 0 | 0 | -1 | 1 | 1 | 342 | 342 | 342 | 5 | 5 | 5
1077st | Serra Del Corvo | PINT | 19 | 26 | 12 |  | 5 | 7 | 2 | 14 | 22 | 9 | -34 | -14 | -51 | 0 | 6 | 16 | 17 | 0 | 0 | 0 | 225 | 345 | 139 |  | -18 | -5 | -1 | 0 | 0 | -2 | 25 | 1 | 404 | 404 | 404 | 6 | 6 | 6
1078st | HPS LADONAS | PINT | 13 | 18 | 6 |  | 2 | 2 | 1 | 5 | 8 | 2 | -11 | -9 | -14 | 0 | 2 | 5 | 6 | 0 | 0 | 0 | 73 | 128 | 35 |  | -5 | -2 | -2 | 0 | 0 | -1 | 3 | 0 | 113 | 113 | 113 | 1 | 1 | 1
1081st | CAES Ahaus, Germany | PINT | 63 | 71 | 55 |  | -2 | 8 | -11 | 15 | 18 | 13 | 11 | 72 | -51 | 14 | 0 | 0 | 0 | 3 | 7 | 7 | 239 | 287 | 191 |  | -55 | -5 | -32 | -1 | -2 | -2 | 214 | 13 | 411 | 411 | 411 | 5 | 5 | 5

## 2040DE-EU27
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1001st | Kaunertal Extension Project | PINT | 95 | 95 | 95 |  | 7 | 10 | 3 | 45 | 60 | 30 | -50 | -23 | -69 | 8 | 10 | 24 | 26 | 1 | 4 | 4 | 647 | 862 | 426 |  | -32 | -4 | -21 | -1 | -1 | -1 | 20 | 4 | 739 | 739 | 739 | 8 | 8 | 8
1003st | Hydro-pumped storage in Bulgaria - Yadenitsa | PINT | 94 | 108 | 74 |  | 28 | 32 | 24 | 19 | 28 | 6 | -188 | -165 | -216 | -6 | 36 | 91 | 97 | -1 | -3 | -3 | 272 | 398 | 86 |  | -90 | -27 | -24 | -1 | -1 | -10 | -103 | -5 | 593 | 593 | 593 | 6 | 6 | 6
1004st | Estonian PHES (pumped-hydro energy storage) | PINT | 37 | 43 | 29 |  | 5 | 8 | 3 | 30 | 33 | 26 | -36 | -20 | -54 | 1 | 7 | 17 | 18 | 0 | 0 | 0 | 429 | 459 | 371 |  | -58 | -2 | -37 | -1 | -2 | -1 | 105 | 4 | 803 | 803 | 803 | 11 | 11 | 11
1006st | HPS AMFILOCHIA | PINT | 49 | 95 | 2 |  | 10 | 20 | -1 | 18 | 29 | 4 | -67 | 4 | -138 | -1 | 13 | 32 | 34 | 0 | -1 | -1 | 254 | 418 | 51 |  | -5 | -2 | -1 | 0 | 0 | -1 | -42 | -2 | 230 | 230 | 230 | 2 | 2 | 2
1012st | Purifying -Pumped Hydroelectric Energy Storage Navaleo (P-PHES Navaleo) | TOOT | 82 | 84 | 80 |  | 12 | 13 | 11 | 75 | 78 | 72 | -83 | -75 | -87 | 9 | 16 | 40 | 43 | 2 | 4 | 5 | 1073 | 1093 | 1037 |  | -34 | -4 | -15 | -1 | -1 | -2 | 281 | 13 | 410 | 410 | 410 | 3 | 3 | 3
1013st | CAES Zuidwending, NL | PINT | 53 | 68 | 37 |  | -3 | 1 | -8 | 15 | 26 | 4 | 22 | 54 | -10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 373 | 59 |  | -21 | -2 | -10 | 0 | -1 | -1 | -78 | -1 | 323 | 323 | 323 | 21 | 21 | 21
1025st | Silvermines Hydroelectric Power Station | PINT | 11 | 14 | 5 |  | 2 | 5 | 1 | 12 | 21 | 3 | -16 | -6 | -34 | 1 | 3 | 7 | 8 | 0 | 0 | 0 | 177 | 307 | 37 |  | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1 | 1030 | 1030 | 1030 | 10 | 10 | 10
1026st | Hydro pumped storage Riedl | PINT | 28 | 30 | 25 |  | 4 | 6 | 1 | 20 | 23 | 17 | -25 | -7 | -38 | 1 | 5 | 12 | 13 | 0 | 0 | 0 | 283 | 329 | 238 |  | 4 | -1 | 6 | 0 | 0 | 0 | -16 | 0 | 1113 | 1113 | 1113 | 14 | 14 | 14
1027st | Purifying -Pumped Hydroelectric Energy Storage CUA (P-PHES CUA) | PINT | 51 | 54 | 49 |  | 10 | 12 | 9 | 48 | 51 | 44 | -70 | -63 | -83 | 5 | 13 | 34 | 36 | 1 | 2 | 3 | 688 | 733 | 630 |  | -10 | -1 | -7 | 0 | 0 | -1 | 177 | 9 | 443 | 443 | 443 | 3 | 3 | 3
1029st | PSPP Kozjak | PINT | 33 | 37 | 25 |  | 7 | 8 | 6 | 17 | 21 | 14 | -45 | -39 | -55 | 2 | 9 | 21 | 23 | 0 | 1 | 1 | 249 | 293 | 195 |  | -8 | -2 | -8 | 0 | 0 | -1 | 46 | 2 | 421 | 421 | 421 | 5 | 5 | 5
1035st | Ptolemaida Battery Energy Storage System | PINT | 7 | 9 | 1 |  | 3 | 5 | 0 | -1 | 1 | -3 | -17 | -2 | -31 | 0 | 3 | 8 | 9 | 0 | 0 | 0 | -8 | 13 | -36 |  | -1 | 0 | -2 | 0 | 0 | 0 | -6 | 0 | 116 | 116 | 116 | 1 | 1 | 1
1038st | CAES Zuidwending Extension | PINT | 60 | 68 | 52 |  | -1 | 5 | -8 | 20 | 26 | 14 | 9 | 54 | -36 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 373 | 199 |  | -19 | -2 | -12 | 0 | -1 | -1 | -78 | -1 | 323 | 323 | 323 | 21 | 21 | 21
1041st | Purifying-Pumped Hydroelectric Energy Storage "Velilla del Río Carrión" (P-PHES VELILLA) | PINT | 19 | 23 | 15 |  | 4 | 5 | 4 | 16 | 24 | 9 | -30 | -24 | -37 | 1 | 6 | 14 | 15 | 0 | 1 | 1 | 224 | 349 | 133 |  | -5 | -1 | -3 | 0 | 0 | 0 | 63 | 2 | 314 | 314 | 314 | 2 | 2 | 2
1044st | Green Hydrogen Hub CAES | PINT | 46 | 57 | 35 |  | 1 | 7 | -4 | 28 | 31 | 24 | -9 | 30 | -49 | 14 | 2 | 5 | 5 | 3 | 7 | 7 | 393 | 447 | 339 |  | -31 | -3 | -20 | -1 | -1 | -1 | -332 | -9 | 203 | 203 | 203 | 5 | 5 | 5
1046st | Online Grid Controller “PSKW-Rio” | PINT | 26 | 29 | 24 |  | 3 | 6 | 0 | 17 | 20 | 14 | -23 | -3 | -37 | -1 | 4 | 11 | 12 | 0 | -1 | -1 | 244 | 281 | 200 |  | 1 | -1 | -1 | 0 | 0 | 0 | 260 | 19 | 1115 | 1115 | 1115 | 14 | 14 | 14
1048st | WSK PULS (PHES) | PINT | 32 | 41 | 21 |  | 3 | 4 | 1 | 23 | 24 | 21 | -19 | -7 | -27 | 0 | 4 | 9 | 10 | 0 | 0 | 0 | 322 | 349 | 292 |  | 5 | 0 | 6 | 0 | 0 | 0 | 3 | 0 | 1487 | 1487 | 1487 | 18 | 18 | 18
1050st | SE Integrator | PINT | 35 | 36 | 34 |  | 14 | 15 | 13 | 4 | 11 | 0 | -96 | -91 | -104 | 3 | 18 | 46 | 49 | 1 | 2 | 2 | 57 | 153 | 4 |  | -52 | -12 | -18 | -1 | -1 | -4 | 27 | 2 | 1226 | 1226 | 1226 | 8 | 8 | 8
1052st | Purifying -Pumped Hydroelectric Energy Storage Buseiro (P-PHES BUSEIRO) | PINT | 21 | 22 | 19 |  | 5 | 5 | 4 | 17 | 23 | 14 | -31 | -28 | -33 | 2 | 6 | 15 | 16 | 0 | 1 | 1 | 247 | 328 | 200 |  | 1 | -1 | -1 | 0 | 0 | 0 | 100 | 3 | 325 | 325 | 325 | 2 | 2 | 2
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 125 | 126 | 124 |  | 22 | 24 | 20 | 116 | 116 | 115 | -149 | -134 | -165 | 12 | 29 | 72 | 77 | 2 | 6 | 6 | 1643 | 1671 | 1615 |  | -24 | -3 | -14 | -1 | -1 | -1 | 630 | 23 | 598 | 598 | 598 | 5 | 5 | 5
1064st | CHR IRENE | PINT | 69 | 73 | 64 |  | 14 | 16 | 12 | 63 | 65 | 61 | -93 | -82 | -111 | 3 | 18 | 45 | 48 | 1 | 1 | 1 | 901 | 926 | 859 |  | -14 | -3 | -7 | 0 | 0 | -1 | 268 | 7 | 480 | 480 | 480 | 4 | 4 | 4
1066st | Kemijoki PSP | PINT | 36 | 39 | 33 |  | 5 | 7 | 3 | 30 | 41 | 21 | -32 | -19 | -46 | 1 | 6 | 15 | 17 | 0 | 0 | 0 | 425 | 588 | 305 |  | -44 | -2 | -29 | -1 | -2 | -1 | 37 | 2 | 888 | 888 | 888 | 7 | 7 | 7
1067st | PSP CONSO II | PINT | 276 | 285 | 267 |  | 46 | 48 | 43 | 238 | 243 | 233 | -310 | -292 | -328 | 38 | 60 | 149 | 160 | 7 | 18 | 19 | 3370 | 3480 | 3259 |  | -55 | -13 | -14 | -1 | -1 | -5 | 1202 | 61 | 623 | 623 | 623 | 5 | 5 | 5
1068st | Hydro-pumped electricity storage GIRONÉS & RAÏMATS | PINT | 493 | 522 | 458 |  | 82 | 83 | 80 | 443 | 450 | 433 | -555 | -542 | -563 | -5 | 107 | 267 | 286 | -1 | -2 | -2 | 6402 | 6434 | 6370 |  | -152 | -22 | -72 | -3 | -5 | -8 | 2785 | 44 | 620 | 620 | 620 | 5 | 5 | 5
1070st | Hydro-Pumped Electricity Storage in Estonia Mine | PINT | 13 | 22 | 8 |  | 3 | 4 | 2 | 4 | 5 | 3 | -19 | -11 | -25 | 0 | 4 | 9 | 10 | 0 | 0 | 0 | 61 | 81 | 41 |  | -11 | -1 | -6 | 0 | 0 | 0 | 40 | 2 | 644 | 644 | 644 | 9 | 9 | 9
1071st | Villarosa | PINT | 20 | 29 | 14 |  | 5 | 7 | 4 | 11 | 18 | 7 | -37 | -29 | -50 | 1 | 7 | 18 | 19 | 0 | 1 | 1 | 161 | 253 | 92 |  | -6 | -2 | -3 | 0 | 0 | -1 | 8 | 0 | 418 | 418 | 418 | 8 | 8 | 8
1072st | HPS VROCHONERA | PINT | 54 | 59 | 45 |  | 10 | 12 | 8 | 26 | 31 | 22 | -70 | -55 | -83 | 2 | 13 | 34 | 36 | 0 | 1 | 1 | 367 | 448 | 316 |  | -3 | -2 | 3 | 0 | 0 | -1 | 60 | 0 | 233 | 233 | 233 | 2 | 2 | 2
1073st | Taccu Sa Pruna | PINT | 24 | 31 | 19 |  | 5 | 6 | 5 | 25 | 33 | 18 | -37 | -32 | -41 | 0 | 7 | 18 | 19 | 0 | 0 | 0 | 352 | 472 | 251 |  | -8 | -3 | 1 | 0 | 0 | -1 | 15 | 0 | 426 | 426 | 426 | 2 | 2 | 2
1074st | Construction of pumped-storage hydropower plant “Batak”, which utilizes the pre-existing dams of the “Batashki hydroelectric cascade” - (PSHPP “Batak”) | PINT | 68 | 73 | 62 |  | 23 | 27 | 15 | 15 | 24 | 6 | -154 | -101 | -185 | 156 | 30 | 74 | 79 | 30 | 75 | 80 | 211 | 345 | 84 |  | -94 | -27 | -24 | -1 | -1 | -9 | -184 | 94 | 599 | 599 | 599 | 5 | 5 | 5
1075st | Construction of pumped-storage hydropower plant “Dospat” - (PSHPP "Dospat") | PINT | 87 | 87 | 87 |  | 24 | 30 | 15 | 25 | 26 | 24 | -167 | -101 | -207 | -2 | 32 | 80 | 86 | 0 | -1 | -1 | 364 | 382 | 345 |  | -102 | -32 | -20 | -1 | -1 | -11 | -5 | -1 | 583 | 583 | 583 | 5 | 5 | 5
1076st | Favazzina | PINT | 19 | 31 | 8 |  | 4 | 6 | 4 | 9 | 10 | 8 | -31 | -26 | -38 | 1 | 6 | 15 | 16 | 0 | 0 | 0 | 131 | 150 | 112 |  | -7 | -2 | -4 | 0 | 0 | -1 | 1 | 0 | 426 | 426 | 426 | 2 | 2 | 2
1077st | Serra Del Corvo | PINT | 28 | 37 | 23 |  | 6 | 7 | 5 | 19 | 25 | 15 | -42 | -34 | -49 | 2 | 8 | 20 | 21 | 0 | 1 | 1 | 266 | 363 | 211 |  | -9 | -2 | -5 | 0 | 0 | -1 | 25 | 1 | 483 | 483 | 483 | 3 | 3 | 3
1078st | HPS LADONAS | PINT | 16 | 18 | 15 |  | 5 | 7 | 3 | 7 | 10 | 2 | -33 | -21 | -51 | 3 | 6 | 16 | 17 | 1 | 1 | 1 | 99 | 144 | 22 |  | -4 | -1 | -1 | 0 | 0 | 0 | 3 | 0 | 121 | 121 | 121 | 1 | 1 | 1
1081st | CAES Ahaus, Germany | PINT | 68 | 81 | 55 |  | -2 | 3 | -7 | 19 | 22 | 15 | 12 | 46 | -22 | -1 | 0 | 0 | 0 | 0 | 0 | -1 | 262 | 312 | 213 |  | -8 | -1 | -2 | 0 | 0 | 0 | 214 | 20 | 446 | 446 | 446 | 5 | 5 | 5

## Trans.ProjectLevelBenefits
Project ID | Project name | B7.1 Balancing Energy Exchange | [5 empty] | B8.1 Frequency stability | [5 empty] | B9 Reduction of necessary reserve for re-dispatch power plants
|  | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040 | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040 | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040
|  | Qualitative assessment by ENTSO-E | [5 empty] | MWh/year | [5 empty] | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year

## Stor.ProjectLevelBenefits
Project ID | Project name | B7.1 Balancing Energy Exchange | [5 empty] | B9 Reduction of necessary reserve for re-dispatch power plants
|  | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040 | NT2030 |  | NT2040 |  | DE2030 |  | DE2040 |  | 2030 |  | 2040
|  | Qualitative assessment by ENTSO-E | [5 empty] | M€ / year |  | M€ / year |  | M€ / year |  | M€ / year |  | M€ / year |  | M€ / year
1001 | Kaunertal Extension Project | [6 empty] | 5,09 | 1,13 GW/a GW/a | 2,03 | 0,45 GW/a GW/a | 10,43 (value for DE 2040) | 2,32 GW/a (value for DE 2040) GW/a | -9,58 (value for DE 2050) | - 2,13 GW/a (value for DE 2050) GW/a
1003 | Hydro-pumped storage in Bulgaria - Yadenitsa
1004 | Estonian PHES (pumped-hydro energy storage)
1006 | HPS AMFILOCHIA
1012 | Purifying -Pumped Hydroelectric Energy Storage Navaleo (P-PHES Navaleo) |  |  |  |  | 1.7 | 2.0 | [8 empty] | 4.3 | 7,791 €/MW |  | €/MW
1013 | CAES Zuidwending, NL
1025 | Silvermines Hydroelectric Power Station |  |  |  |  | 4.5 | [9 empty] | 15.7 | 87GWh 87GWh |  | 87GWh
1026 | Hydro pumped storage Riedl | [6 empty] | -2.46 | -0,55 GWh/year | 4.95 | 1.1 GWh/year | 9.24 (value for DE 2040) | 2.05 (Value for DE 2040) GWh/year | -14.92 (value for DE 2050) | -3.32 (value for DE 2050) GWh/year
1027 | Purifying -Pumped Hydroelectric Energy Storage CUA (P-PHES CUA) |  |  |  |  | 1.7 | 2.0 | [8 empty] | 4.8 | 12,989 €/MW |  | €/MW
1029 | PSPP Kozjak |  |  |  |  | 3.2 | 4.9
1035 | Ptolemaida Battery Energy Storage System
1038 | CAES Zuidwending Extension
1041 | Purifying-Pumped Hydroelectric Energy Storage "Velilla del Río Carrión" (P-PHES VELILLA) |  |  |  |  | 1.7 | 2.0 | [8 empty] | 4.9 | 31,324 €/MW |  | €/MW
1044 | Green Hydrogen Hub CAES
1046 | Online Grid Controller “PSKW-Rio” | [6 empty] | 7.93 | 1.76 GW/year |  | GW/year |  | GW/year |  | GW/year
1048 | WSK PULS (PHES)
1050 | SE Integrator
1052 | Purifying -Pumped Hydroelectric Energy Storage Buseiro (P-PHES BUSEIRO) |  |  |  |  | 1.7 | 2.0 | [8 empty] | 4.2 | 29,688 €/MW |  | €/MW
1054 | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" |  |  |  |  | 13.13 | [9 empty] | 23.61 | 582.97 GWh 582.97 GWh |  | 582.97 GWh
1064 | CHR IRENE
1066 | Kemijoki PSP
1067 | PSP CONSO II | [6 empty] | 54 | 1333 GWh |  | GWh |  | GWh |  | GWh
1068 | Hydro-pumped electricity storage GIRONÉS & RAÏMATS | [6 empty] | 26000000 | 933 . | 64000000 | 2285 . |  | . |  | .
1070 | Hydro-Pumped Electricity Storage in Estonia Mine
1071 | Villarosa
1072 | HPS VROCHONERA
1073 | Taccu Sa Pruna
1074 | Construction of pumped-storage hydropower plant “Batak”, which utilizes the pre-existing dams of the “Batashki hydroelectric cascade” - (PSHPP “Batak”)
1075 | Construction of pumped-storage hydropower plant “Dospat” - (PSHPP "Dospat")
1076 | Favazzina
1077 | Serra Del Corvo
1078 | HPS LADONAS
1081 | CAES Ahaus, Germany