## Readme
ABOUT THE INFORMATION IN THIS EXCEL TEMPLATE | COST-BENEFIT ANALYSIS RESULTS
Information presented in this excel file has been downloaded from ENTSO-E's TYNDP 2024 projects platform, accessible to project promoters at https://tyndp2024.entsoe.eu/projects-map/transmission/ and https://tyndp2024.entsoe.eu/projects-map/storage/. This excel files contains, for all or part of the projects depending on the filters applied before downloading: - TYNDP 2024 transmission projects data, at project level and at investment level - TYNDP 2024 storage projects data - Results of the cost-benefit analysis performed by ENTSO-E About the data Information presented in the tabs Trans.Projects, Trans.Investments and Stor.Projects was submitted by project promoters. CBA results presented in tabs 2030NT, 2040NT and 2040DE are the outcome of the assessment performed by ENTSO-E. Information presented in the tabs Trans.ProjectLevelBenefits and Stor.ProjectLevelBenefits was provided by project promoters. | Tabs 2030NT, 2040NT and 2040DE present the results of the cost-benefit analysis performed by ENTSO-E, for each scenario studied in the TYNDP 2024. Refer to the following table for information on each indicator. Results in the tabs 2030NT, etc are for the full area covered by the study (see TYNDP 2024 CBA Implementation Guidelines).
Indicators
| Shortcut | Full name | Indicator | Unit
| ΔSEW | Annual Socio-Economic Welfare (SEW) increase (excluding Energy Not Served cost) | B1 | M€ / year
| ΔSEW_CO2 | Annual Socio-Economic Welfare variation resulting from CO2 emmisions | B1_CO2 | M€ / year
| ΔSEW_RES | Annual Socio-Economic Welfare increase resulting from RES integration | B1_RES | M€ / year
| ΔCO2_market | Annual CO2 varation from market simulation | B2a | ktonnes / year
| ΔCO2_network | Annual CO2 varation due to network losses | B2b | ktonnes / year
| ΔCO2_market_monetised | Annual Societal cost variation resulting from CO2 variation from market simulation | B2a_€ | M€ / year
| ΔCO2_network_monetised | Annual Societal cost variation resulting from CO2 variation from network simulation | B2b_€ | M€ / year
| ΔRES | Annual avoided curtailment (RES integration) | B3 | GWh / year
| ΔRES_MW | Connected RES | B3a | MW
| ΔNOx | Nitrogen oxides | B4a | kg / year
| ΔNH3 | Ammonia | B4b | kg / year
| ΔSO2 | Sulphur dioxide | B4c | kg / year
| ΔPM5 | Particulate matter 5 | B4d | kg / year
For questions on TYNDP 2024 data, contact tyndp@entsoe.eu | ΔPM10 | Particulate matter 10 | B4e | kg / year
| ΔNMVOC | Non-methane volatile organic compounds | B4f | kg / year
| Δlosses | Variation of network losses | B5 | GWh / year
| Δlosses_monetised | Variation of network losses monetised | B5_€ | M€ / year
| ΔSoS | Annual reduction in Energy Not Served | B6 | MWh / year
| ΔSoS_monetised | Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served | B6_€ | M€ / year

## Trans.Projects
TYNDP 2024 - General information on transmission projects | [17 empty] | Needs addressed by the project |  |  |  | Expected transfer capacity increase |  |  | CBA
Project ID | Project Name | Description of the project | Promoters | Country | National development plan(s) | Commissioning Year estimated by the promoter | Status ID 1 : Under Consideration, 2 : In Planning but not permitting, 3 : In permitting, 4 : Under Construction | Is the project cross-border? | Is the project internal? | Type of project - Is it an upgrade of existing infrastructure? | Is the project on the 5th PCI list? | PCI number | Reason for investment clustering | Inclusion in previous TYNDPs | Is the project in the 2030 reference grid? | Is the project in the 2035 reference grid? | Where can one find more information on the project? (ex: project website url) | Needs addressed by the project | Explanation by the promoter on how the project addresses the need | Relevant system needs study results in 2030 (Border - Capacity Increase) | Relevant system needs study results in 2040 (Border or country - Capacity Increase - Storage flexibility) | Border | Transfer capacity increase A-B (MW) | Transfer capacity increase B-A (MW) | Comments on CBA results by the project promoter
1 | RES in north of Portugal | The main objective of this project consists in introducing the network reinforcements that are needed to allow the connection of new RES generation (hydro with pumping and also wind) that is foreseen in the north of Portugal, where the RES potential is high. The project includes a set of new 400 kV OHL that will form a new axis between V. Minho-R. Pena-Feira (PCI 2.16.3). | Rede Elétrica Nacional | PT | NDP 1, Portugal, Draft NDP 2022-2031 (2021); Main report, Page 13 (https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf); Apendix 11, page 5 (https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf) | 2025 | 4 | False | True | New | True | 2.16.3 | Clustering: This project includes a set of new 400 kV OHL that will form a new axis between V. Minho-R. Pena-Feira, ensuring the network capacity to evacuate the new amounts of generation, taking also into consideration the n-1 security criteria. The new substations of R. Pena is also considered in this axis for direct connection of generation. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | Portuguese National Development Plan: https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf; https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf Project website https://www.ren.pt/en-gb/activity/main-projects/res-in-northern-portugal-pic-2163-on-the-2021-pic-list-of-the-ce-5th-list-tyndp-2020-project-1-1 https://www.ren.pt/en-gb/activity/main-projects/linha-dupla-ribeira-de-pena-vieira-do-minho-a-400-kv-1 PCI page – link to EC platform: https://ec.europa.eu/energy/en/topics/infrastructure/projects-common-interest | Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The integration of Hydro power plants with pumping capabilities (included in this project) are necessary in order to comply with national adequacy standards. Storage facilities such as pumped storage and hydro storage schemes with peak generation are one of the solutions to cope with high power ramps Project for integration of Hydro power plants with pumping |  |  | internalPT00 | 1400 | 1400
4 | Interconnection Portugal-Spain | In order to reach a complete operational Iberian Electricity Market (MIBEL), and strengthen the Internal Energy Market (IEM), the increase of the interconnection between Spain and Portugal is needed. A new OHL 400kV interconnection between Fontefría (Spain) and Ponte de Lima (Portugal). Internal reinforcements complement the cross border section, such as the axis in Spain between Fontefría and Beariz, in order to be able to connect the crossborder project to the existing network, and in Portugal between Ponte de Lima (previously Viana do Castelo) and Vila Nova de Famalicão (previously Vila doConde). This project was included in all the PCI list since 2013 (PCI 2.17). | REN and Red Eléctrica | ES ;PT | Spanish NDP, " Plan de desarrollo de la red de transporte de energia eléctrica. Periodo 2021-2026" , Project Label INT_ESP-POR and Project Sheet in Annex I Page 133 (Main Report in https://www.planificacionelectrica.es/sites/webplani/files/2022-04/REE_Plan_Desarrollo.pdf and interactive project map https://www.planificacionelectrica.es/proyectos) & Portuguese Draft NDP 2022-2031 (2021); Main report, Page 13 (https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf); Apendix 11, page 5 (https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf) | 2025 | 4 | True | False | New | True | 1.1 | Clustering: the project consists of a set of investments in the same transmission corridor, based on a 400 kV OHL axis linking the substations of Beariz and Fontefría, in Spain, with P. Lima-V. N. Famalicão, in Portugal. These reinforcements are all needed (as they are in series) to achieve the main objectives of the project: reinforcement of the interconnection capacity between Portugal and Spain having in mind the MIBEL targets agreed by the Portuguese and Spanish governments and also to allow Portugal to achieve the 10% interconnection ratio defined by the EC, both contributing for the IEM. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | Project website http://www.ree.es/es/actividades/gestor-de-la-red-y-transportista/proyectos-de-interes-comun-europeos-pic ; https://www.ren.pt/en-gb/activity/main-projects/portugal-spain-interconnection-pci-217-on-ec-s-2021-pci-list-5th-list-tyndp-2020-project-4 PCI page – link to EC platform https://ec.europa.eu/energy/en/topics/infrastructure/projects-common-interest Other links: Spanish National Development Plan: https://www.planificacionelectrica.es/sites/webplani/files/2022-04/REE_Plan_Desarrollo.pdf and its interactive project map platform: https://www.planificacionelectrica.es/proyectos Portuguese National Development Plan: https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf; https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf Inter-Governmental agreement (Madrid and Lisbon Declarations) https://ec.europa.eu/energy/sites/ener/files/documents/Madrid%20declaration.pdf ; https://ec.europa.eu/info/sites/info/files/lisbon_declaration_energyinterconnections_final.pdf Constitution of the High Level Group on Interconnections for South West Europe The High Level Group is responsible to prepare a plan to implement the Madrid Declaration and ensure regular monitoring of progress of the projects and provide adequate technical assistance to the Member states. The group will deal with both gas and electricity infrastructure. http://europa.eu/rapid/press-release_IP-15-5187_en.htm XXII Portuguese-Spanish Summit (main conclusions) Main conclusions from the XXII Portuguese-Spanish summit where both governments agreed to continue working on the definition and routes for two new interconnection in order to reach an interconnection capacity of 3000 MW by 2010 between both countries. https://www.madrid.embaixadaportugal.mne.pt/images/Declara%C3%A7%C3%A3o_XXII_Cimeira_Luso-Espanhola.pdf | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | IoSN report shows that the yearly average marginal price difference is higher than the 2€/MWh defined by Interconnection Target Expert Group as threshold for developing new interconnections. In addition, Spanish interconnectors nominal transmission capacity is below 30% of the RES capacity. The increase of interconnection capacity will be essential to cope with the residual load ramps challenge. The increase of interconnection capacity between countries will allow to exchange the power flows from flexibility sources. New interconnections with cross border impact can enable the increase of exchange of balancing energy (Welfare savings through exchanging balancing energy and trough imbalance netting). Balancing energy refers to products such as Replacement Reserve (RR), manual and automatic Frequency Regulation Reserve (FRR). TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity. |  |  | ES00-PT00 | 1500 | 800
16 | Biscay Gulf | The project consists of 370 km HVDC-VSC link (2 bipoles of 1000 MW each) mainly subsea in the Biscay Gulf, between Gatica (Basque Country, ES) and Cubnezais (Aquitaine, FR). Included in the Madrid Declaration, this project aims at improving the interconnection ES-FR. This project was included in all the PCI list since 2013 (PCI 2.7) | Red Eléctrica, Rte | ES ;FR | Spanish NDP "Plan de Desarrollo de la Red de Transporte de Energía Eléctrica. Período 2021-2026", Project Label INT_ESP-FRA_1: Interconexión España-Francia por el Golfo de Vizcaya pg276 https://www.planificacionelectrica.es/sites/webplani/files/2022-06/REE_Plan_Desarrollo.pdf, page 144 and Project Sheet - French NDP, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°476, page 441, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2028 | 4 | True | False | New | True | 1.2 | This project has interdependence with the internal projects P378 and P379 that reinforce the Gatica area in Spain. These internal reinforcements should be commissioned together with the Biscay Gulf. Although the clustering of all projects would have sense, it was not possible due to the CBA methodology clustering rules. A global profitability would have sense considering the 3 projects together. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | - PCI page – link to EC platform: http://ec.europa.eu/energy/infrastructure/transparency_platform/map-viewer/main.html - Other links Spanish National Development Plan: https://www.planificacionelectrica.es/sites/webplani/files/2022-06/REE_Plan_Desarrollo.pdf and its project sheet platform: https://www.planificacionelectrica.es/proyectos - French National Development Planhttp://www.rte-france.com/fr/article/schema-decennal-de-developpement-de-reseau - Inter-Governmental agreement (Madrid and Lisbon Declarations): https://ec.europa.eu/energy/sites/ener/files/documents/Madrid%20declaration.pdf, https://ec.europa.eu/info/sites/info/files/lisbon_declaration_energyinterconnections_final.pdf - Constitution of the High Level Group on Interconnections for South West Europe: http://europa.eu/rapid/press-release_IP-15-5187_en.htm | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The increase of interconnection capacity will be essential to cope with the residual load ramps challenge. The increase of interconnection capacity between countries will allow to exchange the power flows from flexibility sources. On the French-Spanish border, the yearly average marginal price difference is higher than the 2€/MWh defined by Interconnection Target Expert Group as threshold for developing new interconnections. In addition, Spanish interconnectors nominal transmission capacity is below 30% of the national peak load and RES capacity. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity in ES-FR border. |  |  | ES00-FR00 | 2200 | 2200
28 | Italy-Montenegro | The Italy-Montenegro interconnection project foresees a new HVDC subsea cable between the DC Converter Stations of Villanova (Italy) and Lastva (Montenegro). The realization of the second pole of the interconnection will increase the transmission capacity from 600 MW to 1200 MW and is strictly correlated with the Transbalkan Corridor (project 227) and the Mid Continental East Corridor (project 144). The Project will provide greater integration of the Italian electricity market with the South-Eastern Europe (SEE) energy systems, support the energy transition towards greater integration of renewable energy sources and promote the exchange of renewable energy. | Terna, CGES | IT ;ME | Piano di Sviluppo 2023 – Analisi costi-benefici del secondo polo dell’interconnessione HVDC Italia – Montenegro, Italy, 2023, https://www.arera.it/allegati/operatori/pds/23/Analisi%20costi%20benefici%20e%20approfondimenti%20del%20collegamento%20Italia%20-%20Montenegro.pdf | 2027 | 4 | True | False | New | False |  |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian market zones and Montenegro This project will help to solve important congestions among Italian transmission grid This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity This project will improve the integration of italian RES generation | Italy - Montenegro - 1100 | Italy - Montenegro - 600 - Italy - - 1000 - 5000 | ITCS-ME00 | 600 | 600
29 | Italy-Tunisia | The project consists of a new HVDC submarine interconnection between Tunisia (Mlaabi - Cape Bon Peninsula) and Sicily (Partanna) with a rated power of 600 MW. The realization of the project is supported by the Italian and Tunisian Governments to increase the interconnection capacity of the Euro-Mediterranean system. The Project will strengthen and further support the renewable energy projects in both involved regions, optimise the use of energy production sources, enable the share of balancing resources, improve the security of supply and increase the operational flexibility of both electricity systems. Given the strategic importance of the Project in 2017, it was acknowledged as a pivotal cross-border infrastructure project for the EU and designated as a Project of Common Interest (PCI) by the European Commission. Furthermore, in 2022, the project secured funding exceeding 300 M€ from the EU Connecting Europe Facility (CEF). | Terna, STEG | IT ;TN | Piano di Sviluppo 2023 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Centro Sud, Italy, 2021, ID: 601-I, Pag. 41, https://www.terna.it/en/electric-system/grid/national-electricity-transmission-grid-development-plan | 2028 | 4 | True | False | New | True | 1.19 |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | Link to the official site of the project: https://elmedproject.com/it/ | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian and Tunisia market zones This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity This project will improve the integration of italian RES generation | Italy - Tunisia - 600 | Italy - Tunisia - 600 - Italy - - 1000 - 5000 | ITSI-TN00 | 600 | 600 | It is worth to point out that the comparison between the benefits and the costs makes sense only when they have the same perimeter. Therefore, European benefits should not be compared to the overall costs (European and Non European).
33 | Central Northern Italy | The project consists of the strengthening of interconnection between the northern and the central part of Italy. It will involve the upgrading of the existing 220 kV over-head line to 400 kV between Colunga and Calenzano substations as well as the removal of limitations on the existing 220 kV network in Central Italy. | Terna SpA | IT | Piano di Sviluppo 2023 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Est, pag. 146, ID: 302-P and 432-P, https://download.terna.it/terna/Terna_PdS_2023_Avanzamento_Piani_Sviluppo_Precedenti_Avanzamento_Nord_Est_8db254a9ec58dd8.pdf | 2026 | 4 | False | True | Upgrade | False |  | The two investments will closely contribute to reduce congestions and guarantee a major market integration between Italy-North and Italy Center | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | "Link to the last release of the Italian National Development Plan http://www.terna.it/en-gb/sistemaelettrico/pianodisviluppodellarete.aspx" | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | The new line will allow congestion reduction on the North Center-Northern border, in order to transport the foreign import to the local loads and to integrate the southern renewable production. In case of failure of the OHL along the Adriatic or Thyrrenic coast the upgraded lines will improve transient stability. |  |  | ITCN-ITN1 ITCN-ITCS | 400 150 | 400 150
35 | CZ Southwest-east corridor | A corridor of internal 400 kV overhead lines inside the Czech Republic connecting existing 420 kV substations between Prestice, Kocin and Mirovka in the southwest-east direction. The project consists of building a new AC 400 kV overhead line which connects 420 kV substations Kocin and Mirovka with double circuit line of about 120.5 km length and a nominal transmission capacity of 2 x 2445 A, building a AC 400 kV overhead lines that involves changing of a 400 kV existing single-circuit line to double-circuit line with a nominal capacity of 2 x 2445 A between Kocin and Prestice. | CEPS | CZ | Ten-year investment plan for the development of the TS 2021 – 2030, CZ, 2021, V406/407–New KOC–HBM Line and V432/429–Line Doubling, 128 pg., https://www.ceps.cz/en/transmission-system-development | 2029 | 3 | False | True | MostlyNew | True | 2.3.2 and 2.3.3 | Project 35 that contains investment items 313 and 315 altogether with Project 200 that contains investment item 308 (item 309 was already commissioned) forms a geographically continuous (uninterrupted) network corridor from a new 420 kV substation Vernerov (already commissioned at the end of 2017), through a new 420 kV substation Vitkov (which is also already commissioned at the end of 2020), existing 420 kV substation Prestice, existing 420 kV substation Kocin and ending up to the existing substation 420 kV Mirovka. It is actually what is referred as a “convoy lines” or "sequential projects" with all 4 involved 400 kV overhead lines (investment 308 (Vernerov-Vitkov), 309 (Vitkov-Prestice), 315 (Prestice-Kocin) and 313 (Kocin-Mirovka)) connected in series forming a corridor from the northern-western part of the Czech grid related to the DE-CZ border into the south and eastern direction towards the CZ-SK and CZ-AT borders. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | Information about Czech development plan and PCI projects can be found on the following links below on the CEPS website: https://www.ceps.cz/en/transmission-system-development https://www.ceps.cz/en/pci-projects-of-common-interest |  |  | Czech Republic - Germany - 1000 | Czech Republic - Germany - 1000 - Germany - - 5000 - 10000 | CZ00-DE00 | 500 | 500
40 | Belgium-Luxembourg-Germany: long-term perspective | An increase of transfer capacity across the BE-LU-DE corridor is envisioned towards the 2040 time horizon. Further studies will determine the appropriate implementation option and timing, taking into account the expected evolution on the LU-DE border as presented in project 328 Project motivation: This project increases the degree of interconnectivity between the Belgian - Luxemburg - German corridor. The possibility of higher market exchanges between bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | Amprion, Creos, Elia | BE ;DE ;LU | NDP1, Belgium, 2024-2034, ID70, 186, NDP2, Luxemburg, 2040, Scenario report 2040 p.43 ( 2nd February 2018) | 2040 | 1 | True | False | New | False |  |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | More information about the project can be found following this link: - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase of crossborder capacity between Belgium-Luxembourg-Germany. Increase of crossborder capacity between Belgium-Luxembourg-Germany. Contribution of the adequacy of Belgium, Luxembourg and Germany. Increase of crossborder capacity between Belgium-Luxembourg-Germany leading to also a better integration of RES | Belgium - Luxemburg - 500 Luxemburg - Germany - 400 | Belgium - Luxemburg - 500 - Luxemburg - Germany - 400 - Germany - - 5000 - 10000 Luxemburg - - <1000 Belgium - - <1000 | BE00-LUG1 | 500 | 500
47 | Westtirol (AT) - Vöhringen (DE) | This project will increase the current power exchange capacity between Austria and Germany by an upgrade of the existing overhead line Vöhringen (DE) - Westtirol (AT) to 380 kV and the extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. | Amprion, Austrian Power Grid | AT ;DE | Germany: Netzentwicklungsplan 2035 Version 2021, Project P74, p.457, Austria: APG Netzentwicklungsplan 2021, AT, 2021, 13-2, 48, https://www.apg.at/en/Stromnetz/Netzentwicklung | 2030 | 2 | True | False | Upgrade | False |  |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | https://www.apg.at/stromnetz/netzausbau/ https://www.netzentwicklungsplan.de/de/projekte/projekte-nep-2035-2021 The project was part of the previous TYNDP 2022, Link to the Website: https://tyndp2022-project-platform.azurewebsites.net/projectsheets/transmission/47 | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase of Austrian German interconnection level Better utilization of existing and future pump storage power plants by improved transport capacities. Connecting German RES power with pump storages in Austria | Austria - Germany - 3100 | Austria - Germany - 3100 - Austria - - <1000 Germany - - 5000 - 10000 | AT00-DE00 | 600 | 600
81 | North South Interconnector | A new 400 kV interconnector between Woodland in Ireland and Turleenan in Northern Ireland. | Eirgrid, SONI | GB ;IE | Transmission Development Plan Northern Ireland 2021-2030, Northern Ireland, page 74: https://www.soni.ltd.uk/media/documents/Transmission-Development-Plan-Northern-Ireland-2021-2030.pdf • https://www.eirgridgroup.com/site-files/library/EirGrid/Transmission-Development-Plan-2021-2030.pdf | 2029 | 3 | True | False | New | False |  |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | Project website: http://www.eirgridgroup.com/the-grid/projects/north-south/the-project/ This circuit will establish a second interconnector between Ireland and Northern Ireland, effectively eliminating the ongoing risk of system separation, thus allowing an increased transfer capacity. The project has received the required consents in both jurisdictions. The project will be implemented by the respective transmission asset owners with an expected completion date of 2025. | Mitigate the risk of power failures Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | The second North-South interconnector will enhance electricity supply security across Ireland, strengthen the grid, and support an integrated all-island system. It will benefit nearby communities and boost social and economic growth by increasing grid capacity. It will transport up to 1,250 MW of electricity, removing a major bottleneck or constraint at the border. Currently, only one interconnector exists, making the system vulnerable to power failures and limiting North-South flows to 300 MW. The increased capacity will also enable 900MW of constrained or yet to be connected renewable energy on the grid. This is essential to achieve our climate change targets and increase energy independence. The new interconnector will increase the capacity, and the reliability, of interconnection between the Ireland and Northern Ireland networks. This will allow the two independent networks to operate together as if they were one system for the mutual benefit of residents and businesses in both jurisdictions. |  |  | IE00-UKNI | 950 | 900
85 | Integration of RES in Alentejo | The main objective of this project consists in introducing the network reinforcements that are needed to allow the connection of new RES generation (mostly solar but also some wind) that is foreseen for the south region of Portugal, where the solar potential is considerably high. The project includes two new 400 kV OHL that will constitute a new axis between F. Alentejo-Panóias-Ourique-Tavira substations. It is also included the new Panóias substation and a new 400KV OHL Alqueva-Divor. | Rede Elétrica Nacional | PT | NDP 1, Portugal, Draft NDP 2022-2031 (2021); Main report, Page 13 (https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf); Apendix 11, page 5 (https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf) | 2024 | 4 | False | True | MostlyUpgrade | False |  | Clustering: the project consists of a new axis connecting Ferreira do Alentejo and Tavira substations, passing through intermediate substations (Panóias and Ourique). All these investments are in series so a lack of any of them will not allow to get the desired GTC increase of the project. Also a new 400 OHL Alqueva-Divor is included in this cluster in order to increase and allow the maximum utilization of the potential of the main investment. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | Portuguese National Development Plan: https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf; https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf Video: https://www.youtube.com/watch?v=RihzW55870c | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Previous IOSN editions showed high level of congestion in the network resulting from the integration of RES (mainly Solar) in the south of Portugal where the solar potential is considerably high Project for integration of RES (mainly Solar) |  |  | internaPT00 | 1000 | 1000
94 | GerPol Improvements | The new Phase Shifting Transformers (PST) in Mikulowa on the 400 KV double line Mikulowa–Hagenwerder were already finally commissioned in June 2016. The first two PST in Vierraden have been commissioned in August 2018. The updated 400 kV double line Krajnik – Vierraden is in operation with one system and these two PST in series. On the German side there is a link to the existing 220 kV lines using two 380/220 kV transformers as an intermediate step. Two further Phase Shifting Transformers (380 kV/380 kV) will replace these two 380/220 kV transformers in substation Vierraden after the upgrade of the existing German Uckermark-line to 380 kV. This necessary upgrade of the connecting Uckermark-line is delayed due to court case against the building permission. The court case has been settled in July 2022 and the upgrade of the Uckermark-line is proceeding. | 50Hertz | DE ;PL | German NEP2037_2045, version 2023, 2nd draft, Germany, 2023, project 128, p. 299-301, https://www.netzentwicklungsplan.de/sites/default/files/2023-06/NEP%20kompakt_2037_2045_V2023_2E_1.pdf; | 2025 | 4 | True | False | Upgrade | False |  |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | [5 empty] | DE00-PLI0 PLI0-PL00 | 500 500 | 1500 1500
107 | Celtic Interconnector | Celtic Interconnector will be the first interconnection between Ireland and France. A survey of the route of the HVDC (VSC) link with 700 MW capacity has been done from the southern coast of Ireland to La Martyre (Finistère) in France. Motivation for the project : The CELTIC project will improve security of supply in both Ireland and France. It will facilitate increased electricity trading that will result in increased competition and downward pressure on electricity prices. The CELTIC project will also support the development of renewable sources of energy. | Eirgrid, RTE | FR ;IE | NDP1 Transmission Development Plan, Ireland, 2021, 107, page 86, https://www.eirgridgroup.com/site-files/library/EirGrid/Transmission-Development-Plan-2021-2030.pdf - NDP2, France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, project n°437, page 442, https://www.rte-france.com/en/analyses-trends-and-perspectives/ten-year-network-development-plan#Documents | 2027 | 4 | True | False | New | True | 1.3 |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | More information can be found on Project Websites : https://www.rte-france.com/fr/projet/celtic-interconnector-projet-d-interconnexion-entre-la-france-et-l-irlande and http://www.eirgridgroup.com/the-grid/projects/celtic-interconnector/the-project/. The project is also part of both RTE and Eirgrid National Development plans. In addition, CELTIC as a Project of Common Interest 1.6 in the priority corridor Northern Seas Offshore Grid (NSOG)." | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Figures 2.9 and 2.10 of IoSN 2022 Report show that average marginal price difference would be higher than 10€/MWh between France and Ireland in future scenarios if no investment is done, and only between 5 and 10€/MWh with the investment. Based on IoSN 2022 Report, 15% IC-target requires higher cross border transmission capacity. This project P107 contributes to satisfy this need (especially for Ireland, by increasing the transmission capacity while the installed RES generation is going higher too). IoSN 2020 Report Chapter 5 (Flexibility aspect, Transient and voltage stability related aspects): the ramp increases from NT2025 to NT2040. The project allows Ireland to take benefits from the more stable continental grid, participates in reactive power management and frequency management by quickly changing its active power. IoSN 2020 Report, figures 2.8-2.11: main drivers of NT scenarios are better access to RES generation (avoiding curtailment) which replaces expensive thermal generation. Figures 2.2-2.3: in Ireland, curtailment decreases by half with the IoSN SEW needs in 2030 compared to 2020. Same for 2040 compared to 2025. | France - Ireland - 700 | France - Ireland - 700 - France - - 1000 - 5000 Ireland - - <1000 | FR00-IE00 | 700 | 700
111 | Aurora line (3rd AC Finland-Sweden north) | Third AC 400 kV overhead line interconnector between Finland north and Sweden SE1. Strengthening the AC connection between Finland and Sweden is necessary due to market needs, security of supply in the Nordics, new RES generation and larger conventional units. | Fingrid, Svenska Kraftnät | FI ;SE | Fingrid's Main grid development plan 2024-2033, available here: https://www.fingrid.fi/globalassets/dokumentit/fi/kantaverkko/kantaverkon-kehittaminen/fingrid_kehittamissuunnitelma_26_engb.pdf; System Development Plan 2022-2031, Sweden, 2021: Availble online: {https://www.svk.se/siteassets/om-oss/rapporter/2021/svk_systemutvecklingsplan_2022-2031.pdf} | 2025 | 4 | True | False | New | True | 3.4.1 and 3.4.2 | Investment 1710 is needed to get the full capacity of investment 396 | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | Wep page of the project: https://www.fingrid.fi/en/grid/construction/cross-border-connections/Aurora-Line-new-finland-sweden-interconnector/#41cebfa7 Svenska kraftnät has published a grid investment plan in 2021. The purpose of the plan is to be an investment plan for the following ten years, 2022-2031. The report is available as follows: System Development Plan 2022-2031, Sweden, 2021: Availble online: {https://www.svk.se/siteassets/om-oss/rapporter/2021/svk_systemutvecklingsplan_2022-2031.pdf} Fingrid's Main grid development plan 2024-2033, available here: https://www.fingrid.fi/globalassets/dokumentit/fi/kantaverkko/kantaverkon-kehittaminen/fingrid_kehittamissuunnitelma_26_engb.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | Adds market capacity 800/900 MW. Adds market capacity 800/900 MW. Contributes to all three interconnection targets. Improves Finnish power balance after Russia suspended electricity and gas delivery to Finland. Also strengthens the connection of Finland with the other Nordic countries. Strengthens the connection of Finland and Sweden and improves stability of the Nordic synchronous system. | Finland - Sweden - 1700 | Finland - Sweden - 2500 - | FI00-SE01 | 900 | 800
120 | Princess Elisabeth Island (MOG 2) | The Princess Elisabeth Island aims at centralizing the offshore wind farms in an offshore hub and transporting offshore energy to a substation along a new 380kV corridor Ventilus (project 329). The current working hypothesis supposes a total capacity of +-3,5 GW of offshore wind. An artificial island is planned in the Princess Elisabeth Zone defined in the Belgian Marine Spatial Plan 2020-2026. Project consists of offshore grid investments that allows to connect the new wave of offshore energy to the mainland (on top of the existing 2,3GW) in an efficient, reliable and future-proof way and strongly facilitates RES integration in Belgium. Belgian law, approved on 4th of April 2019 (DOC 54 3581/008), creates a legal framework for a second Modular Offshore Grid. Additional offshore (wind) capacity will be connected to the onshore grid partly via a HVDC and a AC system. Such a setup offers synergies with future (hybrid) interconnectors (eg. project 121 and 1092). | Elia | BE | NDP1, Belgium, 2024-2034, §4.2.1 | 2029 | 3 | False | True | New | False |  | Both investments will be jointly built an offshore energy hub and serve the same purpose of integrating the offshore energy to the mainland and facilitate potential future further integration offshore. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | More information can be found following these links: - Project site: https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/princess-elisabeth-island - National Development Plan: https://www.elia.be/en/infrastructure-and-projects/investment-plan/federal-development-plan-2024-2034 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | Creation of artificial energy island enabling connection to other countries around the North Sea. Creation of artificial energy island enabling connection to other countries around the North Sea. Integration of up to 3.5 GW of offshore wind through an artificial energy island. Integration of up to 3.5 GW of offshore wind through an artificial energy island. |  |  | internalBE00 | 1400 | 1400
121 | Nautilus: multi-purpose interconnector Belgium - UK | A multi-purpose HVDC interconnection between GB (Leiston) and BE (Princess Elisabeth Island) of 1,4 GW. The capacity of the HVDC link between the PEI and the onshore network in Belgium will be shared between Nautilus and a 1,4 GW offshore wind park located in the Belgian part of the North Sea. | Elia, National Grid | BE ;GB | NDP1, Belgium, 2024-2034, ID3, p126;NDP2, UK, 2017, p.23 §2.3 | 2030 | 2 | True | False | New | True | 4.5 |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | More information on the project can be found following these links: - Project site: https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/nautilus - National Development Plan Belgium: https://www.elia.be/nl/infrastructuur-en-projecten/investeringsplannen/federaal-ontwikkelingsplan-2024-2034 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project increases crossborder capacity between Belgium and the United Kingdom. Project increases crossborder capacity between Belgium and the United Kingdom. Project increases crossborder capacity between Belgium and the United Kingdom and as such is beneficial for both countries adequacy. Project increases crossborder capacity between Belgium and the United Kingdom, allowing renewable to be shared more efficiently. | Belgium - UK - 1400 | Belgium UK - 1400 - Belgium - - <1000 | BE00-UK00 | 1400 | 1400
124 | Ekhyddan-Nybro-Hemsjö | Second phase includes the internal network reinforcement in Sweden, a key investment to accomplish full utilization of the NordBalt cable between Lithuania and Sweden. The rest of internal investments already commissioned. | AST, Svenska Kraftnat, Litgrid AB | LT ;LV ;SE | System Development Plan 2022-2031, Sweden, 2021, p. 146 | 2027 | 3 | True | False | New | True | 4.4.2 | The investment Grobina (LV) - Imanta (LV) in Latvia is commissioned. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Svenska kraftnät has published a national development plan in 2021. The purpose of the plan is to be an investment plan for the following ten years, 2022-2031. The investment plan presents a detailed look of the projects Svenska kraftnät intends to realize under the stated time period. The plan is available in Swedish through the following link: https://www.svk.se/siteassets/om-oss/rapporter/2021/svk_systemutvecklingsplan_2022-2031.pdf (Swedish) |  |  |  |  | LT00-SE04 | 0 | 0
126 | SE North-south short-term reinforcements | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. | Svenska Kraftnät | SE | 10-Year Grid Investment Plan 2022-2031 , Sweden, 2021, p. 142. {Available online: https://www.svk.se/siteassets/om-oss/rapporter/2021/svk_systemutvecklingsplan_2022-2031.pdf} | 2035 | 2 | False | True | Upgrade | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | Svenska kraftnät has published a national development plan in 2021. The purpose of the plan is to be an investment plan for the following ten years, 2022-2031. The investment plan presents a detailed look of the projects Svenska kraftnät intends to realize under the stated time period. The plan is available in Swedish through the following link: https://www.svk.se/siteassets/om-oss/rapporter/2021/svk_systemutvecklingsplan_2022-2031.pdf (Swedish) |  |  |  |  | SE02-SE03 | 2000 | 2000
127 | Central Southern Italy | The project consists of the reinforcement of southern Italy's 400 kV network through new 400 kV lines. The activities will involve the network portions between the substations of Gissi and Foggia, Deliceto and Bisaccia as well as Laino and Altomonte. | Terna | IT | Piano di Sviluppo 2023 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Centro Sud, pag. 62 and 118, ID: 402-P and 505-P, https://www.terna.it/en/electric-system/grid/national-electricity-transmission-grid-development-plan | 2029 | 3 | False | True | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The new line will allow congestion reduction in the Southern-Northern border, and the integration of the local renewable production. In case of failure of the first OHL Foggia-Villanova the new line will improve transient stability. Reduction of expected RES curtailment |  |  | ITCS-ITS1 | 500 | 500
130 | HVDC SuedOstLink Wolmirstedt to area Isar | 2 GW HVDC-connection from North-East Germany (Area of Wolmirstedt), an area with high installed capacities of RES, to the South of Bavaria (area of Isar), an area with high consumption and connections to storage capabilities. | 50Hertz, TenneT DE | DE | NEP Strom 2037/2045 version 2023, Germany, 2023, Project DC5 (=P130), page 443 - 446 (German National Development Plan); https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_1.pdf | 2027 | 3 | False | True | New | True | 2.2 |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | Permitting status in the TYNDP reflects the fact, that the necessity of the project is approved by the NRA and is German Law (so called Bundesbedarfsplangesetz, listed as project No. 5). Therefore the realization is mandatory. In addition, according to German law, the permitting process has already started. http://www.gesetze-im-internet.de/bbplg/BBPlG.pdf (Page 4, Project Nr. 5) https://www.netzausbau.de/leitungsvorhaben/de.html?cms_map=2 German grid development plan: http://www.netzentwicklungsplan.de/en Project Homepage: http://www.50hertz.com/en/Grid-Extension/Projects/SuedOstLink https://www.tennet.eu/de/unser-netz/onshore-projekte-deutschland/suedostlink/ 3rd PCI-list: https://ec.europa.eu/energy/sites/ener/files/documents/annex_to_pci_list_final_2017_en.pdf 4th PCI-list: https://ec.europa.eu/energy/sites/ener/files/c_2019_7772_1_annex.pdf 5th PCI-list: https://energy.ec.europa.eu/system/files/2021-11/fifth_pci_list_19_november_2021_annex.pdf |  |  | Germany - Czech Republic - 1000 Austria - Germany - 3100 | Germany - Czech Republic - 1000 - Austria - Germany - 3100 - Germany - - 5000 - 10000 | DE00-PL00 DE00-CZ00 PL00-CZ00 internalDE00 | 500 200 250 2000 | 350 0 0 2000
132 | HVDC Line A-North | Project 132 consists of two new HVDC cable from Emden-East to Osterath. The HVDC has a transfer capacity of 2,4 GW. The project is a grid expansion project for low-loss transmission of high power over long distances from Northern Germany to the Rhineland. Northern Germany is characterized by a large number of regenerative onshore and offshore energy sources which exceed the demand of Northern German loads. The Rhineland, however, is a high-production region with large conventional generation capacity that has to be substituted by renewable generation capacity due to the German coal phase-out. | Amprion | DE | NDP, Germany, Netzentwicklungsplan 2037 Version 2023, Project DC1, p. 436 | 2027 | 3 | False | True | New | True | 1.4.1 |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | 5th PCI-List: https://ec.europa.eu/energy/sites/default/files/fifth_pci_list_19_november_2021_annex.pdf The project was part of the previous TYNDP 2022, Link to the Website: https://tyndp2022-project-platform.azurewebsites.net/projectsheets/transmission/132 Further information of the project, its investments and their necessity particularly for the German Energiewende can be found in the German grid development plan (mostly in German): http://www.netzentwicklungsplan.de/en/front Bundesbedarfsplan 2024 (BBPIG): https://www.netzausbau.de/Vorhaben/ansicht/de.html?cms_nummer=1&cms_gruppe=bbplg More detailed information can be found on the project website (in German): https://www.amprion.net/Netzausbau/Aktuelle-Projekte/A-Nord/ Link to the website of the project: https://a-nord.amprion.net/ Link tot he current NDP: https://www.netzentwicklungsplan.de/sites/default/files/2024-04/NEP_2037_2045_V2023_Anhang_2E_Aktualisierung_April_2024.pdf Add Link to the 6th PCI list: Delegated regulation - EU - 2024/1041 - EN - EUR-Lex (europa.eu) |  |  |  |  | DE00-BE00 DE00-NL00 internalDE00 | 600 2200 2400 | 250 600 2400
138 | Black Sea Corridor | The project consists of one 400kV double circuit OHL Cernavoda-Stalpu with in/out connection of one circuit in Gura Ialomitei, one 400 kV double circuit OHL Smardan-Gutinas in Romania and also the new 400 kV OHL Dobrujda-Burgas in Bulgaria. This project enables the transfer of production from the west coast of the Black Sea to the consumption and storage centers of Central and South-Eastern Europe. | ESO, Transelectrica | BG ;RO | Plan de Dezvoltare RET 2022-2031 (Transelectrica development plan 2022-2031), pages 78 and 85 - available at: https://www.transelectrica.ro/ro/web/tel/planul-de-dezvoltare-ret-2022-2031 | 2026 | 4 | False | True | MostlyNew | False |  | These investments are completely dependent on each other as the main enhancements in Romania and Bulgaria which remove bottlenecks and integrate RES to the network. Clustering of investments had the purpose to identify investments contributing to the increase of transfer capacity on the same corridor. Proposed Project supports market development in South East Europe which is less developed. Based on upper mentioned information it is crucial to cluster all these investment together, to fully utilize the possible benefits. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | [5 empty] | BG00-RO00 | 600 | 600
144 | Mid Continental East corridor | The project consists of one double circuit 400 kV interconnection line between Serbia and Romania and reinforcement of the network along the western border in Romania: one new simple circuit 400 kV line from Portile de Fier to Resita and upgrade from 220 kV double circuit to 400 kV double circuit of the axis between Resita and Arad, including upgrade to 400 kV of three substations along this path: Resita, Timisoara, Sacalaz. The main aim of this project is increasing the transmission capacity along the East-West corridor in the South-Eastern and Central Europe, simultaneously contributing to the market integration in the region of interest and enhancing the integration of large renewable sources in the Banat region, located in the close proximity of the Serbia-Romania and Hungary-Romania borders. Along with that, the commissioning of the project will strongly improve the security of supply in the mentioned area, thus fulfilling one of the primary postulates of the modern transmission systems' reliable operation. | EMS, Transelectrica | RO ;RS | Plan de Dezvoltare RET 2022-2031 (Transelectrica development plan 2022-2031), pages 78 and 85 - available at: https://www.transelectrica.ro/ro/web/tel/planul-de-dezvoltare-ret-2022-2031; Plan razvoja prenosnog sistema Republike Srbije za period 2019 - 2028, Serbia, 2019-2027, page 115 | 2029 | 3 | True | False | MostlyNew | False | 3.22 Cluster Romania-Serbia [currently known as "Mid Continental East corridor''] | This Project aims to enhance the transmission capacity along the East-West corridor in the South-Eastern and Central Europe. The investments are complementing each other as the main enhancements in Romania which remove bottlenecks and integrate RES to the network. Clustering of investments had the purpose to identify investments contributing to the increase of transfer capacity on the same corridor. Based on upper mentioned information it is crucial to cluster all these investments together, to utilize the possible benefits. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | On the fifth PCI list are included the following investments: PCI 3.22.1 Interconnection between Resita (RO) and Pancevo (RS) PCI 3.22.2 Internal line between Portile de Fier and Resita (RO) PCI 3.22.3 Internal line between Resita and Timisoara/Sacalaz (RO) PCI 3.22.4 Internal line between Arad and Timisoara/Sacalaz (RO) http://www.transelectrica.ro/web/tel/proiecte-de-interes-comun | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | The increase of transfer capacity at the boundary between Romania and Serbia will support the large scale integration of RES (the curtailed energy will decrease) | Romania - Serbia - 844 | Serbia - Romania - 1524 - | RO00-RS00 HU00-RO00 | 844 617 | 600 335
150 | Italy-Slovenia | The project is about a new HVDC link between Salgareda (Italy) and Divaca (Slovenia) which will strengthen the connection between Slovenia and Italy. On Italian side the project is under authorization since 2012 and the permitting process is now close to the conclusion. On Slovenian side the project is under consideration. ELES has performed a study based on TYNDP 2020 from the perspective of the Slovenian System, which determined that most of the benefits start arising from 2040 onwards, leading to the conclusion that its implementation should be planned accordingly. Terna and ELES will continue evaluating options for increasing NTC up to 1000 MW between Slovenia and Italy in the new TYNDP scenarios considering various solutions: • reinforcement of existing grid (PSTs, upgrade of existing lines) • HVDC link | Eles, Terna | IT ;SI | Piano di Sviluppo 2023 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Est (pag.92) - https://download.terna.it/terna/Terna_PdS_2023_Avanzamento_Piani_Sviluppo_Precedenti_Avanzamento_Nord_Est_8db254a9ec58dd8.pdf/Pag.190, Italy | 2042 | 1 | True | False | MostlyNew | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Slovenian NDP (only in slovenian): https://www.eles.si/Portals/EN/Documents/EN/ELES_development_plan_2023-2032.pdf?ver=2023-06-16-154317-607 Italian Development Plan: https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete https://download.terna.it/terna/Terna_PdS_2023_Avanzamento_Piani_Sviluppo_Precedenti_Avanzamento_Nord_Est_8db254a9ec58dd8.pdf/Pag.190, Italy | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian and Slovenia market zones. This project will contribute to overcome flexibility/stability problems due to scarcely meshed grid. This project will improve the integration of Italian RES generation. | Italy - Slovenia - 125 | Italy - Slovenia - 125 - Italy - - 1000 - 5000 | ITN1-SI00 | 400 | 400
153 | France-Alderney-Britain | France-Alderney-Britain (FAB) is a new HVDC subsea interconnector between Exeter (UK) and Menuel (France) with 1,25 GW capacity. Motivation for the project : The project has as its main objectives to increase the interconnection capacity between France and Great Britain, to answer the market needs, to integrate additional RES generation and to improve security of supply. | FABLINK Limited, Rte | FR ;GB | NDP1, UK, n°153, 2017 , page 21 - NDP2, France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°127, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2031 | 3 | True | False | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | More information related to the project can be found on internet platforms : http://www.fablink.net and https://www.rte-france.com/fr/projet/interconnexion-france-aurigny-grande-bretagne-fab. The project is also part of both System Operator National Development Plans. In addition, FAB project has been confirmed on 31st of October 2019 as Project of Common Interest 1.7.1 in the priority corridor Northern Seas Offshore Grid (NSOG). | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | FAB will provide cross border capacity facilitating further access between French and GB markets thereby converging GB and French prices. Entsoe has identified a need for an additional 4800 MW of interco FR-UK over the 4000 MW currently. FAB contributes to this objective and to the reduction of price differentials and to reach the 15% interconnection target for 2030. The GB and French generation mixes are fundamentally different and both are forecast to undergo significant change over the assessment period. FAB will provide further capacity between these two markets enhancing security of supply and reducing the risk of power failures. With increasing levels of RES forecast for both France and GB, FAB will support the integration and provide these generators access to wider markets thereby reducing the chance of curtailing these carbonized sources of power. | France - UK - 4800 | France - UK - 4800 - France - - <1000 | FR00-UK00 | 1250 | 1250
170 | Baltic States Synchronization with Continental Europe | Goal of the project is to prepare Baltic states electrical networks for synchronous operation with Continental Europe. Synchronization of the Baltic States with the CESA will take place by modification of the existing connection between Lithuania and Poland (LitPol Link), and a new HVAC land cable (Harmony Link). Internal electricity transmission grids of the Baltic States and Poland will also be strengthened, the system will be ready for disconnection from the IPS / UPS system and for independent frequency control, and synchronous condensers will be installed. As part of the project, a new HVAC connection will be established between LT-PL (investment No. 1034) allowing for a commercial exchange of the Baltic States with Continental Europe in the amount of 700 MW. | AST, Elering, Litgrid AB, Polskie Sieci Elektroenergetyczne S.A. | EE ;LT ;LV ;PL | Lithuania: "Development plan of the electric power system and transmission grid. 2021-2030" (https://www.litgrid.eu/uploads/files/dir580/dir29/dir1/10_0.php), June 2021, pages 22, 40-43. Estonia: NDP (https://elering.ee/sites/default/files/public/VKA2020.pdf) pages 41-42; Latvia: NDP "The Power Transmission System Development Plan 2022-2031", approved by resolution of the Public Utilities Commission Council of 21 October 2020, Annex 3. Poland: "Development Plan for meeting the current and future electricity demand for 2021-2030", Poland, Year 2020, Project II.88, II.26, II.27, II.28, II.29, II.34, II.35, II.36, Page 42, https://www.pse.pl/documents/31287/84e7121a-e0c0-4dee-ab2c-61bba30f4646?safeargs=646f776e6c6f61643d74727565. | 2030 | 2 | True | False | MostlyNew | True | 3.3.1, 3.3.2, 3.3.3, 3.3.4, 3.3.5, 3.3.6, 3.3.7, 3.3.8, 3.3.9, 3.3.10, 3.3.11, 3.3.12, 3.3.13, 3.3.1 | After desynchronisation of Baltic States from Russia and Belarus electricity networks, electricity system in Baltic States should be ready for reliable and secure operation having one synchronous double-circuit 400 kV AC line on border with Poland. This goal could be achievable only when eliminating all negative contingency (n-1) factors and eliminating internal bottlenecks in Baltics and Poland. All investments in this project serves one or another goal from above. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | https://www.litgrid.eu/index.php/synchronisation/synchronisation/31363 https://www.ast.lv/en/projects/synchronisation-europe | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to allow by 2025 for the synchronisation of the Baltic States with the rest of the EU network Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | Harmony Link will increase NTC between Lithuania and Poland. Investments are essential part to be able to synchronize Baltics with Continental Europe synchronous area. Nine synchronous compensators will be added in the system which will significantly improve RoCof. Without additional measures RoCof would increase over acceptable level. | Lithuania - Poland - 700 | Latvia - - <1000 Estonia - - <1000 Lithuania - Poland - 700 - Poland - - <1000602 | LT00-PL00 | 700 | 700
174 | Greenconnector | Greenconnector is an HVDC interconnector project between Italy and Switzerland for power transport using DC cables rather than overhead lines. The route length is about 165 km. The design power is 1000 MW (1200 MW in overload condition), while the DC voltage is +/- 400 kV DC. Two cables will be installed, working with a bipolar scheme. Great part of the cables route will exploit a section of an existing oil pipeline, no longer in service since January 1997. This pipeline crosses the Italian and Switzerland border at Splügenpass and is running close by the two end stations of the Greenconnector project (Bonaduz in Graubunden Canton and Verderio, Lecco). The cables will be pulled inside the pipeline itself, reducing the amount of civil works required before and after cable laying and therefore limiting even temporary environmental impact. For about 47 km the cables will run across the Como lake. The selected technology and voltage level make it possible to build a very efficient interconnector with very low losses. | Worldenergy SA | CH ;IT | Terna Piano di Sviluppo della Rete 2023, Italy, The Hypergrid Project, page 50, figure 23: "Interconnection projects planned and developed by third parties - details", url: https://download.terna.it/terna/Terna_Piano_Sviluppo_2023_Progetto_Hypergrid_necessit%C3%A0_Sviluppo_infrastrutturale_8db2549ed056bf0.pdf | 2029 | 3 | True | False | New | False | 2.14 |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | Project website: www.greenconnector.it The Greenconnector project has been selected by the Renewables Grid Initiative "Good Practice of the Year" award jury as one of the favourite practices in the "Environmental Protection" category. As a relevant and applaudable practice, Greenconnector appears in the award brochure that has been presented at the award ceremony at the European Energy Infrastructure Forum in Copenhagen on June 1, 2017. |  |  | Italy - Switzerland - 200 | Italy - Switzerland - 2200 - Italy - - 1000 - 5000 Switzerland - - <1000 | CH00-ITN1 | 1000 | 1000
176 | Hansa PowerBridge I | New HVDC interconnector between Sweden (SE4) and Germany (50Hertz, Continental) aiming to enhance the integration of the Nordic and the continental power market. Moreover the interconnector facilitates RES integration and increases the system adequacy in both systems. | 50Hertz, Svenska kraftnät | DE ;SE | German NEP2037_2045, version 2023, 2nd draft, Germany, 2023, project P221, p. 329-332, https://www.netzentwicklungsplan.de/sites/default/files/2023-06/NEP%20kompakt_2037_2045_V2023_2E_1.pdf; Systemutvecklingsplan 2022-2031, Sweden, 2021, p.141, https://www.svk.se/siteassets/om-oss/rapporter/2021/svk_systemutvecklingsplan_2022-2031.pdf | 2029 | 3 | True | False | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | The last version of the German national development plan with the project No. 176 was published in 2023 und is available under the following link: https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_1.pdf , page 329-332 Svenska kraftnät has published a national development plan in 2021. The purpose of the plan is to be an investment plan for the following ten years, 2022-2031. The investment plan presents a detailed look of the projects Svenska kraftnät intends to realize under the stated time period. The plan is available in Swedish through the following link: https://www.svk.se/siteassets/om-oss/rapporter/2021/svk_systemutvecklingsplan_2022-2031.pdf (Swedish) |  |  | Germany - Sweden - 1400 | Germany - Sweden - 2900 - Germany - - 5000 -10000 | DE00-SE04 | 700 | 700 | On 13 June 2024, the Swedish government decided to reject Svenska kraftnät's application for a concession for the Hansa PowerBridge 1 project. With this, Svenska kraftnät has ended the project.
187 | St. Peter (AT) - Pleinting (DE) | Increase of the cross border transmission capacity by erecting a new 380kV line between St. Peter (Austria) and Pleinting (Germany). This leads to an improved connection of the very high amount of RES in Germany and the pump storages in the Austrian Alps. | Austrian Power Grid, TenneT DE | AT ;DE | DE:NEP2037, Germany, v2023 P 112, p. 529 ff; https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_onshore.pdf.; APG Netzentwicklungsplan 2021, AT, 2021, 11-7, 58, https://www.apg.at/de/Stromnetz/Netzentwicklung | 2030 | 3 | True | False | New | True | 2.1.4 |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | This project is highly connected to and partly based on TYNDP 2016 Project 47/Investment 212. German grid development plan: https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_onshore.pdf Austrian National development plan: http://www.apg.at/en/netz/netzausbau/Netzentwicklungsplan Austrian Project homepage Austria: https://www.apg.at/en/projekte/380-kv-deutschland-leitung | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | helps to reach 15% target in Germany high RES generation connected to pump storage high RES generation connected to pump storage | Austria - Germany - 3100 | Austria - Germany - 3100 - Germany - - 5000 - 10000 Austria - - <1000 | AT00-DE00 | 2500 | 2500
200 | CZ Northwest-South corridor | A corridor of internal 400 kV overhead lines inside the Czech Republic connecting new 420 kV substations between Vernerov, Vitkov and existing substation Prestice (OHL Prestice - Vitkov was already commissioned in 2021) in the northwest-south direction. The project consists building of two 400 kV overhead lines involving changing a 220 kV double-circuit lines to 400 kV double-circuit lines with a capacity of 2 x 2445 A each between Vernerov and Vitkov and Vitkov and Prestice. Part of the project is also a construction of a new 420 kV substation Vitkov (already commissioned in 2020) and upgrading and extension of the existing 420 kV substation Kocin (phase 1 was already commissioned). | CEPS | CZ | Ten-year investment plan for the development of the TS 2021 – 2030, CZ, 2021, V487/488–Line Doubling, 87 pg., https://www.ceps.cz/en/transmission-system-development | 2024 | 5 | False | True | MostlyNew | True | 2.3.1 | Project 200 that contains investment item 308 (item 309 was already commissioned) altogether with project 35 that contains investment items 313 and 315 forms a geographically continuous (uninterrupted) network corridor from a new 420 kV substation Vernerov (already commissioned at the end of 2017), through a new 420 kV substation Vitkov (which is also already commissioned at the end of 2020), existing 420 kV substation Prestice, existing 420 kV substation Kocin and ending up to the existing substation 420 kV Mirovka. It is actually what is referred as a “convoy lines” or "sequential projects" with all 4 involved 400 kV overhead lines (investment 308 (Vernerov-Vitkov), 309 (Vitkov-Prestice), 315 (Prestice-Kocin) and 313 (Kocin-Mirovka)) connected in series forming a corridor from the northern-western part of the Czech grid related to the DE-CZ border into the south and eastern direction towards the CZ-SK and CZ-AT borders. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | Information about Czech development plan and PCI projects can be found on the following links below on the CEPS website: https://www.ceps.cz/en/transmission-system-development https://www.ceps.cz/en/pci-projects-of-common-interest |  |  |  |  | CZ00-DE00 | 500 | 500
210 | Würmlach (AT) - Somplago (IT) interconnection | Somplago - Würmlach interconnection is a cross-border electrical line promoted by Alpe Adria Energia Srl. The project concerns a 220kV a.c. merchant line, about 300 MW thermal capacity from Somplago substation to new Würmlach substation, including Phase Shifter Transformer located in Austria. | Alpe Adria Energia Srl | AT ;IT | The Austrian NRA, E-Control, issued the NDP 2023 (consultation phase) in which the project is included at page 41, 117, https://pb1-medien.apg.at/im/dl/pboxx-pixelboxx-21991/APGNetzentwicklungsplan2023-Konsultationsversion.pdf. National Development Plan 2023 by Terna, Italy, The Hypergrid project and development requirements page # 50 https://download.terna.it/terna/2023_Hypergrid_project_and_development_requirements_8db79602cedc732.pdf; Resolution of the Italian ANR - ARERA - with which the Somplago - Würmlach project is considered an integral and priority part of the National Development Plan (Ref. 335/2022/I/EEL - https://www.arera.it/allegati/docs/22/335-22.pdf). | 2029 | 3 | True | False | New | True | 2.4 |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | Web site: https://corporate.enel.it/en/stories/a/2017/01/alpe-adria-energia | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project will increase the cross-border capacity between the interconnected Countries and will allow market exchanges which lead to a minimising price differentials of the Italian border also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios with a different generation mix . In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems involved by the line. This cross border project allows higher flows in the meshed AC-grid and consequentially it allows better integration of RES in the interconnected Countries. | Austria - Italy - 500 | Austria - Italy - 1000 - Italy - - 1000 - 5000 Austria - - <1000 | AT00-ITN1 | 150 | 150
219 | Great Sea Interconnector | The Great Sea Interconnector PCI 2.6 is a multi-terminal VSC-HVDC scheme of 1000 MW which will connect the transmission networks of Greece (Crete), Cyprus and Israel, and will comprise two converter stations with sea-electrodes, interconnected by HVDC cable systems. Its total offshore length is 1208 km (310 km CY-IL, 898 km CY–Crete) while its onshore length is 25 km. The cables will be laid at a max. water depth of 2200 m between IL and CY and 3000 m between CY and CR. The Great Sea Interconnector is a European Project of Common Interest (PCI) since 2013 listed in the ‘NSI East Electricity’ priority corridor. It is defined as a cluster PCI 2.6 on the 1st Union PCI/PMI list (3.10 on the fifth PCI list) consisting of the following PCIs: • PCI 2.6.1 – Interconnection Hadera (IL) - Kofinou (CY) • PCI 2.6.2 – Interconnection Kofinou (CY) - Korakia, Crete (EL) The project will end the energy isolation of Cyprus (the last isolated EU member), ensure security of supply and enable further RES penetration in all countries involved. | IPTO | CY ;GR ;IL | Title of the document: “ΔΕΚΑΕΤΕΣ ΠΡΟΓΡΑΜΜΑ ΑΝΑΠΤΥΞΗΣ ΣΥΣΤΗΜΑΤΟΣ ΜΕΤΑΦΟΡΑΣ 2023-2032” Country: Greece Year: 2023 Page number: 55 TSO: IPTO url: https://www.admie.gr/sites/default/files/users/dssas/DPA%202023-2032/%CE%94%CE%A0%CE%91%202023-2032%20%CE%9A%CF%8D%CF%81%CE%B9%CE%BF%20%CE%A4%CE%B5%CF%8D%CF%87%CE%BF%CF%82.pdf Title of the document: “ΔΕΚΑΕΤΕΣ ΠΡΟΓΡΑΜΜΑ ΑΝΑΠΤΥΞΗΣ ΣΥΣΤΗΜΑΤΟΣ ΜΕΤΑΦΟΡΑΣ 2023-2032” Country: Cyprus Year: 2023 Page number: 13 TSO: TSOC url: https://tsoc.org.cy/files/electrical-system/tydplan/%CE%94%CE%A0%CE%91%CE%A3%CE%9C%202023-2032web.pdf | 2029 | 4 | True | False | New | True | 2.6.1 and 2.6.2 | The projects have been clustered for more efficient procedures regarding licencing since it involves three countries | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | https://www.great-sea-interconnector.com/en | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to offer more supply options to isolated areas Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project will connect Cyprus to the continental electricity network allowing for energy imports / exports and trading, ensuring security of supply and rendering the wholesale electricity prices lower and more competitive The project will, end the energy isolation of Cyprus as the last isolated EU member, contribute to the 15% interconnection target of EU members, boost competition, reduce the cost of energy and ensure security of energy supply for the involved countries and the EU The project will effectively link Cyprus with the continental EU power markets, ending Cyprus’s energy isolation (currently Cyprus is the only Member State that is not interconnected with other European Member) States), enhancing security of supply and reducing the cost of energy The project will allow the further exploitation of RES potential and limit future curtailments in the countries involved. Especially for Cyprus, it will enable the realization of ambitious RES penetration targets, creating the conditions for full decarbonisation of the energy system, which is not realistically possible under autonomous operation. | Cyprus - Greece (Crete) - 1000 Cyprus - Israel - 1000 | Cyprus - Greece (Crete) - 1000 - Cyprus - Israel - 1000 - Cyprus - - <1000 | CY00-GR03 CY00-IL00 | 1000 1000 | 1000 1000
225 | 2nd interconnector Belgium - Germany | This project considers the possibility of a second HVDC interconnection between Belgium and Germany with a capacity of 1 or 2 GW and a commissioning by 2037 or as soon as possible thereafter. The timing as well as location, routing and capacity are subject to further bilateral studies. Project motivation: In the past, various studies have already been carried out at national and European level. The results of those studies so far show that a second interconnector has the potential to create socio-economic welfare for both Belgium and Germany and in extension the entire European network. Furthermore, it facilitates RES integration in as well as CO2 savings. Moreover, an increased cross-border interconnection capacity may allow for a further integration of the domestic electricity sector in the European energy market, thus driving electricity price convergence between European domestic markets. | Amprion, Elia | BE ;DE | NDP1, Belgium, 2024-2034, ID 10, p136; NDP2, Germany, Netzentwicklungsplan 2037 Version 2023, Project 313, p. 641 | 2037 | 1 | True | False | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | More information about the project can be found following this link: - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en The project was part of the previous TYNDP 2020, Link to the Website: https://tyndp2020-project-platform.azurewebsites.net/projectsheets/transmission/225 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project increases crossborder capacity between Belgium and Germany. The project increases crossborder capacity between Belgium and Germany. The project increases crossborder capacity between Belgium and Germany and as such support the adequacy of both countries. The project increases crossborder capacity between Belgium and Germany allowing the better integration of renewables. | Belgium - Luxemburg - 500 Germany - Luxemburg - 400 | Belgium - Luxemburg - 500 - Germany - luxemburg - 400 - Belgium - - <1000 Germany - - 5000 - 10000 | BE00-DE00 | 2000 | 2000
227 | Transbalkan Corridor | The remaining sections of the project contain six investments, with the new corridor spanning from Western Serbia (SS Obrenovac and SS Bajina Basta) all the way to SS Visegrad in Bosnia and Herzegovina and SS Lastva (across SS Pljevlja 2) in Montenegro. As can be seen from the brief list of the investments, the project aims to increase both the transmission capacity within Serbian transmission system and the transfer capacities on the borders between the mentioned countries. Thus, it is expected that it will largely facilitate the energy exchange between the north-east and south-west parts of Europe, setting a foundation for the enhanced market integration and leveling of the marginal energy costs and guaranteeing the security of supply throughout the region. It will also be essential for connecting new PSHPP Bistrica, one of the most important planned flexibility sources in the entire region, to the grid. This project is tightly connected to the project 28 (Italy - Montenegro) and the project 342 (Central Balkan Corridor). | EMS, NOS-BIH, CGES | BA ;ME ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2021 - 2030 (JSC EMS Development Plan 2021-2030), page 121, available at: https://ems.rs/wp-content/uploads/2022/07/Plan-razvoja-prenosnog-sistema-2.pdf; PREDLOG AŽURIRANOG PLANA RAZVOJA PRENOSNOG SISTEMA 2020-2029 (CGES Development Plan), page 150, available at: https://www.cges.me/regulativa/razvoj-sistema; Indikativni plan razvoja proizvodnje 2024-2033 (NOS BiH), page 56, available at: https://www.nosbih.ba/files/2023/09/20230914-lat-Indikativni-plan-razvoja-proizvodnje-2024-2033.pdf. | 2027 | 3 | True | False | MostlyNew | False |  | These investments will form new HV AC and DC corridor from Serbia, through Montenegro to Italy (with project 28), enhancing energy exchange and further market integration in SEE region. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project significantly aids the energy market integration, set as one of the top priorities of the European grid development, and, as such, massively helps the process of equalizing the marginal energy prices in the EU and non-EU countries, which is particularly relevant for the CSE region. As the power lines in the Western Serbia are rather old and should be decommissioned due to their age, this project will provide an alternative for them, resolving, among other benefits, the issues related to security of supply, becoming increasingly important with the growth of load in this region. This project will contribute to the parameters of system stability in two ways - by increasing the NTC values and enabling the larger cross-border energy trades, and by allowing the connection of new PSHPP Bistrica to the grid, foreseen as the large flexibility source in this region. Even though the impact that this project may have on the connection of RES, the Drina river, located near the foreseen paths of OHLs included in the project, offers significant additional potential for energy generation in hydro capacities, thus amplifying the importance of Transbalkan corridor for this system need. | Montenegro - Serbia - 840 Bosnia-Herzegovina - Serbia - 2310 | Montenegro - Serbia - 840 - Bosnia-Herzegovina - Serbia - 1200 - | BA00-RS00 ME00-RS00 | 1200 240 | 1200 840
228 | Muhlbach - Eichstetten | Reinforcement of the existing 400kV OHL and deployment of a second 400kV circuit at existing double circuit OHL Muhlbach - Eichstetten, instead of the currently operated circuit Eichstetten - Vogelgrun (currently operated with 225kV). The project includes also a transformer in Sierentz substation to balance flows between 225kV and 400kV grid in the area. Motivation for the project: Germany and the Continental Central South-Region is characterised by a significant increase in RES generation. The grid has to be developed in order to support these new exchange possibilities, facilitating the access to the most economic energy mix, while minimising grid congestions. High flows in both directions West-East and North-South are expected. By increasing of interconnection capacity, the project strengthens the European electricity market and contributes to the security of supply. | Rte, TransnetBW | DE ;FR | German NDP: Netzentwicklungsplan Strom 2037/2045 Version 2023, Germany, Project No.176, p.428; https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_1.pdf | 12-2027 | 3 | True | False | Upgrade | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | German National Development Plan 2037/2045 Version 2023: https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_1.pdf French National Development Plan: SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, France, project No. 880, page 442, https://www.rte-france.com/en/analyses-trends-and-perspectives/ten-year-network-development-plan#Documents Bundesbedarfsplan 2021 (Germany): https://www.netzausbau.de/Vorhaben/ansicht/de.html?cms_nummer=72&cms_gruppe=bbplg http://www.gesetze-im-internet.de/bbplg/BJNR254310013BJNE000605377.html Project specific websites: TransnetBW: https://www.transnetbw.de/de/netzentwicklung/projekte/eichstetten-bundesgrenze-frankreich/projektueberblick | Infrastructure to reduce price differentials between EU and/or non-EU countries Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL-BE-LU-FR-DE Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Although this is not the main driver for this project, increase the interconnectivity between the German and French bidding zone give the possibility of higher market exchanges between these two bidding zones leading to a higher price convergence in more hours of the year. Flows on 380kV OHL could be adjusted with both PSTs installed in Muhlbach substation rather than current 220kV interconnector. France and Germany face decreasing figures of installed conventionals due to reduction or phaseout of nuclear and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE region. Rising figures of RES capacities especially in Germany lead to increasing RES-curtailment in the coming decades. This interconnector project allows a higher export in hours of high RES infeed particularly in Western Germany. |  |  | DE00-FR00 | 300 | 300
231 | Beznau - Tiengen | This project comprises the upgrade of a 220 kV crossborder line to 380 kV between the substations of Tiengen (DE) and Beznau (CH). | Amprion, Swissgrid | CH ;DE | NDP Germany, Netzentwicklungsplan 2037 Version 2023, Project P204 | 2035 | 2 | True | False | Upgrade | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2.pdf The project was part of the previous TYNDP 2022, Link to the Website: https://tyndp2022-project-platform.azurewebsites.net/projectsheets/transmission/231 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the price differentials between Switzerland, Germany and Austria. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | Germany - Switzerland - 1550 | Germany - Switzerland - 1550 - Germany - - 5000 - 10000 Switzerland - - <1000 | CH00-DE00 | 100 | 600
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | 4 GW HVDC connection from Northern Germany (areas of Brunsbüttel/Wilster) to Bavaria / Baden-Württemberg (areas of Großgartach/ Bergrheinfeld West). Northern Germany is characterised by a high amount of RES, the feed-in exceeds the local load and therefore there is a high demand for electricity transfer to the load centres in southern parts of Germany. With the further installation of additional renewable energy, the relevance of this project increases. | TransnetBW, Tennet DE | DE | German NDP: Netzentwicklungsplan Strom 2035/2045 Version 2023, Germany, Project No. DC3/DC4, p.440; https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_1.pdf | 2028 | 3 | False | True | New | True | 1.5 |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | German Network Development Plan 2037/2045 Version 2023: https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_1.pdf 3rd PCI-list: https://ec.europa.eu/energy/sites/ener/files/documents/annex_to_pci_list_final_2017_en.pdf 4th PCI-List: https://ec.europa.eu/energy/sites/ener/files/c_2019_7772_1_annex.pdf 5th PCI-List: https://eur-lex.europa.eu/legal-content/EN/TXT/?uri=CELEX%3A32022R0564&qid=1663087079030 Bundesbedarfsplan 2021: https://www.netzausbau.de/Vorhaben/ansicht/de.html?cms_nummer=3&cms_gruppe=bbplg http://www.gesetze-im-internet.de/bbplg/BJNR254310013BJNE000605377.html Project specific websites: TransnetBW: https://www.suedlink.com/ TenneT DE: https://www.tennet.eu/de/de/projekte/suedlink Video: https://www.youtube.com/watch?v=gk8d-K_39uo | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | In critical grid situations, costly congestion management measures are taken to avoid overload of grid elements. The project will reduce the demand for re-dispatching, countertrading and curtailment of renewable energy producers by adding significant transmission capacity between the congested routes in the North-Western part of Germany Reducing the redispatch leading to more flexibility and increasing the stability of the system. The project enables the integration of offshore and onshore wind energy by preventing potential bottlenecks in northern and southern Germany. |  |  | DE00-DKW DE00-NL00 internalDE00 | 0 2250 4000 | 1150 50 4000
239 | Fenno-Skan 3 | Replacement of the existing 400 kV HVDC cable interconnection between Finland and Sweden. Fenno-Skan 1 will be decomissioned and a new interconnector with the capacity of 800 MW will be built between FI and SE3, resulting in a total capacity of 1600 MW between FI and SE3. Previously (in TYNDP2020) this project was planned between FI and SE2, and now it has been changed to be situated between FI and SE3. According to new studies, this location provides more market benefits. The first decision depended also on the first simulation results that showed the complexities of connection between FI and SE3. However, these complexities were not observed in the updated simulations. The project is a point-to-point HVDC connection, but could possibly be extended in the future to become a hybrid connection. | Fingrid, Svenska Kraftnät | FI ;SE | Not yet included | 2038 | 1 | True | False | Upgrade | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | The concept is discussed for example in Fingrid's Electricity system vision report: https://www.fingrid.fi/globalassets/dokumentit/en/news/electricity-market/2023/fingrid_electricity_system_vision_2023.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | Adds market capacity 800 MW. Adds market capacity 800 MW. Contributes to all three interconnection targets. Improves local power balance and mitigates risk of power failures in Sweden and Finland. Improves system stability both in Sweden and Finland and Nordic synchronous area. | Finland - Sweden - 1700 | Finland - Sweden - 2500 - | FI00-SE03 | 400 | 400
243 | New 400 kV interconnection line between Serbia and Croatia | Construction of new 400 kV interconnection line SS Sombor 3 (RS) - SS Ernestinovo (HR), expected to provide a significant asset in terms of increasing the NTC between Serbia and Croatia, hence allowing the more prominent energy flow in the East-West direction across the CSE region, improving the market integration among the beneficiary countries and further ensuring the security of supply primarily in Serbia and Croatia, but, under certain circumstances, contributing to the reliable functioning of the systems in the rest of the countries in the region as well. Alongside that, it should be mentioned that the project will have a rather positive impact related to the possibility of integration of renewable energy sources in the Backa region. | EMS, HOPS | HR ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2021 - 2030 (Serbian national TYNDP 2021-2030), page 150 - available at: https://ems.rs/wp-content/uploads/2022/07/Plan-razvoja-prenosnog-sistema-2.pdf; Desetogodišnji plan razvoja prijenosne mreže 2022-2031(Croatian NDP 2022-2031), page 80 - avalable at: http://hops.hr/page-file/bsAQ9AhqCaU33Auv0GyGe5/92136ad3-dfa8-4674-b6aa-3c7a0d41654c/HOPS%2010G%20plan%20razvoja%202022%20-%202031%20web.pdf | 2038 | 1 | True | False | New | False |  | There is only one investment, so there are no clustering issues. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Since this interconnection means the increase of NTC between Croatia (EU country) and Serbia (non-EU country), it is seen by promoters as a mean of reaching the defined market integration goals and consequently reducing the price differentials in the Continental Southeast Europe area. As nearly all of the scenarios foreseen for the future period predict rather high energy flow across almost all borders in the CSE region, each of the new interconnections in this area can be seen as an additional step towards vouching for the timely reaching of the set goal. In the conditions of ever higher needs for the intensive cooperation between the neighboring TSOs, every new interconnection, such as the one included in this project, can be seen as the new and valuable asset that will aid in the improvement of systems' flexibility and reliability of operation. According to the currently available information, the Bačka region in Northern Serbia is predicted to host several wind power plants of sustainable installed capacity (exceeding 1 GW), with new line between SS Sombor 3 and SS Ernestinovo ensuring the uninterrupted and secure evacuation of the produced energy. | Croatia - Serbia - 1600 | Croatia - Serbia - 1600 - Croatia - - <1000 | HR00-RS00 | 746 | 306
244 | Vigy - Uchtelfangen area | An upgrade of the existing over headline between the substations Ensdorf, Uchtelfangen and Vigy is planned to increase the thermal cross-border capacity. For this reinforcement the options are either the implementation of High Temperature Low Sag (HTLS) conductors. To allow an optimal use of the capacity increase the installation of phase shifter transformers (PSTs) is necessary. For these measures the substations have to be adjusted accordingly. Motivation for the project : Germany and also the CCS-Region is characterised by a significant increase in RES generation. The grid has to be developed in order to support these new exchange possibilities, facilitating the access to the most economic energy mix, while minimising grid congestions. High flows in both directions West-East and North-South are expected. The project strengthens the European single market. This project increases the interconnector capacity between France and Germany and therefore also the security of supply. | Amprion, Rte | DE ;FR | NEP2037(2023)- Project P314 https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2.pdf - NDP2; France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, project n°444, page 442, https://www.rte-france.com/en/analyses-trends-and-perspectives/ten-year-network-development-plan#Documents | 12-2029 | 3 | True | False | MostlyUpgrade | False |  | The two investments are for us two parts of the same project to contribute together to the increase of exchange capacity between France and Germany. For some historical reasons (different commissioning date, more clarification on the description of the project) they have been described with separate IDs . With our current overview on the project (two investments on the same elements of the grid with close commissioning dates), both RTE and Amprion consider them as two steps of the same project with no need to assess them separately. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | The project was part of the previous TYNDP 2022, Link to the Website: https://tyndp2022-project-platform.azurewebsites.net/projectsheets/transmission/244 Considering the border France-Germany, the expected increase of capacity of project 244 in both direction could be fully available as soon as PSTs in the area are optimized. https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL-BE-LU-FR-DE Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Although this is not the main driver for this project, increasing the interconnectivity between the German and French bidding zone gives the possibility of higher market exchanges between these two bidding zones leading to a higher price convergence in more hours of the year. RES infeed in the north of Germany often bypasses via Netherlands, Belgium and France. The project allows a better limitation of these loop flows via new PSTs on the French-German border. France and Germany face decreasing figures of installed conventionals due to reduction or phaseout of nuclear and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE region. Rising figures of RES capacities especially in Germany lead to increasing RES-curtailment in the coming decades. This interconnector project allows a higher export in hours of high RES infeed particularly in Western Germany. | France - Germany - 1500 | France - Germany - 1500 - France - - 1000 - 5000 Germany - - 5000 - 10000 | DE00-FR00 | 1500 | 1500
247 | AQUIND Interconnector | AQUIND Interconnector is a proposed High Voltage Direct Current (HVDC) subsea and underground electric power transmission link between Great Britain (Lovedean substation, Hampshire) and France (Barnabos switching station, Seine-Maritime) with a net transmission capacity of 2,000 MW. The interconnector is designed as two parallel monopole 1000 MW circuits employing Voltage Source Converter technology. The project will be able to: • Boost competition by providing access to wider electricity markets; • Help improve security of supply by creating additional source of supply and by providing ancillary services to the respective national grids; and • Increase sustainability of energy supply by helping to integrate more renewable energy sources. The project will consist of the following elements: • One converter station on each end of the link, • The 320 kV DC subsea cable route will be approximately 182 km in length between Eastney (UK) and Pourville (France). • The British 320 kV DC terrestrial cable route will be approximately 20 km long. • The French 320 kV DC terrestrial cable route will be approximately 36 km long. • The 400 kV AC cable routes are several hundred meters in France and UK. | Aquind Limited (UK) and AQUIND SAS (France, 100% subsidiary of Aquind Limited) | FR ;GB | France – Schéma Décennal de Développement du Réseau 2019, project number 991 (page 442) - https://assets.rte-france.com/prod/public/2020-07/SDDR%202019%20Annexe%2002%20-%20Les%20projets_0.pdf. AQUIND Interconnector is also included in the latest available “Programmations pluriannuelles de l'énergie of France 2019 – 2023 2024 – 2028” (page 194) - https://www.ecologique-solidaire.gouv.fr/sites/default/files/0-PPE%20English%20Version%20With%20Annex_0.pdf. Great Britain - Future Energy Scenarios 2021, (FES Modelling Methods 2023, page 40 - https://www.nationalgrideso.com/document/283071/download). AQUIND is also included in latest available Electricity Ten Year Statement 2022, as it is part of National Grid's TEC Register (page 4 - https://www.nationalgrideso.com/document/275566/download and https://data.nationalgrideso.com/connection-registers/interconnector-register/r/interconnector_register ) | 2030 | 3 | True | False | New | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Official Websites: English - http://aquind.co.uk/ French - http://aquind.fr/ Consultation websites: English - http://aquindconsultation.co.uk/ French - https://aquindconsultation.fr/ Investment in electricity interconnectors: immediate economic benefits and key role in the French energy transition. Example of AQUIND Interconnector. (Asterès, June 2020) - https://asteres.fr/site/wp-content/uploads/2020/06/ASTERES-AQUIND-Investir-dans-les-interconnexions-19062020.pdf AQUIND Interconnector - reducing the cost of transition to Net Zero for GB energy consumers (FTI Consulting, July 2020) - https://www.fticonsulting-emea.com/~/media/Files/emea--files/insights/reports/2020/aug/reducing-cost-transition-net-zero-gb-consumers.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Structural differences in the wholesale electricity prices between the electricity markets in GB and France clearly demonstrate the need for more capacity. By providing additional 2GW of interconnection capacity AQUIND Interconnector will reduce price differentials on a congested France - GB border. By providing additional 2GW of interconnection capacity AQUIND will contribute to reaching the objectives of the European ITEG indicators in France and GB. AQUIND Interconnector will facilitate more efficient generation dispatch in the connected markets required for cross-border balancing services AQUIND will provide an opportunity for the efficient dispatch of renewables in GB, France and across connected markets. The additional cross-border capacity provided by AQUIND offers the opportunity to export additional power, that otherwise could be curtailed, during periods of high renewable generation. | France - UK - 4800 | France - UK - 4800 - France - - 1000 - 5000 | FR00-UK00 | 2075 | 2075
250 | Merchant line Castasegna (CH) - Mese (IT) | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Rationalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200-250 MW. | Repower, MERA SRL | CH ;IT | Piano di sviluppo Terna 2023. https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete. PDF, Avanzamento Nord Ovest pg 11 | 2027 | 3 | True | False | New | False |  | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Ra-tionalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200-250 MW. The Investement is composed by the purly Merchant line Project, around 45M€ and the TERNA Investment part for the rationalisation of the existing 380/132-kV Network and the Realisation of a new 380/132-kV Substation in Mese, other 45M€ Investment. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | TYNDP 2016, 2018, 2020 and 2022 PDS Terna from 2011 till actual (2023) |  |  | Italy - Switzerland - 200 | Italy - Switzerland - 2200 - Italy - - 1000 - 5000 Switzerland - - <1000 | CH00-ITN1 | 200 | 200
254 | HVDC Ultranet Osterath to Philippsburg | The Ultranet project consists of a 2 GW HVDC-connection from the Region of Osterath (Rhineland) to the Region of Philippsburg (Baden-Württemberg). It's a pilot project with DC circuits on the same pylons as AC lines and will therefore deliver profund knowledge. The project forms the southern section of the so-called “Corridor A” concept (with project 132) foreseeing connection of the northern and southern regions of Germany via HVDC power lines. As such, Ultranet will reinforce the grid for the completed nuclear phase-out. It also complies to the European North-South Interconnection idea aiming at connecting the significant offshore renewable generation capacities in the North Sea with the load centres in the southern parts of Europe. | Amprion, TransnetBW | DE | German NDP: Netzentwicklungsplan Strom 2037/2045 Version 2023, Germany, Project No. DC2, p.438; https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_1.pdf | 2026 | 3 | False | True | New | True | 1.6 |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | German Network Development Plan 2037/45 Version 2023: https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_1.pdf 5th PCI-List: https://ec.europa.eu/energy/sites/default/files/fifth_pci_list_19_november_2021_annex.pdf 4th PCI-List: https://ec.europa.eu/energy/sites/ener/files/c_2019_7772_1_annex.pdf 3rd PCI-list: https://ec.europa.eu/energy/sites/ener/files/documents/annex_to_pci_list_final_2017_en.pdf Bundesbedarfsplan 2022 (BBPIG): https://www.netzausbau.de/Vorhaben/ansicht/de.html?cms_nummer=2&cms_gruppe=bbplg http://www.gesetze-im-internet.de/bbplg/ Project specific websites: Amprion: https://www.amprion.net/Netzausbau/Aktuelle-Projekte/Ultranet/ TransnetBW: https://www.transnetbw.de/de/netzentwicklung/projekte/eichstetten-bundesgrenze-frankreich/projektueberblick Link to the website of the project: https://ultranet.amprion.net/ Link tot he current NDP: https://www.netzentwicklungsplan.de/sites/default/files/2024-04/NEP_2037_2045_V2023_Anhang_2E_Aktualisierung_April_2024.pdf | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL-BE-LU-FR-DE Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | In connection with P132, the planned HVDC connection transports the energy of regenerative Energy sources in northern Germany directly to the demand regions of southern Germany. It strengthens the common German market area through targeted energy transport. The project reduces loop flows to Germany's neighboring countries by reducing bottlenecks in northern Germany and providing a transport task from western Germany to southern Germany. The project contributes significantly to security of supply and grid stability through the widespread integration of renewable energies in northern (wind offshore and onshore) and southern Germany (wind onshore). In particular, the system flexibility is increased by the use of HVDC converter. In combination with P132 the project enables the integration of offshore and onshore wind energy by preventing potential bottlenecks in northern and southern Germany. |  |  | DE00-FR00 internalDE00 | 950 2000 | 650 2000
259 | HU-RO | The project consists of a new 400 kV new interconnection line Debrecen Dél (HU) - Oradea (RO) and 2nd circuit of 400 kV OHL Nadab (RO) - Békéscsaba (HU). In Romania, the following internal investments are necessary associated to this project: new 400/220 kV transformer in substation Rosiori, reconductoring 220 kV OH line Urechesti-Tg. Jiu-Paroseni- Baru Mare-Hasdat. | MAVIR, Transelectrica | HU ;RO | A Magyar Villamosenergia-rendszer Hálózatfejlesztési Terve 2022., Hungary, 2023, Page 19 (https://www.mavir.hu/documents/10258/239341965/HFT2022_A+magyar+VER+h%C3%A1l%C3%B3zatfejleszt%C3%A9si+terve.pdf); Plan de Dezvoltare RET 2022-2031 (Transelectrica development plan 2022-2031), pages 78 and 85 - available at: https://www.transelectrica.ro/ro/web/tel/planul-de-dezvoltare-ret-2022-2031 | 2030 | 2 | True | False | MostlyNew | True | 2.5.1, 2.5.2, 2.5.3, 2.5.4, 2.5.5 | These investments will enhance energy exchange in the East-West corridor. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | "The project was originally proposed by the ENTSO-E Common Planning Study performed during TYNDP 2016, which found potential when assessing against TYNDP 2014 Vision 4. The need was confirmed during the IoSN process of TYNDP 2018, in scenarios DG2040 and GCA2040 and during the IoSN process of TYNDP 2020" | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | According to ENTSO-E System Needs study for TYNDP 2022, the difference in the marginal cost of electricity between Romania and Hungary in 2040, in the No investment case is 10-20 EUR/MW and with project case is 5-10 EUR/MW The ratio between nominal transmission capacity and installed RES capacity in 2030 in Romania increase from 25.5 % in TYNDP 2022NT2030 scenario without projects to 96.4% with projects According to ENTSO-E System Needs study for TYNDP 2022, the increase of transfer capacity at the boundary between Romania and Hungary, will support the large scale integration of RES (the curtailed energy will decrease) | Hungary - Romania - 2027 | Hungary - Romania - 2027 - Hungary - - 1000 - 5000 Hungary - - 1659 | HU00-RO00 | 1410 | 740
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | This project considers a multi-purpose HVDC interconnection between Great Britain and The Netherlands, that combines the benefits of connecting electricity markets and offshore wind generation in Great Britain and The Netherlands. The base capacity of the cross border interconnection is around 2GW, but more can be considered. | National Grid, TenneT-NL | GB ;NL | No | 2030 | 2 | True | False | New | True | 4.6 |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True |  |  |  | The Netherlands - UK - 2000 | The Netherlands - UK - 2000 - The Netherlands - - 1000 - 5000 | UK00-NL00 | 2000 | 2000
267 | Hansa PowerBridge II | Possible second HVDC cable interconnector between southern Sweden (Bidding area SE4) and Germany (50Hertz). The German grid interconnection point is located in the search area of the municipalities Sanitz/Gnewitz/Dettmannsdorf/Town of Marlow. This project candidate is driven by market based target capacities found in the Common Planning Studies by Regional Group Baltic Sea. | Svenska kraftnät, 50Hertz | DE ;SE | German NEP2037_2045, version 2023, 2nd draft, Germany, 2023, project P221, p. 587-590, https://www.netzentwicklungsplan.de/sites/default/files/2023-06/NEP%20kompakt_2037_2045_V2023_2E_1.pdf | 2040 | 1 | True | False | New | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | The last version of the German national development plan with the project No. 176 was published in 2023 und is available under the following link: https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_1.pdf , page 329-332 (project 221) |  |  | Germany - Sweden - 1400 | Germany - Sweden - 2900 - Germany - - 5000 - 10000 | DE00-SE04 | 700 | 700
270 | FR-ES project -Aragón-Atlantic Pyrenees | This project consist of a new HVDC interconnection between France and Spain located in the Central part of the Pyrenees between Aragón region (Spain) and Marsillon (France). Internal AC reinforcements in Spain complement the cross border section, in order to connect the new converter station to the existing network. This project was included in the PCI list since 2015 (PCI 2.27.1) | Red Eléctrica, Rte | ES ;FR |  | 2040-2041 | 1 | True | False | New | True | 1.7.2 | A joint study performed by Red Electrica and RTE show that without internal reinforcements on the French network, and especially the one between Cantegrit and Marsillon, target NTC would be reached at best 30% of the year. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | - Spanish National Development Plan: https://www.planificacionelectrica.es/sites/webplani/files/2022-06/REE_Plan_Desarrollo.pdf and its project sheet platform: https://www.planificacionelectrica.es/proyectos - French National Development Plan http://www.rte-france.com/fr/article/schema-decennal-de-developpement-de-reseau - Inter-Governmental agreement (Madrid and Lisbon Declarations): https://ec.europa.eu/energy/sites/ener/files/documents/Madrid%20declaration.pdf https://ec.europa.eu/info/sites/info/files/lisbon_declaration_energyinterconnections_final.pdf - Constitution of the High Level Group on Interconnections for South West Europe: http://europa.eu/rapid/press-release_IP-15-5187_en.htm | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The IoSN report show high price differentials in FR-ES that would be reduced with a project in this border. On the French-Spanish border, the yearly average marginal price difference is higher than the 2€/MWh defined by Interconnection Target Expert Group as threshold for developing new interconnections. In addition, Spanish interconnectors nominal transmission capacity is below 30% of the national peak load and RES capacity. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity in ES-FR boder. | France - Spain - 3000 | France - Spain - 4500 - France - - 1000 - 5000 Spain - - >10000 | ES00-FR00 | 1500 | 1500
276 | FR-ES project -Navarra-Landes | This Project consist of a new HVDC interconnection between France and Spain in the Western part of the Pyrenees between Pamplona area (Spain) and Cantegrit (France). The project is considered as an HVDC project of 2x1000 MW. Internal reinforcements complement the cross border section. This project was included in the PCI list since 2015 (PCI 2.27.2) | Red Eléctrica, Rte | ES ;FR |  | 2035-2036 | 1 | True | False | New | True | 1.7.1 | A joint study performed by Red Eléctrica and RTE show that without internal reinforcements on the French network, and especially the one between Cantegrit and Saucats, target NTC would not be reached at best 30% of the year. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | - Spanish National Development Plan: https://www.planificacionelectrica.es/sites/webplani/files/2022-06/REE_Plan_Desarrollo.pdf and its project sheet platform: https://www.planificacionelectrica.es/proyectos - French National Development Plan: http://www.rte-france.com/fr/article/schema-decennal-de-developpement-de-reseau - Inter-Governmental agreement (Madrid and Lisbon Declarations): https://ec.europa.eu/energy/sites/ener/files/documents/Madrid%20declaration.pdf https://ec.europa.eu/info/sites/info/files/lisbon_declaration_energyinterconnections_final.pdf - Constitution of the High Level Group on Interconnections for South West Europe: http://europa.eu/rapid/press-release_IP-15-5187_en.htm | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The IoSN report show high price differentials in FR-ES that would be reduced with a project in this border. On the French-Spanish border, the yearly average marginal price difference is higher than the 2€/MWh defined by Interconnection Target Expert Group as threshold for developing new interconnections. In addition, Spanish interconnectors nominal transmission capacity is below 30% of the national peak load and RES capacity. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity in ES-FR border. | France - Spain - 3000 | France - Spain - 4500 - France - - 1000 - 5000 Spain - - >10000 | ES00-FR00 | 1500 | 1500
280 | FR-BE: Lonny-Achene-Gramme | The project aims at sustaining further market integration within the long-term perspective of the energy transition and subsequent need to develop interconnection capacity on the French-Belgium border whilst alleviating Lonny-Achene-Gramme as bottleneck. The reinforcement strategy consists of maximizing the potential of the existing 400kV interconnector Lonny-Achene-Gramme through the use of cost-efficient technologies such as PSTs and HTLS . The project will further reinforce the existing Lonny-Achêne-Gramme cross-border transmission line on horizon 2030-2032 with high-performance (HTLS) conductors, which requires substation upgrades and installing a second phase shifting transformer in Achêne to handle the increased power flows. Indeed, this project builds further on a first phase which foresees a first PST in Achêne already by 2025. The line reinforcement accompanied by the second PST will further improve market exchange opportunities and RES integration in general. The project aims at increasing the transfer capacity between France and Belgium with approx. 1 GW. | Elia, Rte | BE ;FR | NDP1, Belgian NDP (2024-2034) in §4.3.1, https://www.elia.be/en/infrastructure-and-projects/investment-plan/federal-development-plan-2024-2034 - NDP2, France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, project n°1050, page 442, https://www.rte-france.com/en/analyses-trends-and-perspectives/ten-year-network-development-plan#Documents | 2030/2032 | 2 | True | False | MostlyUpgrade | True | 1.8 |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | More information about the project can be found following this link: - National Development Plan §4.3.1: https://www.elia.be/en/infrastructure-and-projects/investment-plan/federal-development-plan-2024-2034 Project website: https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/lonny-gramme | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project increases crossborder capacity between Belgium and France. The project increases crossborder capacity between Belgium and France. The project increases crossborder capacity between Belgium and France. The project increases crossborder capacity between Belgium and France allowing a better integration of renewables. | Belgium - France - 1000 | Belgium - France - 2000 - Belgium - - <1000 France - - 1000 - 5000 | BE00-FR00 | 1000 | 1000
283 | TuNur Italy | TuNur Italy is a 2,000MW HVDC transmission project between Tunisia and Italy enabling the delivery of 12TWh of dispatchable, competitively priced, renewable power to Europe supporting the energy transition, REPowerEU and the EU Green Deal. The transmission project will connect a hybrid renewable energy and storage facility in Southern Tunisia, where solar and wind resources are extremely high, to the Italian network. The +/-525kV HVDC system consists of two independent bipoles of 1GW, each including a DC overhead line from the power plant in southern Tunisia to the shoring point in northern Tunisia; a 660km submarine cable from the shoring point to Montalto di Castro; VSC converter stations at both terminal points; and a short AC cable to Terna’s 400kV substation. The project provides a robust connection in the central Mediterranean corridor in line with the initiative for developing the region into a Green Energy Hub. The reinforcement of this energy highway will enable investment, economic development, and technology transfer in Tunisia; and the integration of large quantities of dispatchable renewable power into Europe, supporting energy and climate policy objectives, specifically demand for low carbon power and diversification of supply. | TuNur Ltd | IT ;TN | The project is mentioned in the Italian 2023 development plan “Il progetto HYPERGRID e necessita di sviluppo infrastructturale” at page 50. There is no project number allocated to the project. The development plan can be found at: https://download.terna.it/terna/Terna_Piano_Sviluppo_2023_Progetto_Hypergrid_necessit%C3%A0_Sviluppo_infrastrutturale_8db2549ed056bf0.pdf | 2034 | 1 | True | False | New | False |  | To connect to Terna’s grid, the main investment (DC cable) requires a short AC cable. The AC cable has no standalone purpose without the main investment. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | https://www.tunur.tn/project/tunur-italy-transmission-line/ | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | The TuNur project will contribute to improving market integration and reducing price differentials between EU and non EU countries by providing an additional 2000 MW of low cost and low carbon available capacity through a new connection between a non EU (Tunisia) and EU (Italy) country. The TuNur project will provide dispatchable low-carbon power and will contribute to system adequacy deficiencies by increasing transmission capacity. This power source will improve security of supply by reducing Loss of Load durations across EU networks, making a significant contribution to system stability. The TuNur project will significantly contribute to system flexibility through direct access to a new source of renewable energy. TuNur will also contribute to system stability by improving transient stability and helping to meet RoCoF system needs. TuNur will provide flexible power with black-start capacity. TuNur consists in infrastructure that will contribute to balancing flexibility by providing the European network with a new source of low-carbon dispatchable power. Additionally, the TuNur project will deliver a 2000 MW power reserve through a new HVDC interconnection between Tunisia and Italy. |  |  | ITCS-TN00isolated | 2000 | 2000
285 | GridLink | 1.25 GW HVDC electricity interconnector between UK and France Voltage Source Converter (VSC) Grid connection point (substations name): Kingsnorth (UK) and Warande (France) Total cable length (substation to substation) 158km (110km in UK and 48km in France) Symmetrical monopole converters Two cables (XLPE) laid in a single trench Nominal DC voltage: ±320 kV Nominal DC rated current: 1995 A Bus-bar to bus-bar losses profile over MW range: 2.1% (27 MW) full load; 0% (0 MW) at zero load Annual Availability: 98% availability, 2% planned outages, 0% forced outages. Maximum single failure according to the design: 1.25 GW UK Transmission network reinforcement required: Uses spare bay with minimum works at Kingsnorth 400kV substation France transmission network reinforcement: Requires new substation next to existing Warande 400kV substation Main environmental impact: reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. No significant environmental impacts during construction and operation. | iCON Infrastructure | FR ;GB | 1. RTE Ten-Year Electricity Grid Development Plan 2019 (Schéma Décennal de Développement du Réseau 2019), https://www.rte-france.com/analyses-tendances-et-prospectives/le-schema-decennal-de-developpement-du-reseau#Documents; 2. NGESO Electricity Ten Year Statement ETYS 2023, https://www.nationalgrideso.com/research-and-publications/electricity-ten-year-statement-etys; 3. NGESO Electricity Ten Year Statement ETYS 2023 Appendix C, https://www.nationalgrideso.com/document/275591/download; 4. NGESO Network Options Assessment NOA 2021-22, https://www.nationalgrideso.com/research-and-publications/network-options-assessment-noa/noa-interconnectors; 5. NGESO interconnector-register-06-10-2023, https://www.nationalgrideso.com/data-portal/interconnector-register; 6. Ofgem approved interconnectors list, https://www.ofgem.gov.uk/energy-policy-and-regulation/policy-and-regulatory-programmes/interconnectors | 2030 | 3 | True | False | New | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Project web-site: www.gridlinkinterconnector.com/ Statement on unbundling pursuant to Appendix 6.1.1 of the Practical Implementation Guide dated 2 October 2017: "GridLink Interconnector will abide by the European rules governing unbundling pursuant to the 3rd Energy Package." | Infrastructure to reduce price differentials between EU and/or non-EU countries Mitigate the risk of power failures Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. |  | France - UK - 4800 | France - UK - 4800 - France - - 1000 - 5000 | FR00-UK00 | 1250 | 1250
297 | BRABO III | Realization of a new 380 kV corridor between Zandvliet and Mercator consisting of a double-circuit AC overhead line, including a new substation 380kV in Lillo. BRABO II and III sustain the development of interconnection capacity on the Belgian North Border towards a broader scenario framework, hereby securing the supply of electricity around the Antwerp harbour area in light of the increasing industrial demand , as well as developing capacity for the potential integration of new production in the Antwerp area. This project contributes to resolving internal congestions, considering expected high international transit & loop flows. This project increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This project allows to deal with the growth in industrial consumption from the Antwerp harbour and to increase the grid hosting capacity for the connection of new production capacity, thereby contributing to the overall adequacy of the system, especially relevant considering the partial nuclear phase out in Belgium. | Elia | BE | NDP1, Belgium, 2024-2034, p145, ID 38 | 2026 | 4 | False | True | Upgrade | True | 1.9 | The project of Brabo III was clustered in the past with Brabo II. As Brabo II has been completely energized, that part of the investment has been removed from the TYNDP. Both project Brabo II and III are needed to increase the NTC on the border between Belgium and the Netherlands. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | More information about the project can be found following these links: - https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/brabo-lll - NDP: https://www.elia.be/en/infrastructure-and-projects/investment-plan/federal-development-plan-2024-2034 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) | Project increases the crossborder capacity between Belgium and the Netherlands. Project increases the crossborder capacity between Belgium and the Netherlands. Project increases the crossborder capacity between Belgium and the Netherlands allowing a better integration of renewables. Project increases the crossborder capacity between Belgium and the Netherlands and reinforces the security of supply of the harbor of Antwerp and its energy intensive industries. |  |  | BE00-NL00 | 1000 | 1000
299 | SACOI 3 | New HVDC line between Italy mainland, Corsica and Sardinia replacing existing link SACOI2. | Terna, EDF | FR ;IT | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Ovest, Italy, 2023, ID: 301-P, pag. 30, https://www.terna.it/en/electric-system/grid/national-electricity-transmission-grid-development-plan | 2029 | 4 | True | False | New | True | 1.10 |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian and Corsica market zones This project helps Italy to reach the 15% interconnection target by 2030 This project will contribute to overcome flexibility/stability problems due to scarsely meshed grid This project will improve the integration of italian RES generation | Italy - Corsica - 100 | Italy - Corsica - 100 - Corsica - - 123 Corsica - - <1000 Italy - - 1000 - 5000 | ITSA-ITCO FR15 - ITCO ITCN-ITCO | 400 100 400 | 400 100 400
309 | NeuConnect | NeuConnect will be the first subsea HVDC electricity Interconnector to connect the UK and German electricity markets. It will be approximately 700km long with a capacity of 1.4GW. NeuConnect is a new interconnector under development that will create the first direct link between the countries by connecting the markets for the first time and is forecasted to deliver significant consumer benefits and will deliver a 16 million tonne reduction in CO2 emissions over 25 years. This approach offers clear benefits on both sides by reducing costs for consumers whilst increasing consumer choice and offering the best choice for fighting climate change. | NeuConnect Britain Limited, NeuConnect Deutschland GmbH | DE ;GB | Germany - Bedarrfsermittlung 2019-30 Measure M534 Fedderwarden – Großbritannien (NeuConnect) Leitung United Kingdom - National Grid - NeuConnect appears in the Interconnectors Connection Register www.nationalgrideso.com/connections/registers-reports-and-guidance | 2027 | 4 | True | False | New | False |  | NeuConnect is an Independent Interconnector and not connected to any other transmission project. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | https://neuconnect-interconnector.com |  |  | Germany - UK - 1400 | Germany - UK - 2800 - Germany - - 5000 - 10000 | DE00-UK00 | 1400 | 1400
312 | St. Peter (AT) - Tauern (AT) | This project is part of the Austrian 380-kV security ring. It therefore provides based on the concept a redundant and robust connection and increases security of supply significantly. In addition higher transport capacities are able to connect RES production in the corners of the region with the Alpine storages and therefore integrate both efficiently and properly. | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, 11-10, 52, https://www.apg.at/en/power-grid/grid-expansion/ | 2025 | 4 | False | True | New | True | 2.1.2 |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | PCI 3.1.2: 3rd List: https://ec.europa.eu/energy/sites/ener/files/documents/annex_to_pci_list_final_2017_en.pdf 4th List: https://ec.europa.eu/energy/sites/ener/files/c_2019_7772_1_annex.pdf National development plan: https://www.apg.at/en/power-grid/grid-expansion/ Project Homenpage: https://www.apg.at/en/projects/salzburg-line/ | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | facilitates interconnection capacity Interconnection between huge amounts of RES and storage capacity in the Alps provides flexibility and stability. Interconnection between huge amounts of RES and storage capacity in the Alps helps to reduce the amount of RES curtailment significantly |  |  | AT00-DE00 | 2000 | 2000
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | New 380kV Line between TenneT-DE and APG (Isar/Altheim/Ottenhofen - St. Peter). This project reinforces the interconnection capacity between Austria and Germany. It supports the interaction of RES in Northern Europe (mainly in Germany) and in the eastern part of Austria with the pump storages in the Austrian Alps and therewith facilitates their utilisation. | Austrian Power Grid, TenneT DE | AT ;DE | DE: NEP2037 v2023, P 67, p. 401 ff ( https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_onshore.pdf). APG Netzentwicklungsplan 2021, AT, 2021, 11-7, 58, https://www.apg.at/en/Stromnetz/Netzentwicklung | 2027 | 3 | True | False | New | True | 2.1.1 |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | PCI Lists: https://eur-lex.europa.eu/legal-content/EN/TXT/?uri=CELEX%3A32022R0564&qid=1663087079030 https://ec.europa.eu/energy/sites/ener/files/c_2019_7772_1_annex.pdf https://ec.europa.eu/energy/sites/ener/files/documents/annex_to_pci_list_final_2017_en.pdf NDP Austria: http://www.apg.at/de/netz/netzausbau/Netzentwicklungsplan NDP Germany: https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_onshore.pdf Projekt homepage Germany: https://www.tennet.eu/de/projekte/altheim-st-peter Project homepage Austria: https://www.apg.at/en/projekte/380-kv-deutschland-leitung | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | helps to reach 15% target in Germany high RES generation connected to pump storage high RES generation connected to pump storage |  |  | AT00-DE00 | 1400 | 1400
323 | Dekani (SI) - Zaule (IT) interconnection | The Zaule (IT) - Dekani (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3, ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o.. and Holding Slovenske Elektrarne d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Zaule (IT) substation to Dekani (SI) substation, including a 110/135 kV Phase Shifter Transformer. | HSE d.o.o. (Holding Slovenske Elektrarne, d.o.o.) - E3 d.o.o. (ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o) - Adria Link Srl | IT ;SI | National Development Plan 2023 by Terna, Italy, The Hypergrid project and development requirements page #50 and 51, https://download.terna.it/terna/2023_Hypergrid_project_and_development_requirements_8db79602cedc732.pdf - Eles Development Plan 2023_2032 page 89: https://www.eles.si/Portals/EN/Documents/EN/ELES_development_plan_2023-2032.pdf?ver=2023-06-16-154317-607 | 2026 | 3 | True | False | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | https://corporate.enel.it/en/stories/a/2023/01/adria-link | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project will increase the cross-border capacity between the interconnected Countries and will allow market exchanges which lead to a minimising price differentials of the Italian border also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios with a different generation mix . In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems involved by the line. This cross border project allows higher flows in the meshed AC-grid and consequentially it allows better integration of RES in the interconnected Countries. | Italy - Slovenia - 125 | Italy - Slovenia - 125 - Italy - - 1000 - 5000 | ITN1-SI00 | Up to 60 | Up to 10
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | "The Redipuglia (IT) - Vrtojba (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E 3, ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o. and Holding Slovenske Elektrarne d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Redipuglia (IT) substation to Vrtojba (SI) substation, including a 110/135 kV Phase Shifter Transformer." | Adria Link Srl - HSE d.o.o. (Holding Slovenske Elektrarne, d.o.o.) - E3 d.o.o. (ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o) | IT ;SI | National Development Plan 2023 by Terna, Italy, The Hypergrid project and development requirements page #50 and 51, https://download.terna.it/terna/2023_Hypergrid_project_and_development_requirements_8db79602cedc732.pdf; Resolution of the Italian ANR - ARERA - with which the Redipuglia (IT) - Vrtojba (SI) project is considered an integral and priority part of the National Development Plan (Ref. 335/2022/I/EEL - https://www.arera.it/allegati/docs/22/335-22.pdf). Eles National Development plan page 89: https://www.eles.si/Portals/EN/Documents/EN/ELES_development_plan_2023-2032.pdf?ver=2023-06-16-154317-607 | 2026 | 3 | True | False | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | https://corporate.enel.it/en/stories/a/2023/01/adria-link | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project will increase the cross-border capacity between the interconnected Countries and will allow market exchanges which lead to a minimising price differentials of the Italian border also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios with a different generation mix . In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems involved by the line. This cross border project allows higher flows in the meshed AC-grid and consequentially it allows better integration of RES in the interconnected Countries. | Italy - Slovenia - 125 | Italy - Slovenia - 125 - Italy - - 1000 - 5000 | ITN1-SI00 | Up to 70 | Up to 100
325 | Obersielach (AT) - Podlog (SI) | Obersielach (AT) - Podlog (SI); 380-kV Upgrade; +700 MW NTC in both directions | Austrian Power Grid, Eles | AT ;SI | CD not in the NDP 10 year time frame. | 2035 | 1 | True | False | Upgrade | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | ENTSO-E TYNDP 2022: https://tyndp2022-project-platform.azurewebsites.net/projectsheets/transmission/325 ENTSO-E TYNDP 2022 System Needs Study: https://eepublicdownloads.blob.core.windows.net/public-cdn-container/tyndp-documents/TYNDP2022/public/system-needs-report.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project increases capacity of SI-AT border and decreases price difference between both markets in all future scenarios. This project will contribute to reduction of system adequacy deficiencies by increasing transmission capacity on SI-AT border. This project improves the integration of RES generation into the Continental European transmission grid. | Austria - Slovenia - 1000 | Austria - Slovenia - 1500 - Austria - - <1000 | AT00-SI00 | 700 | 700
328 | Interconnector DE-LUX | The project comprises the construction of two new 380/220-kV-substations in Germany (Aach) and Luxemburg (Bofferdange). The new substations will be connected via a new AC-link to allow a higher cross border capacity between Germany and Luxembourg. | Amprion, Creos | DE ;LU | NDP1; Germany, Netzentwicklungsplan 2037 Version 2023, Project 406, p. 694; NDP Luxembourg 2040 Version 2024, Projects L4202 + P4203 p.35-38 | 2028 | 2 | True | False | New | False |  | The new AC double circuit overhead 400 kV line between Germany and Luxembourg is clustered with substation Aach (DE) and Bofferdange (LU) to secure the needed capacity and distribute the energy into lower voltage levels. The existing 220 kV OH-lines Trier-Blooren and Quint-Heisdorf will be decommissioned after the 400 kV OH lines and substations will be put in operation. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | The project was part of the previous TYNDP 2020 and TYNDP 2022, (Link to the Website: https://tyndp2020-project-platform.azurewebsites.net/projectsheets/transmission/328) A dedicated Website describing the 380 kV reinforcements are available under following link: www.creos.net/380 In line with Scenario report 2040 http://www.creos-net.lu/actualites/actualites/article/scenario-report-2040-public-consultation.html The existing 220-kV-line between Heisdorf/Blooren - Niederstedem/Quint will be partially dismantled after commissioning of this project. https://www.netzentwicklungsplan.de/de/projekte/projekte-nep-2035-2021 https://www.creos-net.lu/fileadmin/dokumente/NEWS/pdf/2020-2022/20210820_Network_Development_Plan_2040_-_HV_Transport_Grid__final_.pdf |  |  | Germany - Luxemburg - 400 | Germany - Luxemburg - 400 - Germany - - 5000 - 10000 Luxemburg - - <1000 | DE00-LUG1 | 1000 | 1000
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | The development of ~6 GW transport capacity through the elaboration of a new corridor in the western part of Belgium, between the Stevin axis and the Izegem substation. It is to be complemented with an HTLS upgrade of the existing Izegem/Avelgem connection. Along this corridor a substation functioning as 'gateway' for the evacuation of offshore potential is envisioned. This corridor will be implemented in AC technology. Timing, routing, scope, etc. subject to feasibility studies and subsequent spatial planning procedures. The capacity of the Stevin axis will be fully used by 2020 for the integration of the first wave of 2.3 GW offshore wind in the Belgian North Sea and Nemo Link. A further development of the 380 kV grid via a new corridor towards the coast creates the necessary hosting capacity to unlock 3.5 GW additional wind in the Belgian part of the North sea and develop an additional interconnector with the UK. This new corridor will be linked to the Stevin corridor, creating a meshed 380 kV grid structure and hence considerably increasing the reliability. | Elia | BE | NDP, Belgium, 2024-2034, §4.5.2.1, page 296 - https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2024-2034/20230504_federaal_ontwikkelingsplan_van_het_transmissienet_2024-2034_nl.pdf | 2028 | 3 | False | True | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | More information about the project can be found following these links: - Project site: https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/ventilus - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2024-2034/20230504_federaal_ontwikkelingsplan_van_het_transmissienet_2024-2034_nl.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | Project needed to efficiently integrate and connect the artificial energy island to the Belgian grid and as such allow the connection of links to other countries around the North Sea to the artificial energy island. Project needed to efficiently integrate and connect the artificial energy island to the Belgian grid and as such allow the connection of links to other countries around the North Sea to the artificial energy island. Project needed to efficiently integrate and connect the artificial energy island to the Belgian grid. Project needed to efficiently integrate and connect the artificial energy island to the Belgian grid. |  |  | internalBE00 | 6000 | 6000
330 | 4th 400kV CZ-SK interconnector | This new 400 kV cross-border overhead line between the substations Otrokovice (CZ) - Ladce (SK) will strenghten the transmission capacity between Slovak and Czech transmission systems, aiming to maintain secure operation of both transmission systems. | CEPS, SEPS | CZ ;SK | This project is included in the last approved Slovakian NDP (SEPS). This project is not included in the last approved Czech NDP (CEPS) as the Czech Energy Act requires to have in NDP only projects which are commissioned in the ten-year time frame of the NDP. | 2035 | 1 | True | False | New | True | 2.7 | The new 400kV CZ-SK cross-border single OHL Otrokovice (CZ) - Ladce (SK) aims to increase NTC at the CZ-SK cross-border profile. The extension of 400kV substation Ladce (SK) is clustered with the CZ-SK cross-border line into one projects as it is directly connected into the new 400kV substation Ladce (SK). | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Environmental Impact The over-headline project Otrokovice - Ladce is included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed route (corridor) of the over-headline on the Czech territory was chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical study was carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed route was then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above study will be taken as an important input into the environment impact assessment which is scheduled to be conducted between 2022 and 2023 in accordance with EIA legislation. The main proposed route of the over-headline including its local variants on the Czech side does not pass through any NATURA 2000 sites. No bird areas and no European sites of interest are affected (EVL). The nearest locality EVL is EVL CHKO Beskydy (CZ 0724089) in the neighbourhood of Střelná village, to which one section of the route is approaching at the distance of about 93 m at the crossing point on the Czech-Slovakian border. According to the opinion of the Department of Environment and Agriculture of the Regional Authority of the Zlín Region granted on 22nd May 2017, the route of the new over-headline on the Czech side does not pass through the territories of European significant sites and bird areas (NATURA 2000). On the Slovak side this projects aims to replace the existing out-of-date 220kV interconnections between SK and CZ which are planned to be decommissioned in next ten years. For the purpose of its erection (not only) SEPS and CEPS have signed the Memorandum of understanding in order to efficiently coordinate the development activities on the common SK – CZ cross border profile. On the Slovak side the route for the purpose of the OHL erection is reserved in the spatial planning documents of the respective communities (villages, towns, county, etc.). The environmental impact assessment study will be carried out according to the particular Slovak legislation. SEPS does not expect any objection to get an approval from the environmental point of view, as the planned route of the line is the same as the existing 220 kV SK-CZ cross-border line corridor. Currently expected date of commissioning is in year 2035 which is also written in the above mentioned MoU. The new substation 400 kV Ladce (SK) needs to connect this OHL into the Slovak transmission system. Social impact: From the point of view of reliability of power supply in the Zlín region on the Czech side the construction of the over-headline Otrokovice – Ladce is very important because it will strengthen the connection of the Otrokovice substation to the transmission system. Otrokovice substation with three transformers 400/110 kV each with 350 MVA is currently connected to the transmission system with only two over-head lines. The energy transferred between the transmission and distribution system by this substation represents approximately about 7% of the total energy transferred between the transmission system and all distribution companies in the Czech Republic. From the above, it is obvious that strengthening the connection of substation Otrokovice with the transmission system is vital because it will ensure energy supplies to industry and a considerable number of households in the Zlín Region, which is one of the most exposed area in the Czech Republic. Considering the long-term aspect of increasing the consumption and reducing the share of electricity production by traditional generation connected into the 110 kV distribution system, the demand on the power transmitted by the transmission system is further increased, and therefore its strengthening is crucial for the society. The project is aiming to replace the 220 kV system in the west-north Slovakia by the new 400 kV substation with the new 400/110 kV transformation. The connection of the third 400 kV line (cross-border line Otrokovice - Ladce) to the Ladce substation will significantly improve security and reliability of the Slovak power system operation in that region, as well as during maintenance of the transmission system equipment. In the connected 110 kV distribution grid a lot of households and important consumers are connected as well as important power plants providing heat to the households in the cold months and the hydro power plants on the Váh river. This will have a substantial benefit for the society living in the Žilina and Považská Bystrica agglomeration. |  |  | Czech Republic - Slovakia - 500 | Czech Republic - Slovakia - 500 - | CZ00-SK00 | 500 | 500
335 | North Sea Wind Power Hub | TenneT Netherlands, TenneT Germany, Energinet and Gasunie joined forces to develop a large scale European electricity system for offshore wind in the North Sea. The North Sea Wind Power Hub (NSWPH) consortium partners consider the project to be an important possible alternative path of an internationally coordinated roll-out towards accomplishing the green energy transition and achieving the Paris Agreement. Central to the vision is the construction of one or more hubs at a suitable location in the North Sea with interconnectors to bordering North Sea countries and between the hubs. The whole system may function as a hub for transport of wind energy, an interconnection hub to the connected countries, a working hub for offshore wind developers and a location for possible power-to-gas solutions. This project is a first building block in the hub-and-spoke concept (NSWPH) connecting up to 14 GW future offshore wind parks to the systems of Denmark, the Netherlands and Germany around 2035. | Energinet.dk, TenneT-NL, TenneT-DE | DE ;DK ;NL | The NSWPH was analysed in the last National Development Plan of Germany. In the Danish case, a future 'Strategic Investment Plan' will be developed and cover a 20-year period in which the NSWPH will be included. The NSWPH is presently analyzed in various feasibility studies at wider regional level. It builds on long-term system needs also identified in ENTSO-E’s Regional Investment Plan North Sea. Due to the strong internationally coordinated drive of this project, the concept has been first addressed in ENTSO-E’s TYNDP process. | 2035 | 1 | True | False | New | True | 4.1 | The North Sea Wind Power Hub investment items need to be clustered and thereby realized together to meet its full benefit. The investment items are mutually dependent on each other. Realizing one investment contributes to the realization of the full potential of another investment item. The intended system includes a distributed hub situation to enable different realization time lines in the different participating countries. Without the wind farm connections, the configuration would merely provide interconnection while the RES integration would still require additional (radial) connections to shore. And without the interconnection links, the concept would be a single hub to shore, while missing the opportunities of market integration and sharing of reserves. Presently all investments in the NSWPH project are ‘under consideration’, with a provisional commissioning for 2035. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | https://northseawindpowerhub.eu/ https://www.youtube.com/watch?v=lBnWEK9IUn4 Roland Berger for the European Commission, DG-ENER; "North Seas Offshore Energy Clusters - North Sea Wind Power Hub"; 2018. Cost-effective transition of energy through sector coupling: • THE IMPORTANCE OF THE GAS INFRASTRUCTURE FOR GERMANY’S ENERGY TRANSITION – A model-based analysis, Frontier economics et al. 2018 http://frontier-economics.com/publication/der-wert-der-gasinfrastruktur-fuer-die-energiewende-deutschland/ • The Potential role of Power-to-Gas in the e-Highway2050, European Power to Gas Platform/DNV-GL 2017 http://europeanpowertogas.com/new-study-released-on-potential-role-of-power-to-gas-in-the-e-highway2050-study/ • VAWOZ 2040 study “Studie systeemintegratie wind op zee 2030-2040” by the Dutch Government : https://offshorewind.rvo.nl/blog/view/9d736052-eb25-4775-8c4d-062979d6efae/rapport-systeemintegratie-wind-op-zee-2030-2040-in-dutch Increasing the value of wind through the reduction of low electricity prices and curtailment: • System Perpective 2035 – Long-term perspectives for efficient use of renewable energy in the Danish energy system, Energinet 2018 https://en.energinet.dk/-/media/Energinet/Analyser-og-Forskning-RMS/Dokumenter/Analyser/_Analyser-Engelsk/System-Perspective-2035---Main-Report_English.pdf Demand for renewable H2 in countries of the Project Promotors • DE: Role of gaseous energy carriers in decarbonising Germany - Results of a brief meta-study of independent third party studies, Wagner, Elbling & Company 2018 • DK: System Perspective 2035 – Long-term perspectives for efficient use of renewable energy in the Danish energy system, Energinet 2018 (Danish Version) https://energinet.dk/-/media/4DDC27A7159245E985CEC07A92FB70AF.pdf • NL: Chemistry for Climate – Roadmap for the Dutch Chemical Industry towards 2050, Ecofys 2018 https://www.ecofys.com/files/files/vnci_routekaart-2050.pdf |  |  |  |  | DE00-DK/NL00
338 | Adriatic HVDC link | New HVDC line between Villanova (or Villavalle) and Fano (or Portotolle) existing 400 kV substations (the nominal power of the link will be at least 1000 MW) | Terna | IT | Piano di Sviluppo 2023 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Est, pag. 28, ID: 436-P, https://www.terna.it/en/electric-system/grid/national-electricity-transmission-grid-development-plan | 2029 | 3 | False | True | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | Italian Development Plan: http://www.terna.it/it-it/sistemaelettrico/pianodisviluppodellarete/pianidisviluppo.aspx | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | The new line will allow congestion reduction on the Southern-Northern border, and the integration of the local renewable production. |  |  | ITN1-ITCN ITCN-ITCS | 600 1000 | 1000 1000
339 | Tyrrhenian link | Italian HVDC link between Campania, Sicily and Sardinia | Terna | IT | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Est, pag. 46: https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete/ | 2028 | 4 | False | True | New | False |  | The two investments will allow to increase the transmission transport capacity between Italian main islands (Sardinia and Sicily) and mainland | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True |  | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase of security of supply increase RES integration reducing curtailment in overgeneration period |  |  | ITCS-ITSI ITSA-ITSI | 1000 1000 | 1000 1000 | The Tyrrenian Link is a project playing a relevant role both a national and European level. It is worth to point out that significant (additional) benefits would be given by analyses regarding the ancillary service market, that cannot be considered in ENTSO-E methodology, but just in national methodology, taking into account the specific market rules applied within the specific Country.
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | The development of ~6 GW transport capacity through the elaboration of a new corridor between Avelgem and Courcelles. This corridor is envisioned to be implemented in AC technology. Timing, routing, scope, etc. subject to feasibility studies and subsequent spatial planning procedures. Today, the west and the center of the country are connected on 380 kV via only one corridor between Mercator and Horta in HTLS. Additional capacity between the west and the center is, however, required to sustain price convergence within a European merit order increasingly characterized by RES. A new corridor Avelgem-Courcelles would deliver around 6 GW of capacity and at the same time increases the maintainability and reliability of the grid, fulfilling the regulatory expectation that internal grids should be sufficiently strong so that society can fully reap the benefits from European market integration. Avelgem–Courcelles corridor is a prerequisite for the integration of new offshore & onshore production capacity west of Mercator and for integration of a second interconnector with Great-Britain (Nautilus). | Elia | BE | NDP, Belgium, 2024-2034, §4.5.2.2, page 298 - https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2024-2034/20230504_federaal_ontwikkelingsplan_van_het_transmissienet_2024-2034_nl.pdf | 2030 | 3 | False | True | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | More information about the project can be found following these links: - Project site: https://www.elia.be/fr/infrastructure-et-projets/projets-infrastructure/boucle-du-hainaut - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2024-2034/20230504_federaal_ontwikkelingsplan_van_het_transmissienet_2024-2034_nl.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | Project needed to efficiently integrate and connect the artificial energy island to the Belgian grid and as such allow the connection of links to other countries around the North Sea to the artificial energy island. Project needed to efficiently integrate and connect the artificial energy island to the Belgian grid and as such allow the connection of links to other countries around the North Sea to the artificial energy island. Project needed to electrify the energy intensive industries to the south of Brussels. Project needed to efficiently integrate and connect the artificial energy island to the Belgian grid and as such allow the connection of links to other countries around the North Sea to the artificial energy island. |  |  | internalBE00 | 6000 | 6000
341 | North CSE Corridor | This project will consist of four investments. The investments of this project are SS 400/110 Belgrade 50, OHL 400 kV SS Belgrade 50 - WPP Cibuk, new line OHL 400 kV Portile de Fier (RO) - Djerdap 1 (RS) and and reconductoring of the 220 kV double circuit OHL Portile de Fier – Resita. Every investment included in this project represents a segment of the new significant corridor in the East-to-West direction, boasting the massive cross-border impact on the boundary between Serbia and Romania. This, in detail, means that the project will enhance the market integration in the region, allowing the lower difference in marginal energy costs, allow the connection of huge capacities of renewable sources that have applied for connection in the observed area (only in Serbia, there is way over 3 GW of new wind and solar power plants foreseen in the Banat region) and affect the security of supply in the aforementioned region by increasing the available balancing capacity across the mentioned border. New renewable capacities, enabled for connection by project's commissioning, will change the generation mix in Serbia and provide a boost for green transition in the Southeast Europe region. | EMS, Transelectrica | RO ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2021 - 2030 (Serbian national TYNDP 2021-2030), page 149 and 215 - available at: https://ems.rs/wp-content/uploads/2022/07/Plan-razvoja-prenosnog-sistema-2.pdf. Plan de Dezvoltare RET 2022-2031 (Transelectrica development plan 2022-2031), pages 76, 78 and 85 - available at: https://www.transelectrica.ro/ro/web/tel/planul-de-dezvoltare-ret-2022-2031 | 2029 | 2 | True | False | MostlyNew | False |  | These investments will help the evacuation of RES in North-East part of Serbia and enhance energy exchange in the East-West corridor. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | As the project contributes to the increase of the transfer capacity across the border between Serbia (non-EU) and Romania (EU), it is safe to claim that it will enhance market integration in the region and reduce price differentials, as requested by this criterion. The internal investments in Serbia, included in the scope of North CSE Corridor, are foreseen to mitigate the risks of potential blackouts in the Belgrade region. Investment SS Belgrade West will provide major help in reducing the loading of the existing 400/x and 220/x kV substations in Srem area. Due to the fact that the commissioning of this project creates an additional energy corridor between Serbia and Romania, as confirmed by the NTC calculations, it can be claimed that it will, among other benefits, prove to be a major asset in the balancing flexibility area for both sides. As the Banat region in the close proximity of the border between Serbia and Romania offers a great possibility for the connection of renewable sources, the investments enveloped by this project will most certainly help the safe and reliable evacuation of the produced energy to the systems of interest. | Romania - Serbia - 844 | Romania - Serbia - 1524 - | RO00-RS00 | 680 | 720
342 | Central Balkan Corridor | This corridor will enable transmission of energy from east to west on the border between Bulgaria to Serbia and further towards Montenegro and Bosnia and Herzegovina. This corridor will be directly connected with project Transbalkan corridor (therefore, enabling the connection between Bulgarian energy market and Italian energy market), which represents a direct prerequisite for achieving the expected benefits of the Central Balkan corridor. Among the numerous other positive effects expected once this project is commissioned, the increase of NTCs on the borders between the involved countries (implying both the market integration and additional resources in securing the reliability of transmission systems' operation) can be seen as one of the most prominent. These sections could also prove to be a strong asset in fully utilizing the hydro potentials of Western Serbia, as well as the tool for increasing the security of supply to the demand located in the Central Serbia. In addition, the line from SS Jagodina 4 to SS Pozarevac 3 will enable more efficient evacuation of energy from the RES in Banat and Kostolac regions in Serbia, allowing the higher share of this type of sources in the Serbian generation mix in the upcoming years. | JSC EMS, ESO EAD | BG ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2021 - 2030 (Serbian national TYNDP 2021-2030), page 124; URL: https://ems.rs/wp-content/uploads/2022/07/Plan-razvoja-prenosnog-sistema-2.pdf | 2034 | 2 | True | False | MostlyUpgrade | False |  | These investments will form a new 400 kV corridor from Bulgaria, through Serbia to the border with the Bosnia and Herzegovina and Montenegro. New corridor will enable evacuation of energy from new RES in Bulgaria to the western part of Balkan region and significantly enhance the security of supply in the central parts of Serbia. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | https://ems.rs/wp-content/uploads/2022/07/Plan-razvoja-prenosnog-sistema-2.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Central Balkan corridor, among other investments, also includes strengthening of the interconnections in the CSE region (that involves both EU (Bulgaria) and non-EU countries), enhancing the market integration in the area of interest and, hence, succeeding in reducing the price differentials. As the project envelops the replacement of severely ageing 220 kV infrastructure in Central Serbia with the new 400 kV lines and substations, it is expected to significantly improve the system reliability in this area, thus reducing the possibility of putting the security of supply at risk in some operational regimes. Since the Central Balkan corridor strengthens the connections between Serbia and several neighboring countries, it is most certainly envisaged as valuable improvement regarding the system flexibility, the full impact of which becoming apparent in the light of rapidly developing renewable energy sources in the CSE region. This project affect the RES integration in a manner similar to one relevant for the Project 227 (Transbalkan Corridor), focusing, among other benefits, on strengthening the lines in Western Serbia, near the Drina river, offering great potential for the energy production in the hydro plant capacities. | Montenegro - Serbia - 840 Bosnia-Herzegovina - Serbia - 2310 Bulgaria - Serbia - 1490 | Montenegro - Serbia - 840 - Bosnia-Herzegovina - Serbia - 1200 - Bulgaria - Serbia - 1490 - | BG00-RS00 | 490 | 270
343 | CSE1 New | The project will contribute in strengthen Croatian transmission grid along its main north-south axis (in parallel with eastern Adriatic coast) allowing for additional long-distance power transfers (including cross border) from existing and new planned power plants (RES/wind/ and conventional/hydro and thermal/) in Croatia (coastal parts) and BiH to major consumption areas in Italy (through Slovenia) and north Croatia. The increased transfer capacity will support market integration (particularly between Croatia and Bosnia-Herzegovina) by improving security of supply (also for emergency situations), achieving higher diversity of supply & generation sources and routes, increasing resilience and flexibility of the transmission network. | HOPS, NOS-BIH | BA ;HR | Desetogodišnji plan razvoja hrvatske prijenosne mreže 2022.-2031. s detaljnom razradom za početno trogodišnje i jednogodišnje razdoblje, Croatia, 2022, Page 78-81, Page 106; Dugoročni plan razvoja prenosne mreže 2021-2030, Bosnia-Herzegovina, 343-CSE New 1 page 45, chapter 8.17 | 2035 | 2 | True | False | New | False |  | The Project implies increasing of transfer capacity between HR and BA by construction of new SS 400/110 kV Lika and its connection to an existing SS 400/220/110 kV Melina, SS 400/220/110 kV Konjsko and SS 400/110 kV Tumbri in HR, and to an existing SS 400/110 kV Banja Luka in BA. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True |  |  |  | Bosnia-Herzegovina - Croatia - 500 | Bosnia-Herzegovina - Croatia - 1000 - Croatia - - <1000 | BA00-HR00 | 644 | 298
346 | ZuidWest380 NL Oost | New 380 kV connection between Rilland and Tilburg including new substation. | TenneT-NL | BE ;NL | https://tennet-drupal.s3.eu-central-1.amazonaws.com/default/2024-01/IP2024_Netopland_01-1-2024_0.pdf on page 95 (paragraph 8.2.2) | 2030 | 3 | False | True | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | http://www.zuid-west380kv.nl/ (in Dutch) |  |  | Belgium - The Netherlands - 1000 | Belgium - The Netherlands - 1000 - Belgium - - <1000 The Netherlands - - 1000 - 5000 | BE00-NL00 | 1000 | 0
349 | MaresConnect | MaresConnect is a 750MW HVDC, subsea power interconnector between Ireland (Maynooth) and Wales (Bodelwyddan). MaresConnect will consist of two converter stations – one located close to the final agreed transmission substation in the greater Dublin region and the other close to the Bodelwyddan 400kV substation in Denbighshire – connected by two High Voltage Direct Current cables under the Irish Sea. The cable route passes underground from Bodelwyddan to the coast and heads west under the seabed across the Irish Sea to landfall north of Dublin Bay and continues underground to the final agreed connection point. | MaresConnect Limited | GB ;IE | Ireland: The Irish National Policy Statement on Electricity Interconnection published in July 2023 confirms Ireland’s commitment to further interconnection between Ireland and GB by 2030. Refer to commitment 5 on page 3 of the Policy Statement: https://www.gov.ie/pdf/?file=https://assets.gov.ie/265251/7b3080d8-fa48-4011-9a77-1580abf8a9ff.pdf#page=null. MaresConnect is the only project between Ireland and GB which has applied for regulatory approval in Ofgem’s current window 3 for cap and floor interconnectors and is therefore being advanced by the CRU as the Ireland-GB project with the most realistic prospect of connecting by 2030. In the DNV report which accompanied the Policy Statement, MaresConnect is included in the report, see section 4.3.3 ‘2030 Planned Capacity’ page 8. https://www.gov.ie/pdf/?file=https://assets.gov.ie/265468/14606532-28d5-4108-b315-6c4f6327e64d.pdf#page=null Project Ireland 2040 National Development Plan 2021-2030.: Page 37, 127, The reliability of electricity supplies will be strengthened through investment in the electricity transmission and distribution grid and through further interconnection with other electricity markets, including the Celtic Interconnector to France and further interconnection to the UK. https://www.gov.ie/pdf/?file=https://assets.gov.ie/200358/a36dd274-736c-4d04-8879-b158e8b95029.pdf#page=null The Project is included in All-Island Generation Capacity Statement 2021-2030 . "In Ireland, there is a further interconnector project (MARES Connect) from Ireland to GB, it is part of a wider project that includes a sea water pumped hydro station" (please note the current project excludes the pumped hydro station and is point to point interconnector only). https://www.soni.ltd.uk/media/documents/208281-All-Island-Generation-Capacity-Statement-LR13A.pdf MaresConnect has applied to EirGrid for a connection agreement. Supporting documents are provided with this application as evidence. United Kingdom: MaresConnect is included in the GB Transmission Entry Capacity (TEC) register maintained by National Grid ESO, which can be found at Interconnector Register ¦ ESO (nationalgrideso.com) MaresConnect has entered into GB's framework agreement for the Connection Use of System Code (CUSC) on 1 October 2018 and is required to demonstrate compliance with all aspects of the regulations governing access to GB's national electricity transmission system. Copies of MaresConnect’s current construction agreement and bilateral connection agreement are included as supporting documents with this application. MaresConnect was granted an interconnector licence by Ofgem on 27 June 2022 and as part of the license conditions has agreed to be bound by the UK's 1989 Electricity Act. MaresConnect Limited - Notice of grant of an electricity interconnector licence ¦ Ofgem In addition, in February 2023 Ofgem announced that MaresConnect has passed Ofgem’s interconnector Cap & Floor Window 3 eligibility criteria and will now progress to the next stage. https://www.ofgem.gov.uk/publications/decision-project-eligibility-third-cap-and-floor-window-electricity-interconnectors | 2029 | 3 | True | False | New | False |  | MaresConnect is composed of an HVDC system which shall link the electricity grids of Ireland and Great Britain via submarine cables running between converter stations in Ireland and Wales. It is a High Voltage Direct Current (HVDC) connection capable of providing capacity of 750 MW, flowing in both directions (import / export). This system shall consist of convertor stations at Bodelwyddan in Wales and adjacent to the connection point in the Greater Dublin area, linked by a HVDC submarine cable. At each of these locations there is an interface with the TSO’s 245kV or 400kV AC networks with associated infrastructure including connection bays . | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Please see our website at https://www.maresconnect.ie |  |  | Great-Britain - Ireland - 1450 | Great-Britain - Ireland - 1954 - Ireland - - 1000 - 5000 | IE00-UK00 | 750 | 750
350 | South Balkan Corridor | This project consists of two investments: 400 kV OHL Bitola(MK)- Elbasan(AL) and 400/110 kV SS Ohrid, in Macedonia. The interconnection contributes to increasing the transmission capacity in the East-West direction. The mentioned SS will increase the security of supply in the SouthWest part of the FYR of Macedonia. Construction of 400 kV OHTL interconnection from SS Bitola 2 to Macedonian/Albanian border and SS 400/110 kV Ohrid 400 kV interconnection transmission line Bitola (Macedonia) - Elbasan (Albania) is the last part of the implementation of the Corridor 8 in the context of creating a corridor East-West power transmission corridor between Bulgaria, Macedonia, Albania and Italy. | MEPSO | AL ;MK | 2023 | 2026 | 4 | True | False | New | False |  | The construction of investment 1622 (interconnection Bitola - Elbasan) will enable the connection of investment 1623 (SS Ohrid), it will improve the voltage conditions in the southwestern part of Macedonia and contribute to the security of supply. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | https://author.energy-community.org/enc-author-prd/enc/regionalinitiatives/infrastructure/PLIMA/EL13.html https://www.mepso.com.mk/index.php/en/bit-elb-en/ |  |  |  | Albania - Greece - 1000 - Greece - North Macedonia - 1000 - | AL00-MK00 | 500 | 500
375 | Lienz (AT) - Veneto region (IT) 220 kV | Reconstruction of the existing 220kV-interconnection line between Lienz and Veneto Region (IT). The project includes the adjustment of power regulation devices. | Austrian Power Grid, Terna | AT ;IT | Piano di Sviluppo 2023 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Est - https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete; page n.38, Italy; Austrian: National development plan: http://www.apg.at/en/netz/netzausbau/Netzentwicklungsplan | 2035 | 2 | True | False | Upgrade | True | 2.8 |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | Italian Development Plan: http://www.terna.it/it-it/sistemaelettrico/pianodisviluppodellarete/pianidisviluppo.aspx Austrian: National development plan: https://www.apg.at/en/power-grid/grid-expansion/ | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lower the price differentials between Italy North and Austria market area. This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity. This project will improve the integration of italian RES generation. | Austria - Italy - 500 | Austria - Italy - 1000 - Austria - - <1000 Italy - - 1000 - 5000 | AT00-ITN1 | 500 | 500
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | The project aims at the reconductoring of the already existing 400kV interconnection line between Meliti (GR) and Bitola (MK), in order to increase transfer capacity between the power systems of Greece and North Macedonia. | Admie, MEPSO | GR ;MK |  | 2035 | 1 | True | False | Upgrade | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | In the horizons of the TYNDP 2024 System needs study, opportunity for increasing the cross-border capacity on the GR-MK border is indicated. The project, as an upgrade of the existing Meliti(GR)-Bitola(MK) interconnector, will provide balancing flexibility to the Greek and North Macedonian power systems. Project implementation will contribute to a further improvement of the following ITEG indicators: 2. pushing ratio between nominal transmission capacity and installed RES capacity past 30% | Greece - North Macedonia - 500 | Greece - North Macedonia - 1000 - | GR00-MK00 | 500 | 500
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | This study envisions an upgrade of the existing interconnector VanEyck-Maasbracht between Belgium and the Netherlands making use of PSTs and/or HTLS technology.The study will determine the appropriate implementation option and timing, taking into account - The already planned upgrade of the Zandvliet-Rilland interconnector on the BE-NL border (see project 262) - The synchronisation with developments in the NL-DE border Project motivation: A need has been identified to further develop interconnection capacity on the BE-NL border, hereby alleviating VanEyck-Maasbracht as bottleneck. This project effectively increases the degree of interconnectivity between the Belgian and Dutch bidding zone. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. This project is likely to increase the potential for imbalance netting & reserve sharing due to increased remaining available margins of the cross border transmission capacity. PSTs will also help to balance the flows over the different cross border lines of the Belgian Dutch interconnection. | Elia, TenneT-NL | BE ;NL | NDP1, Belgium, 2020-2030, §4.2.3.1, https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/fr/20190516_plan-de-developpement-federal_fr.pdf | 2032 | 1 | True | False | Upgrade | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | More information about the project can be found following this link: - National Development Plan: https://www.elia.be/nl/infrastructuur-en-projecten/investeringsplannen/federaal-ontwikkelingsplan-2024-2034 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project increases the crossborder capacity between Belgium and the Netherlands. The Project increases the crossborder capacity between Belgium and the Netherlands. The Project increases the crossborder capacity between Belgium and the Netherlands. The Project increases the crossborder capacity between Belgium and the Netherlands allowing the efficient integration of renewables. | Belgium - The Netherlands - 1000 | Belgium - The Netherlands - 1000 - Belgium - - <1000 The Netherlands - - 1000 - 5000 | BE00-NL00 | 1000 | 1000
378 | Transformer Gatica | New tranformer 400/220 kV in existing Gatica subestation, with potential impact in cross border values | Red Eléctrica | ES | Spanish NDP, "Plan de desarrollo de la red de transporte de energía eléctrica.Horizonte 2021-2026" Project Label INT_ESP-FRA_2: Refuerzos interconexión España-Francia (Gatica) pg279 | 2027 | 2 | False | True | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | https://www.planificacionelectrica.es/proyectos ;project label INT_ESP-FRA_2: Refuerzos interconexión España-Francia (Gatica) |  |  |  |  | internalES00
379 | Uprate Gatica lines | Uprate of the following 400kV lines that reach Gatica subestation : Gatica-Gueñes, Gatica-Amorebieta-Ichaso and Gatica-Azpeitia. This internal project has influence in the exchange capacity values between France and Spain, and it is directly related to the P16 Biscay Gulf. | Red Eléctrica | ES | Spanish NDP, "Plan de desarrollo de la red de transporte de energía eléctrica.Horizonte 2021-2026" Project Label INT_ESP-FRA_2: Refuerzos interconexión España-Francia (Gatica) pg279 | 2026 | 2 | False | True | Upgrade | False |  | The uprate to increase the capacity of the 3 400kV lines connected to the Gatica subestation are clustered as they serve for the same purpose and have overloads in case of failure of any of them, when the new project HVDC ES-FR is commissioned and connected to the Gatica subestation | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True | https://www.planificacionelectrica.es/proyectos ;project label INT_ESP-FRA_2: Refuerzos interconexión España-Francia (Gatica) |  |  |  |  | internalES00
1034 | HVDC corridor from Northern Germany to Western Germany | Project 1034 consists of two new HVDC cable from Heide/West to Polsum and from Wilhelmshaven to Region Hamm. The HVDC have a transfer capacity of 2 GW each. The project is a grid expansion project for low-loss transmission of high power over long distances from Northern Germany to the Ruhr-Area. Northern Germany is characterized by a large number of regenerative onshore and offshore energy sources which exceed the demand of Northern German loads. The Ruhr-Area, however, is a high-production region with large conventional generation capacity that has to be substituted by renewable generation capacity due to the German coal phase-out. | Amprion | DE | NDP, Germany, Netzentwicklungsplan 2037 Version 2022, Project DC21 and DC25, pp. 447 | 2032 | 2 | False | True | New | True | 1.4.2 and 1.4.3 | implementation as an energy corridor | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | 5th PCI-List: https://ec.europa.eu/energy/sites/default/files/fifth_pci_list_19_november_2021_annex.pdf The project was part of the previous TYNDP 2022, Link to the Website: https://tyndp2022-project-platform.azurewebsites.net/projectsheets/transmission/1034 Further information of the project, its investments and their necessity particularly for the German Energiewende can be found in the German grid development plan (mostly in German): http://www.netzentwicklungsplan.de/en/front Bundesbedarfsplan 2024 (BBPIG): https://www.netzausbau.de/Vorhaben/ansicht/de.html?cms_gruppe=bbplg&cms_nummer=48 https://www.netzausbau.de/Vorhaben/ansicht/de.html?cms_nummer=49&cms_gruppe=bbplg More detailed information can be found on the project website (in German): https://korridor-b.amprion.net/ Link to the website of the project: https://a-nord.amprion.net/ Link tot he current NDP: https://www.netzentwicklungsplan.de/sites/default/files/2024-04/NEP_2037_2045_V2023_Anhang_2E_Aktualisierung_April_2024.pdf Add Link to the 6th PCI list: Delegated regulation - EU - 2024/1041 - EN - EUR-Lex (europa.eu) |  |  |  |  | DE00-NL00 DE00-DKW internalDE00 | 2950 0 4000 | 300 650 4000
1039 | SE North-south long-term reinforcements | Replacement and upgrading of ageing overhead lines and reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. | Svenska Kraftnät | SE | Systemutvecklingsplan 2022-2031, Sweden, 2021, p. 142. {Available online: https://www.svk.se/siteassets/om-oss/rapporter/2021/svk_systemutvecklingsplan_2022-2031.pdf} | 2040 | 1 | False | True | MostlyUpgrade | False |  | There are two parallel lines under consideration. | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Svenska kraftnät has published a national development plan in 2021. The purpose of the plan is to be an investment plan for the following ten years, 2022-2031. The investment plan presents a detailed look of the projects Svenska kraftnät intends to realize under the stated time period. The plan is available in Swedish through the following link: https://www.svk.se/siteassets/om-oss/rapporter/2021/svk_systemutvecklingsplan_2022-2031.pdf (Swedish) |  |  |  |  | SE02-SE03 | 1000 | 1000
1040 | LirIC | LirIC is a new HVDC sub-sea interconnector between Scotland and Northern Ireland. LirIC is being developed to increase the level of interconnection between Scotland and Northern Ireland addressing a market need and resulting in welfare generation opportunities in GB and consumer benefit in Ireland. A second beneficial driver for the project is the alleviation of Ireland's synchronous generation constraint, where there is an imposed limit on the level of demand that can be met by wind. These two effects result in significant benefit for British exports to Ireland to exploit wholesale power price arbitrage and Irish exports to Britain to avoid wind curtailment. | Transmission Investment | GB | No, however concept positively evaluated in NGESO Network Options Assessment, chapter 6, page 86 - see ref below | 2030 | 1 | False | True | New | False |  | N/A - No clustering | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False |  |  |  | Great-Britain - Island of Ireland - 1450 | Great-Britain - Island of Ireland - 1954 - Island of Ireland - - 1000 - 5000 | UKNI-UK00 | 700 | 700
1041 | GREGY Green Energy Interconnector | GREGY concerns the development of a new green energy highway within the Mediterranean Basin, by interconnecting Egypt and Greece. GREGY aims to interconnect Egypt and Greek mainland with a HVDC submarine cable of about 954 km in length, together with the necessary interconnection infrastructure at the two countries. GREGY will supply renewable power on a permanent basis (8760 h) not exceeding the capacity of 3000MW. GREGY has a bi-directional capability. GREGY will transfer 100% RES generated electricity originating from Wind and PV farms. It will transfer the green energy produced by the 9.5 GW of wind and PV parks that Copelouzos Group has under development in Egypt. Moreover, Egypt’s Sustainable Development Strategy: EGYPT VISION 2030 sets the target at 61GW RES installed capacity by 2035. GREGY will allow 100% RES energy exports, contractually ensured by bespoke Power Purchasing Agreements, from Egypt to Greece, contributing to a significant increase of RES participation in the energy mix and reduction of CO2 emissions of the power sector. Furthermore, benefits such as market coupling, enhanced security of supply and socio-economic welfare are enabled through GREGY establishing a new interconnection between two large synchronous areas. | ELICA MEDITERRANEAN ELECTRICAL INTERCONNECTION SINGLE-MEMBER S.A. | EG ;GR | The project is included in the annual report 2020/2021 of the Egyptian Electricity Holding Company. Also, the Greek TSO i.e., IPTO has confirmed that the project will be included in the next National Development Plan 2024-2033. EEHC annual report and IPTO letter are uploaded on the platform. | 2030 | 1 | True | False | New | True | 2.13 |  | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | GREGY establishes a high capacity connection route between southeast Europe and Egypt along with nearby power systems, enabling electricity trading. Therefore, it will constitute a critical asset towards coupling of power markets of EU with North Africa and the Middle East. Higher transmission capacity will be necessary to accommodate new flows due to higher RES penetration. GREGY can contribute with releasing capacity (602-1081 MW/h) at the borders of Greece with Bulgaria and Italy, in addition to the bi-directional power flow between Egypt and Greece. GREGY interconnector will enable access to new balancing sources for both Greek and Egyptian power systems. The high capacity of GREGY will permit trading of significant volumes of balancing and reserve services, increase flexibility and allow optimal operation of variable RES. Implementation of GREGY transferring 100% RES (which can be 1) consumed in Greece, 2) used for producing green H2, 3) transferred to Europe) shall lead to significant reduction of RES curtailment. Such green energy will be secured by long-term PPAs with RES producers in Egypt |  |  | GR00-EG00 | 3000 | 3000
1046 | Finnish North-South reinforcement | This project consists of several 400 kV overhead lines built in the north-south direction inside Finland (+other required investments to achieve the full capacity). The project is built to increase the North-South transmission capacity thus enabling the integration of new renewable generation in northern Finland and transfer of power to the consumption centers in the south. | Fingrid | FI | Fingrid's Main grid development plan 2024–2033, available here: https://www.fingrid.fi/globalassets/dokumentit/fi/kantaverkko/kantaverkon-kehittaminen/fingrid_kehittamissuunnitelma_26_engb.pdf | 2030 | 3 | False | True | New | False |  |  | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Fingrid's Main grid development plan 2024–2033, available here: https://www.fingrid.fi/globalassets/dokumentit/fi/kantaverkko/kantaverkon-kehittaminen/fingrid_kehittamissuunnitelma_26_engb.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Enables Finland to provide full cross border capacity to Swedish and Estonian borders and thus reduces the price differentials between EU countries. Supports the Finnish carbon neutrality goal 2035 by allowing the replacement of natural gas, coal and oil with clean electricity. Supports the Finnish carbon neutrality goal 2035 by allowing the replacement of natural gas, coal and oil with clean electricity, including fossil free steel, data centers, battery manufacturing and hydrogen. Increases the capability to transmit wind power from the northern and western parts to the southern parts of Finland. |  |  | internalFI00 | 3000 | 3000
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | The project refers to the construction of a submarine DC transmission link of total capacity 600MW interconnecting Egypt's North Mediterranean coast and Greece at the island of Crete, where it will be directly linked there with a new Electrolyser-Hydrogen Production Plant (H2E and H2M) named "Cretan Green Hydrogen Value Chain" (already included in TYNDP 2024 of ENTSO-G) aiming to produce hydrogen from electricity coming from dedicated renewable electricity production tranferred via GAP interconnector. A new HVDC conversion station close to the existing thermal power plant of Atherinolakkos in South-East Crete will be the connection point to Greece. The connection point in Egypt will be at its Northern coast where the bulk of Egypt's electrical load and HV transmission grid infrastructure is located. All the aforementioned installations (converter stations, substations etc) will be of closed type using GIS technology. The proposed GAP interconnection project will enhance energy stability to the Eastern Mediterranean Sea area and promote the European Green Hygrogen technologies and targets. | Greece Africa Power Interconnector SMSA (Member of Eunice Energy Group) | EG ;GR | The project is mentioned in the Ten-year Network Development Plan, Greece, Greece Africa Power Interconnector(1048), page 48623 of The Official Government Gαzette No4789 Β'(12/09/2022), https://www.admie.gr/en/grid/development/ten-year-development-plan, | 2030 | 1 | True | False | New | False |  |  | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | https://eunice-group.com/projects/greece-africa-power-interconnector-gap-interconnector/ | Infrastructure designed to offer more supply options to isolated areas Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The island of Crete is a non completely interconnected Island of Aegean Sea so far. The tranfer capacity of GAP Interconnector will offer more sullpy options to the island's elecricity grid. The proposed project will reduce, through the tranfered energy from Egypt to Greece, the price differentials between EU (Greece) and non-EU countries (Egypt) The proposed project will tranfer to the island of Crete high volumes of elecricity produced by RES from a non EU country (Egypt) and therefore will contribute to cover a part of the non interconnected (so far) island's needs for elecricity. |  |  | GR03-EG00 | 600 | 600
1049 | Cronos Energy Ltd | Cronos Energy Ltd (“Cronos”) is developing a 1400MW DC Bipole VSC interconnector between England and Belgium with the financial support of one of Europe's largest infrastructure funds. Cronos’s management team has a successful track record in developing and delivering interconnectors and transmission projects as well as large-scale grid connected power stations in Europe and has been involved in over 40GW of transmission power station and interconnector projects in Europe. Our mandated technical advisors are DNV and WSP Ltd. Cronos has entered into legally binding connection and construction agreements and has applied for a UK cap & floor regulatory regime for 50% of the project costs in the Third Window in 2023 from the NRA with the other 50% of the project under a Belgian regulated regime (which could be also a cap & floor regime), yet to be applied for. The Project will operate under applicable EU Regulations, including Regulation (EU) 2015/1222. In October 2022 Copenhagen Infrastructure Partners (“CIP”) became the majority shareholder in Cronos and is committed to funding the Project through to operation. | Cronos Energy Ltd | BE ;GB | The project is not in the Belgian federal development plan, but Elia, the Belgian Energy Minister and staff and the Belgian Energy Administration FOD government are aware of the project following numerous exchanges and physical meetings that have taken place, particularly in the 6 months to October 2023. Elia has issued an orientation study in 2023. The Belgian Energy Administration supports the project and has written a letter stating such. | 2031 | 1 | True | False | New | True | 1.20 | Not applicable as the project is not clustered with one or more other projects. | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Cronos Energy Ltd is happy to provide any further information requested https://www.cronos-energy.net/ | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project will connect the GB and BE electricity markets which have different wholesale electricity prices. The electricity flow will be dictated by the difference in the electricity price between those markets (flowing to the higher priced market) reducing the price differential between these countries. The interconnector will allow GB more access to the entire BE electricity generation mix and vice versa. In turn, this increases security of supply, system capacity margin and load factors to maximise output and reliability and minimise the risk of power failures. The Project helps system operators at both ends as it can ramp quickly in response to rapid changes in supply and demand being especially useful in the balancing markets. Responding quickly to price signals at times of system stress is an important tool in managing volatility in different timeframes. The interconnector will reduce the cost and curtailment of renewable energy sources as both GB and BE are building much offshore wind that connects into the coast, and the onshore grid is being reinforced in both countries to maximise the efficiency of both interconnectors and offshore wind. | Belgium - UK - 1400 | Belgium - UK - 1400 - Belgium - - <1000 | BE00-UK00 | 1400 | 1400
1050 | Tarchon Energy Ltd | Tarchon Energy Ltd (“Tarchon”) is developing a 1400MW DC Bipole VSC interconnector between England and Germany with the financial support of one of Europe's largest infrastructure funds. Tarchon's management team has a successful track record in developing and delivering interconnectors, transmission projects and large-scale grid connected power stations, having been involved in over 40GW of such projects in Europe. Our mandated technical advisors are DNV and WSP Ltd. Tarchon has entered into legally binding connection and construction agreements and will apply for a UK cap & floor regulatory regime for 50% of the project costs in the Third Window in 2022 from the NRA with the other 50% of the project regulated in accordance with part 2, chapter 3a of the German Energy Industry Act (Energiewirtschaftsgesetz – EnWG). The Project will operate under applicable EU Regulations, including Regulation (EU) 2015/1222 and Regulation (EU) 2019/943 and EU Forward Capacity Allocation Guideline (Commission Regulation (EU) 2016/1719). In October 2022 Copenhagen Infrastructure Partners (“CIP”) became the majority shareholder in Tarchon and is committed to funding the Project through to operation. | Tarchon Energy Ltd | DE ;GB | Attachment to second TSO draft German Network Development Plan 2037/2045 (12 June 2023) – project overview, see the Tarchon project including its German TSO assessment under project number P329, pages 652/653: NEP_2037_2045_V2023_2_Entwurf_Teil2.pdf (netzausbau.de) | 2030 | 1 | True | False | New | True | 1.21 | Not applicable as the project is not clustered with one or more other projects. | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | Tarchon Energy is happy to supply any further info requested https://www.tarchonenergy.net/ | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project will connect the GB and DE electricity markets which have different wholesale electricity prices. The electricity flow will be dictated by the difference in the electricity price between those markets (flowing to the higher priced market) reducing the price differential between these countries. The interconnector will allow GB more access to the entire DE electricity generation mix and vice versa. In turn, this increases security of supply, system capacity margin and load factors to maximise output and reliability and minimise the risk of power failures. The Project helps system operators at both ends as it can ramp quickly in response to rapid changes in supply and demand being especially useful in the balancing markets. Responding quickly to price signals at times of system stress is an important tool in managing volatility in different timeframes. The interconnector will reduce the cost and curtailment of renewable energy sources as both GB and DE are building much offshore wind that connects into the coast, and the onshore grid is being reinforced in both countries to maximise the efficiency of both interconnectors and offshore wind. | Germany - UK - 1400 | Germany - UK - 2800 - Germany - - 5000 - 10000 | DE00-UK00 | 1400 | 1400
1052 | Lienz (AT) - Malta (AT) - Obersielach (AT) | The 380-kV-ring can be completed in Austria with the reinforcement of the Carinthia transmission grid. The advantages of a ring structure are only made possible by the project. Security of supply in Carinthia and Austria can be guaranteed in the long term. With the 380-kV-ring closure in the south, a redundant connection of the renewable energy feed-in centers in the east Austria (mainly wind and PV) and the load centers with the pumped storage power plants in the central Alpine region. The 380-kV-ring closure is essential for the grid integration of renewable energies and the Austrian Federal Government's climate and energy strategy, and its necessity will also be addressed in the Carinthian Government's 2018-2023 program. The project will also enable the development of additional transmission capacity to the neighboring countries | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, 11-14, 63, https://www.apg.at/en/power-grid/grid-expansion/ | 2033 | 2 | False | True | New | True | 3.28 |  | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | https://www.apg.at/en/power-grid/grid-expansion/ | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Enabling future developments (load/generation). Facilitation of capacities between RES and pump storages in Austria as well as optimisation of cross border flows. Facilitation and optimisation of pump storage connections in the western part of Austria and therefore increasing flexibility. Connecting RES with pump storages. | Austria - Slovenia - 1000 | Austria - Slovenia - 1500 - Austria - - <1000 | AT00-SI00 AT00-ITN1 | 700 500 | 700 500
1054 | 220-kV Westtirol (AT) - Zell/Ziller (AT) | An Upgrade of the existing 220kV-line Westtirol (AT) - Zell-Ziller (AT) and the erection of an additional 220/380kV-transformer. | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, 14-3, 69, https://www.apg.at/en/power-grid/grid-expansion/ | 2030 | 2 | False | True | MostlyUpgrade | True | 2.1.3 |  | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | https://www.apg.at/en/power-grid/grid-expansion/ | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Enabling future developments (load/generation). Facilitation of capacities between RES and pump storages in Austria as well as optimisation of cross border flows. Facilitation and optimisation of pump storage connections in the western part of Austria and therefore increasing flexibility. Connecting RES with pump storages. | Austria - Germany - 3100 | Austria - Germany - 3100 - Austria - - <1000 Germany - - 5000 - 10000 | AT00-DE00 | 600 | 600
1055 | Interconnection of Crete to the Mainland System of Greece | Crete is the largest electrically non-interconnected island system in Greece, representing a particular case, due to large size, rapid growth, remote location and large RES potential. The project aims to increase security of supply and improve stability issues of the island by its interconnection to the mainland system. It is expected to contribute to the reduction of the operation of oil-fired units that currently supply the island and in the long run to allow their progressive decommissioning, thus contributing to the reduction of production variable costs and greenhouse gas emissions. It will allow the full exploitation of local RES potential. The project shall ensure a more reliable and cost-effective supply of electricity to the island. This interconnection will be implemented in two phases. In Phase I (completed), Crete connects to Peloponnese with a 150 kV AC double circuit submarine cable interconnector of 2x200 MVA nominal transfer capacity. In Phase II Crete will be connected to Attica with a bipolar submarine HVDC-VSC link of 2x500 MW capacity transfer. The project in total contributes in achieving the EU-wide targets and policy objectives set in the 2030 climate and energy framework. | Admie | GR | NDP 2024-2033, Greece, 2023, 14.26, p. 59-65, https://www.admie.gr/sites/default/files/2023-10/%CE%94%CE%A0%CE%91%202024-2033%20%CE%A4%CE%B5%CF%8D%CF%87%CE%BF%CF%82%20%CE%88%CF%81%CE%B3%CF%89%CE%BD.pdf | 2025 | 4 | False | True | New | False |  | The final design and implementation of the whole project with its clustering into two Phases imposed by several reasons, technical, financial and environmental. The aim to ensure security of supply for the island is the main reason for undertaking the investment. The rapid increase of electricity demand in the island, along with the need for decommissioning of the local oil-fired generation units, in short term horizon, to comply to the environmental Directives IED 2010/75/ΕΕ (IED) and 2015/2193/ΕΕ (MCPD directive), gave a character of urgency. The advanced level of maturity of the subproject of Phase I in terms of studies (detailed engineering, routing, seabed studies, environmental studies), in terms of financing (acquisition of grants in the framework of NSRF 2014-2020 and loans by EIB), in terms of low risk implementation due to capacity of promoter and its experience by similar AC interconnection projects (Cyclades interconnection to HETS) led to proceed immediately. Thus, the implementation of the Phase I has been started. Regarding Phase II project, it took more time to reach maturity. Phase II is technically more complicated. The need for in depth studies and better organization of the project implementation led IPTO to proceed with Phase II after implementation of major parts of Phase I in order to successfully achieve the best results and obtain the objectives as security of supply, increase of RES penetration, reduction of CO2 emissions, reduction of PSOs, etc. | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | True | True |  | Infrastructure designed to offer more supply options to isolated areas Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Crete, being until recently the largest electrically non-interconnected island system in Greece, operated in autonomous mode. The completion of Phase II of the project will increase security of supply and improve stability issues for the electric system of the island The project will allow the full exploitation of local abundant RES potential, which are subject to limitations imposed by its former autonomous operation and completion of Phase II of the project. |  |  | GR00-GR03 | 800 | 800
1058 | HVDC Interconnector DE-CH | This concept project concerns an extension of German internal HVDC lines towards Switzerland via an additional HVDC interconnector. It pursues an ultimate goal to realise a new HVDC North-South corridor connecting the generation capacities in the North Sea area with the pump storages in the Alps and consumption centres in the Mediterranean sea region. | Swissgrid, TransnetBW | CH ;DE | This project is included in the German National Development Plan 2037/2045 Version 2023. | 2037 | 1 | True | False | New | False |  |  | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | TransnetBW Study “Electricity Grid 2050”, p.47: https://www.transnetbw.de/de/stromnetz2050/content/TransnetBW_Study_ElecricityGrid2050_and_Summary.zip German National Development Plan 2037/2045 Version 2023, p.907: https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2_1.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between Germany and Switzerland and possibility of higher market exchanges, which lead to higher price convergence. The full controllability of the HVDC link between Germany and Switzerland will contribute to the voltage stability and security of supply, which can significantly increase the flexibility of power systems in both countries. The further expansion of RES capacities in Germany, especially offshore wind, leads to increasing RES-curtailment in the coming decades. By increasing the transmission capacity between Germany and Switzerland, the alternative HVDC measure allows a higher German export in hours of high RES infeed. | Germany - Switzerland - 1550 | Germany - Switzerland - 1550 - Germany - - 5000 - 10000 Switzerland - - <1000 | CH00-DE00 | 1000 | 1000
1059 | Southern Italy | New 400 kV lines in Campania and in Calabria, affecting existing 400 kV substation. The link will remove grid constraints and congestions due to the new renewable installed capacity. | Terna | IT | Piano di Sviluppo 2023 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Centro Sud (pag 31-120) https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete | 2030 | 3 | False | True | New | False |  | New 400 kV lines between in Calabria and Campania will reduce congestions by increasing NTC between market zones and integrating new RES power attended in the South of Italy. | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True | Piano di Sviluppo 2023 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Centro Sud (pag 31-120) https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to address system adequacy deficiencies | The new line will allow congestion reduction on the Central-Southern/Southern border, and the integration of the local renewable production. Increase of security of supply |  |  | ITCS-ITS1 ITS1-ITCA | 200 900 | 200 900
1066 | Bulgaria - Turkey | The project concerns the construction of a new AC 400kV interconnection Bulgaria - Turkey. The proposed interconnection line with a total length 150 km will connect Maritsa East 2 SS in Bulgaria and Vize Havza SS in Turkey. This project, together with the project for a new interconnection between Greece and Turkey, compose the project “East Balkan Corridor” that will contribute to increasing the cross -border transfer capacities between ENTSO-E countries and Turkey and address a system need, identified in ENTSO-E's System Needs study. The construction of the two interconnections will also improve the stability of the connection of a large electricity system such as the Turkish one to the unified electricity system of the countries of continental Europe. Furthermore the project will allow integration of more renewables to the grids, support the convergence of market price between the neighboring countries and thus will help the realization of clean energy package targets. | ESO | BG ;TR |  | 2035 | 1 | True | False | New | False |  |  | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False |  |  |  | Bulgaria - Turkey - 2100 | Bulgaria - Turkey - 2100 - | BG00-TR00 | 1100 | 700
1067 | New AC 400 kV interconnection line Greece - Turkey | The project concerns the construction of a new AC 400kV interconnection Greece - Turkey. The proposed interconnection line with a total length 130 km will connect Nea Santa SS in Greece and Babaeski SS in Turkey. This project, together with the project for a new interconnection between Bulgaria and Turkey, compose the project “East Balkan Corridor” that will contribute to the increase of the cross-border transfer capacities between ENTSO-E countries and Turkey and address a system need, identified in ENTSO-E's System Needs study. The construction of the two interconnections will also improve the stability of the connection of a large electricity system such as the Turkish one to the unified electricity system of the countries of continental Europe. Furthermore the project will allow integration of more renewables to the grids, support the convergence of market price between the neighboring countries and thus will help the realization of clean energy package targets. | Admie | GR ;TR | NDP 2024-2033, Greece, 2023, 23.12, p. 297-298 & 21.1, p. 213-214, https://www.admie.gr/sites/default/files/2023-10/%CE%94%CE%A0%CE%91%202024-2033%20%CE%A4%CE%B5%CF%8D%CF%87%CE%BF%CF%82%20%CE%88%CF%81%CE%B3%CF%89%CE%BD.pdf | 2031 | 2 | True | False | New | False |  | The new 400 kV OHL Nea Santa - Filippi is a necessary reinforcement in Greece in order for the new interconnection line between Greece and Turkey to deliver its full potential. | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | The project contributes in reducing high price differentials indicated between Turkey and Greece in the future due to the generation shift, enabling lower and more balanced wholesale prices. Project implementation will enhance transmission capacity between Greece and Turkey and thus will contribute to a further improvement of the 2nd ITEG indicator pushing ratio between nominal transmission capacity and installed RES capacity past 30%. Constrains (e.g. congestions) occur in future scenarios where high flows are exchanged between Greece and Turkey with the current grid. The project contributes in transfer capacity increase, thus minimizing congestions at the GR – TR border. The project, as a new interconnector between Greece and Turkey, will provide balancing flexibility to the Greek and Turkish power systems. | Greece - Turkey - 1600 | Greece - Turkey - 1100 - | GR00-TR00 | 600 | 600
1068 | LaSGo Link | LaSGo Link is a new multi terminal HVDC sub-sea interconnector project linking Sweden, the Island of Gotland and Latvia. The project consists of two sections: a 700MW internal grid reinforcement between the Swedish mainland and the island of Gotland and a 500MW cross border connection between the island of Gotland and Latvia. LaSGo Link is being developed to increase grid capacity to Gotland and increase the level of cross border capacity in the Baltic Sea region. This will meet the current challenge of security of supply experienced in this region and therefore support industry and the further growth of wind power in the Gotland region. The cross border element of the project will provide further routes to market for generation thereby reducing internal grid congestion in Sweden and providing socio-economic benefit to both Sweden, Latvia and the interconnected markets in the Baltic Sea region. | Transmission Investment | LV ;SE | This project is not included in a NDP. | 2037 | 1 | True | False | New | True | 4.11 | The LaSGo Link project is a multi-terminal HVDC link with converter stations sited in Sweden, the island of Gotland and Latvia. The Sweden to island of Gotland section is an internal Swedish grid reinforcement project but is required to support the connection of the cross border element between the island of Gotland and Latvia. Equally the sizing of the Sweden to Gotland section is based on the requirement of the cross border section. These two sections are therefore mutually inclusive and must be realised as a single project to maximise the capital efficiency and socio-economic welfare of the project. | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | False | NOTE BY THE PROMOTERS: Beyond the economic benefits of 500MW of cross border capacity between Sweden and Latvia, the mid-terminal located on the island of Gotland will replace the aging existing HVDC cable connection between the Swedish mainland and Gotland which is expected to come to end of life between 2030 and 2035. This internal grid reinforcement will support the connection of significantly more offshore wind expected to be greater than 1GW in the seas around the island. Furthermore, the project will mitigate current security of supply issues limiting the industrial expansion on the island with a decarbonised energy approach. One example of such is a cement factory that could, with an increase of clean energy supply, reduce their emmissions (that is today 5% of Sweden's total emmissions) towards zero. By improving the economic viability and expansion of local industry and creating further job opportunities on the project itself the project will secure and increase the number of jobs on Gotland, which is critical for the local development. The project will be designed using Voltage Sourced Converter (VSC) technology which will provide further security of supply benefits in the form of frequency/voltage control and stability to the three areas in which it will connect. As part of the early stage development of the project, key participants and stakeholders will be established. The project's grid connection request to the Swedish transmission network has been denied by the Swedish TSO Svenska kraftnät in February 2022. The project promoter has until February 2024 to appeal. NOTE BY ENTSO-E: The project's grid connection request to the Swedish transmission network has been denied by the Swedish TSO Svenska kraftnät in February 2022. |  |  | Lithuania - Sweden - 600 | Lithuania - Sweden - 600 - Latvia - - <1000 | LV00-SE03 | 500 | 500
1074 | Pannonian Corridor | The new 400 kV line connecting Serbian and Hungarian transmission systems, or, more specifically, SS Subotica 3 (RS) and SS Sándorfalva (HU), together with the reconstruction of SS Subotica 3 on Serbian side. Also, this project includes strengthening the North-to-South transmission corridor in Serbian system, by building two new 400 kV lines: SS Sombor 3 – SS Novi Sad 3 and SS Belgrade 50 – SS Sremska Mitrovica 2. This is also deemed necessary, as numerous calculations have indicated that the new tie-line may not affect the NTC value enough if it is not accompanied by the two mentioned internal lines. The project can, alongside covering the needs seen in IoSN report, also be seen as a response to the ever-higher requests for integration of renewable sources in the Bačka region, while simultaneously strongly enhancing the security of supply and reliability of the transmission systems' operation in the included countries. | EMS, MAVIR | HU ;RS | "Plan razvoja prenosnog sistema Republike Srbije za period od 2021. do 2030. godine" (in Serbian, English title: Ten-year development plan of Serbian transmission grid), page 125; URL: https://ems.rs/wp-content/uploads/2022/07/Plan-razvoja-prenosnog-sistema-2.pdf; A magyar villamosenergia- rendszer hálózatfejlesztési terve 2022 (MAVIR Development Plan), page 19, available at: https://www.mavir.hu/documents/10258/239341965/HFT2022_A+magyar+VER+h%C3%A1l%C3%B3zatfejleszt%C3%A9si+terve.pdf/38a57b3b-1323-abe5-b07e-3c99752facdc?t=1676903159479 | 2030 | 2 | True | False | New | True | 2.12 | Each of these investments represents a segment of the new corridor for energy transmission, spanning across Serbian-Hungarian border, simultaneously increasing the NTC on it (which is a need stated in IoSN report) and facilitating the renewable sources integration in the Bačka region (area in the close proximity of the mentioned border). | TYNDP 2020 ;TYNDP 2022 ;TYNDP 2024 | False | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | As the foreseen scope of the project envisages the new interconnection between Serbia and Hungary, it can be seen as another step towards the fully integrated energy market of the CSE region, leading to the noteworthy reduction of the price differentials between the EU and non-EU countries. The additional NTC, vouched for by the commissioning of this project, is expected to be a major asset in the field of system flexibility and stability, especially if the massive capacities of variable RES (several GW), predicted along the routes of its investments, are taken into consideration. As the fully integrated market represents one of the main goals set before the system development plans, the new interconnection enveloped by this project will certainly lead the systems of interest in the desired direction, characterized, among other facets, by the balancing flexibility that ensures the reliable energy supply. Since the Bačka region, in the close vicinity of the border between Serbia and Hungary, has proven to be attractive for the investors in the renewable capacities recently, this project represents a guarantee that the energy evacuation from the newly built sources will happen reliably and safely. | Hungary - Serbia - 500 | Hungary - Serbia - 1000 - Hungary - - 1000 - 50001659 | HU00-RS00 | 500 | 500
1085 | Malta-Italy Cable Link No.2 | The project consists of a new ~122km long 200MWe HVAC electrical cable interconnection through a submarine cable operating at 220kV between Malta (Maghtab) and Sicily (Ragusa) to be laid in parallel but at a safe distance to the existing ac cable link. The project is part of Maltese Government’s future energy strategy in meeting the 2030 climate and energy targets and the longer term decarbonisation objectives. It aims at diversifying the island's energy sources and meet the projected increase in electricity demand from economic growth and electrification of the transport sector. The Project will also strengthen the electricity interconnectivity with the EU electricity network, allow for increased importation of electricity sourced from renewables, optimise the use of local power generation, whilst allowing the increase in local renewable energy sources through the enhancement of the grid stability and balancing of intermittent RES. | Interconnect Malta Ltd | IT ;MT | The Project has been included in the draft update of the Maltese 2030 National Energy and Climate Plan in Section 2.4.2 (II) Pg 56 published in September 2023. Url: https://commission.europa.eu/energy-climate-change-environment/implementation-eu-countries/energy-and-climate-governance-and-reporting/national-energy-and-climate-plans_en | 2026 | 4 | True | False | New | False |  |  | TYNDP 2022 ;TYNDP 2024 | False | False | The Project website: https://icm.mt/projects/ |  |  |  | Malta - - 321 | MT00-ITSI | 225 | 225
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | The project includes several reinforcements mainly in the western part of Estonia. The biggest and most important investments are new Lihula 330 KV substation and Kiisa-Paide 330 kV and Paide-Mustvee 330 kV OHL reconstructions. Together with 330 kV reconstruction also the internal 110 kV network is reinforced where it is foreseen the new RES capacities to be connected. The total effect on connection capability increase of the reconstructions in the western part of Estonia is approximately +200 MW in 110 kV network and +500 MW in 330 kV network. The thermal transmission capacity of the new 330 kV OHL is 1400 MW. Together with the offhsore grid porject reinforcements it will prepare the Estonian power system to be ready to integrate large scale wind parks and additional local RES generation. Together with Offshore project ELWIND the reinforcements allow to increase transmission capacity between Estonia (EE) and Latvia (LV). And in case of EstLink3 these investments also improve to eliminate the internal bottlenects for future possible capacity increase between EE and FI | Elering | EE | Part of national development plan | 01-07-2026 | 4 | False | True | MostlyUpgrade | False |  | The investments are interdependent and the effect of the RES capability increase will be achieved when all investments are completed. | TYNDP 2022 ;TYNDP 2024 | False | False | https://rrf.ee/wp-content/uploads/2021/05/RRP-Taastekava-eelnou_200521.pdf page 199-205 |  |  |  |  | EE00internal | 700 | 700
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | Latvia and Estonia 4th interconnection in addition to connecting two states will enable renewable production connection from western part of both states. Especially the project enables connections of off-shore wind parks from Estonian and Latvian offshore wind areas foreseen in both states maritime spatial plans. The planned commissioning date is tied to spatial plannings and is expected between 2033-2035. | AS Augstsprieguma tikls (AST) and AS ELERING | EE ;LV | NA | 2035 | 2 | True | False | New | True | 5.1 | EE-LV 4th interconnector project currently has two main investments (ID 1755 and ID 1761) for the off-shore wind connection to the transmission network in Latvia and Estonia. The rest of investments are important to internal transfer capacity increase. | TYNDP 2022 ;TYNDP 2024 | False | False | https://www.ast.lv/en/events/ast-and-elering-will-jointly-seek-best-solution-grid-connection-offshore-wind-park-baltic https://elering.ee/en/elering-seeking-solutions-order-connect-estonian-latvian-international-offshore-wind-farm-power https://elering.ee/sites/default/files/2023-02/Security%20of%20Supply%20Report%202022.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The project will increase cross-border capacity on LV-EE cross-border as well as integrate additional amount of off-shore RES Project will ensure power system reserve sharing among Baltic States countries The project is in hybrid solution which will integrate up 2000 MW of offshore wind |  | Estonia - Latvia - 700 - Estonia - - <1000 Latvia - - <1000 | EE00-OBZ OBZ-LV00 | 1000 1000 | 1000 1000
1092 | TritonLink: offshore hybrid HVDC interconnector Belgium – Denmark | The construction of a dual-purpose offshore hybrid HVDC interconnector between Belgium and Denmark integrating 4 GW of offshore wind in the Danish Exclusive Economic Zone in the North Sea. This project creates a first transmission link between the Danish and Belgian electricity transmission systems. It is an offshore hybrid project due to merging two purposes: i) interconnecting two countries and ii) connecting offshore RES. | Energinet and Elia Transmission Belgium | BE ;DK | NDP 2024-2034, Belgium, 2023, ID 4, p128, https://www.elia.be/nl/infrastructuur-en-projecten/investeringsplannen/federaal-ontwikkelingsplan-2024-2034 | 2036 | 2 | True | False | New | True | 4.2 | TritonLink entails an offshore hybrid interconnector between Belgium and Denmark integrating the offshore wind on the new Danish Energy platform hub and is split into two investments with interconnections going to Belgium and Denmark. Both interconnections are needed to integrate the planned 4GW of offshore wind of the Danish Energy Island to the onshore systems. | TYNDP 2022 ;TYNDP 2024 | False | False | https://www.elia.be/nl/infrastructuur-en-projecten/infrastructuurprojecten/tritonlink | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The project increases crossborder capacity between Belgium and Denmark. The project increases crossborder capacity between Belgium and Denmark and as such increasing the adequacy of both countries. The project increases crossborder capacity between Belgium and Denmark. Due to its hybrid configuration, it also integrates 4GW offshore wind. The project increases crossborder capacity between Belgium and Denmark. Due to its hybrid configuration, it also integrates 4GW offshore wind. |  | Belgium - - <1000 Denmark - - <1000 | BE00-DKOBZ DKW1-DKOBZ | 2000 1400 | 2000 1400
1094 | Estlink 3 | 3rd HVDC connection between Finland and Estonia. On FI side also includes 400 kV transmission network upgrade and extension to the landing point to connect Estlink 3 converter station to the rest of the transmissions system. The landing point is expected to be Inkoo substation, but is not yet decided. On EE side the project also includes existing 330 kV transmission network upgrade (L346, L347, L360, L506), new grid elements (Tallin area grid reinforcement) and extension of the existing grid to the landfall location to connect Estlink 3 converter station to the rest of the transmissions system. Planned landfall is located in Aulepa. | Fingrid and Elering | EE ;FI | Included in the latest EE and FI national development plan | 2035 | 2 | True | False | New | True | 3.6 | On the Finland side, getting full capacity of Estlink 3 will likely require at least Inkoo-Hikiä 400 kV reinforcement. | TYNDP 2022 ;TYNDP 2024 | False | False | The concept is investigated for example in Fingrid's network vision: https://www.fingrid.fi/globalassets/dokumentit/fi/kantaverkko/kantaverkon-kehittaminen/fingrid_network_vision.pdf EE national development plan: https://elering.ee/sites/default/files/2023-02/Security%20of%20Supply%20Report%202022.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Capability for Black Start & Islanding Operation Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Last years and future perspectives are showing very high price differences between Estonia and Finland market areas. Additional market capacity between these areas are necessary to be implemented. After Baltics syncronization with Continental Europe synchronous area the major challenge is to ensure system stability and to be ready for islanding in case of extreme contingencies. The capability to ensure frequency stability in case of major faults is based on HVDC links that provide fast frequency control. New HVDC link will provide additional black start capabilities in both Finland and Estonia power system. The need for black start capability will be increased in the future due to higher risk of islanding of Baltics and replace conventional generation with RES. With significant increase of RES in Estonia and Finland especially with off- and on-shore wind parks additional transfer capacities are required. It allows to increase export and import for maximum utilization of cost efficient RES generation in both sides of the system. |  | Estonia - Finland - 700 - Estonia - - <1000 | EE00-FI00 | 700 | 700
1095 | Aurora line 2 (4th AC Finland-Sweden north) | Fourth AC 400 kV overhead line between Finland north and Sweden SE1. Strengthening the AC connection between Finland and Sweden is necessary due to market needs, security of supply in the Nordics, new RES generation and substantial investmentents in clean hydrogen economy. | Fingrid, Svenska Kraftnät | FI ;SE | NDP available here (Project name in NDP: "Aurora Line 2"): https://www.fingrid.fi/globalassets/dokumentit/fi/kantaverkko/kantaverkon-kehittaminen/fingrid_kehittamissuunnitelma_26_engb.pdf | 2032 | 2 | True | False | New | True | 3.5 |  | TYNDP 2022 ;TYNDP 2024 | False | False | The line is in Fingrid's National Development Plan: https://www.fingrid.fi/globalassets/dokumentit/fi/kantaverkko/kantaverkon-kehittaminen/fingrid_kehittamissuunnitelma_26_engb.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to address system adequacy deficiencies Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) | Adds market capacity 800 MW. Adds market capacity 800 MW. Contributes to all three interconnection targets. Improves local power balance and mitigates risk of power failures in Sweden and Finland. Supports the connection of energy intensive industry especially in Northern Sweden. | Finland - Sweden - 1700 | Finland - Sweden - 2500 - | FI00-SE01 | 800 | 800
1096 | Beznau - Mettlen | This project • increases the capacity between Switzerland and its northern neighbours. This enables to connect large renewable generation in Northern Europe to pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. • comprises the optimization of the existing route by voltage conversion to 380 kV and a partial reinforcement. | Swissgrid | CH | Bericht zum Strategischen Netz 2025, Switzerland, 2015, page 184, https://www.swissgrid.ch/dam/swissgrid/projects/future-grid/sg2025-technical-report-de.pdf | 2031 | 3 | False | True | MostlyNew | False |  | timely and electrical vicinity to the other investment | TYNDP 2022 ;TYNDP 2024 | False | True | https://www.swissgrid.ch/content/swissgrid/en/home/projects/project-overview/beznau-birr.html https://www.swissgrid.ch/content/swissgrid/en/home/projects/project-overview/niederwil-obfelden.html https://www.swissgrid.ch/en/home/newsroom/newsfeed/20221020-01.html | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to address system adequacy deficiencies | This project contributes to lowering the price differentials between Switzerland, Germany and Austria. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. | Germany - Switzerland - 1550 | Germany - Switzerland - 1550 - Germany - - 5000 - 10000 Switzerland - - <1000 | CH00-DE00 | 0 | 700
1097 | Upgrade to Konti-Skan | This project will add 1000 MW transfer capacity between DK1 and SE3. Additional analyses have fixed the capacity at 1000 MW, compared to previous project data. Existing connections Konti-Skan 1 & 2 (700 MW) will be decommissioned at the end of their technical lifespans in the mid-2030s. After decommissioning of old connections and commissioning of this project, the transfer capacity between DK1 and SE3 will be 1000 MW. | Svenska kraftnät, Energinet | DK ;SE | 10-Year Grid Investment Plan 2020-2029, Sweden, 2019, p.26: Available online: {https://www.svk.se/siteassets/om-oss/rapporter/2020/10-year-development-plan-2020-2029.pdf} | 2036 | 2 | True | False | MostlyNew | False |  |  | TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies | The project adds 1000 MW of transfer capacity between SE3 and DK1 and will contribute to the increased social economic welfare in the European electricity market. The project contributes with 1000 MW transfer capacity between Sweden and Denmark, which contributes with system adaquacy | Denmark (West) - Sweden - 1200 | Denmark (West) - Sweden - 1700 - Denmark - - <1000 | DKW1-SE03 | 700 | 700 | While the planned project upgrades the existing interconnection with 300 MW, this decision was made too late to be incorporated in TYNDP2024. The datasheet therefore reflects the previous plan which consisted of a 700 MW upgrade to the existing Interconnection.
1098 | Offshore Wind LT 2 | Second stage for integration of additional 700 MW off-shore wind farms in Baltic Sea near Lithuania coast. Connection to 330 kV Darbenai substation. | LITGRID AB | LT | "Development plan of the electric power system and transmission grid. 2021-2030" (https://www.litgrid.eu/uploads/files/dir580/dir29/dir1/10_0.php), June 2021, pages 23, 26. | 2030 | 2 | False | True | New | False |  |  | TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) | New offshore wind farms will provide sufficient electricity meeting demand increase (electrification of transport sector, P2H, electrolysers). New offshore wind farms will ensure decarbonization of energy intensive industry (green hydrogen for industry). |  |  | LTOffshore | 700 | 700
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | The project consists in the modernization of an existing double-circuit 400 kV line between the Hradec and Röhrsdorf substations on the Czech side. The project will be implemented only in the section located in the Czech Republic, on an existing route so as to minimize environmental impacts and appropriation of additional land. The project contributes to maintaining reliable supply for domestic demand in case of power shortage in the Czech Republic, using imports from surplus generation in the north of Germany. | CEPS | CZ ;DE | Ten-year investment plan for the development of the TS 2021 – 2030, CZ, 2021, V445/446 – Upgrade, 103 pg., https://www.ceps.cz/en/transmission-system-development | 2028 | 3 | True | False | Upgrade | False |  |  | TYNDP 2022 ;TYNDP 2024 | False | False | Information about Czech development plan can be found on the following link below on the CEPS website: https://www.ceps.cz/en/transmission-system-development |  |  | Czech Republic - Germany - 1000 | Czech Republic - Germany - 1000 - Germany - - 5000 - 10000 | CZ00-DE00 | 0 | 500
1102 | Mettlen - Ulrichen | This project * increases the capacity between Switzerland and its northern neighbours. This enables to connect large renewable generation in Northern Europe to pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. * comprises the optimization of the existing route by voltage conversion to 380 kV and a partial reinforcement. | Swissgrid | CH | https://www.swissgrid.ch/dam/swissgrid/projects/strategic-grid/sg2025-technical-report-de.pdf | 2034 | 3 | False | True | MostlyNew | False |  | no clustering | TYNDP 2022 ;TYNDP 2024 | False | True | https://www.swissgrid.ch/content/swissgrid/en/home/projects/project-overview/mettlen-ulrichen.html | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to address system adequacy deficiencies | This project contributes to lowering the price differentials between Switzerland, Germany and Austria. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. | Germany - Switzerland - 1550 | Germany - Switzerland - 1550 - Germany - - 5000 - 10000 Switzerland - - <1000 | CH00-DE00 | 200 | 0
1103 | Bickigen - Chippis | This project * increases the capacity between Switzerland and its northern neighbours. This enables to connect large renewable generation in Northern Europe to pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. * comprises the optimization of the existing route by voltage conversion to 380 kV and a partial reinforcement. | Swissgrid | CH | Bericht zum Strategischen Netz 2025, Switzerland, 2015, page 184, https://www.swissgrid.ch/dam/swissgrid/projects/future-grid/sg2025-technical-report-de.pdf | 2027 | 3 | False | True | MostlyUpgrade | False |  | no clustering | TYNDP 2022 ;TYNDP 2024 | False | True | https://www.swissgrid.ch/content/swissgrid/en/home/projects/project-overview/bickigen-chippis.html | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to address system adequacy deficiencies | This project contributes to lowering the price differentials between Switzerland, Germany and Austria. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. | Germany - Switzerland - 1550 | Germany - Switzerland - 1550 - Germany - - 5000 - 10000 Switzerland - - <1000 | CH00-DE00 | 0 | 500
1104 | Bauler - Roost | It is planned to upgrade the capacity of the existing 220 kV overhead line between the substations Roost-Flebour-Bauler by implementing High Temperature Low Sag (HTLS) conductors. | Amprion, Creos | DE ;LU | NDP1; Germany, Netzentwicklungsplan 2035 Version 2021, Project 505, p. 680; NDP LUX 2040 Version 2021 p.26 | 2025 | 2 | True | False | Upgrade | False |  | high priority on upgrading existing transmission OHL between Flebour and Bauler for Creos. | TYNDP 2022 ;TYNDP 2024 | False | True | Further information of the project, its investments and their necessity particularly for the German Energiewende can be found in the German grid development plan (mostly in German): http://www.netzentwicklungsplan.de/en/front |  |  | Germany - Luxemburg - 400 | Germany - Luxemburg - 400 - Germany - - 5000 - 10000 Luxemburg - - <1000 | DE00-LUG1 | 400 | 400
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | Georgia-Romania Black Sea submarine interconnection project will connect Georgian power system (and South Caucasus region) to Synchronous grid of Continental Europe. Mentioned project will assist energy security of European Union and Caucasus region, support development of renewable energy sector, increase transit opportunities and trade options between European Union and South Caucasus region which will have positive impact on electricity producers and transmission system operators. Based on preliminary data, construction of double-circuit 500 kV between existing 500 kV SS Jvari and new 500 kV SS Anaklia will be constructed. The next part will be two-pole 500 kV DC submarine cable Anaklia-Constanta. In order to implement such connection, construction of 500/500 kV DC converter station with installed capacity of 2x500 MW at Anaklia substation is considered. Implementation of this project may require additional reinforcement of high voltage network of mentioned interconnected power systems. Feasibility study of the Georgia-Romania Black Sea submarine transmission and digital line construction project has commenced on May 11, 2022 and be finalized in 2024. | JSC Georgian State Electrosystem (GSE) | GE ;RO | Ten-Year Network Development Plan of Georgia 2023-2033, Georgia, 2023, p 68, https://https://www.gse.com.ge/communication/Publications/Ten-Year-Network-Development-Plan-of-Georgia | 2031 | 1 | True | False | New | False |  | Since the project is under consideration, the parameters of its constituent components have not been currently clarified. | TYNDP 2022 ;TYNDP 2024 | False | False | Project website: https://www.gse.com.ge/projects/international-projects/Black-Sea-Submarine-Cable-Project | Infrastructure to address system adequacy deficiencies Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | For the years of 2030, 2035 and 2040 adequacy of Project involved countries (South Caucasus and South-East Europe) will be improved by the BSSC project. Implementation of the BSSC Project leads to reduction of reserves for Georgia, Romania and Hungary. For instance, by 785 MW for 2030 year, by 1,091 MW for 2040 year and by 1,137 for 2050 year. Since, the HVDC will be implemented with VSC technology it has high possibility to control voltage and reactive power at connection point, in result facilitates control of voltage profile. |  |  | GE00-RO00 | 1000 | 1000
1106 | Bornholm Energy Island (BEI) | Both Parties aim to establish an innovative new hybrid offshore interconnection between the Danish Zealand, the Danish Island of Bornholm, and Germany by 2030. This hybrid interconnector, referred to as the “Bornholm Energy Island Project” (BEI) is not only intended as an interconnection between both countries, but also to integrate 3 GW of offshore windfarm capacity, located southwest of Bornholm, in the Exclusive Economic Zone of Denmark. The Parties have the ambition to realise this via a multi-terminal, multi-vendor DC solution (MTDC) on the island of Bornholm, which would be a technical novelty for the European transmission grid. Moreover, the Parties want to establish a true energy hub, with the possibility for future extensions including the connections of further interconnectors to other countries or possibly the integration of additional generation or load, including but not limited to Power-to-X facilities. With this project, the Parties aim to support the EU Commission’s new Green Deal and climate targets, help to reduce the overall CO2 emissions of the European energy system and strengthen the integration of the internal European electricity market as well as security of supply. | Energinet, 50Hertz | DE ;DK | The BEI project is included in the last National Development Plan of Germany: NEP Strom 2037/2045 version 2023, Germany, 2023, P640, page 891 - 894, https://www.netzentwicklungsplan.de/sites/default/files/2023-07/NEP_2037_2045_V2023_2_Entwurf_Teil2.pdf , (German National Development Plan). In the Danish case, the upcoming Danish 'Strategic Investment Plan' will include the BEI project. The BEI project is presently analyzed in various feasibility studies at wider regional level. | 2030 | 1 | True | False | New | True | 5.2 | The BEI investment items need to be clustered and thereby realised together to meet its full benefit. The investment items are mutually dependent on each other. Realising one investment contributes to the realisation of the full potential of another investment item. Without the wind farm connections, the configuration would merely provide interconnection while the RES integration would still require additional (radial) connections to shore. And without the interconnection links, the concept would be a single hub to shore, while missing the opportunities of European-wide market integration and sharing of reserves. Presently, all investments in the BEI project are ‘under consideration’, with a provisional commissioning for 2030. | TYNDP 2022 ;TYNDP 2024 | False | False | The cooperation by the Project Partners build on a Letter of Intent signed in January, 2021, following a Letter of Intent signed by the Danish and German ministries in December, 2020 (https://www.bmwi.de/Redaktion/DE/Downloads/J-L/letter-of-intent-between-german-minister-denmark-minister-hybrid-offshore.html). https://www.50hertz.com/en/News/FullarticleNewsof50Hertz/id/7388/50hertz-and-energinet-sign-letter-of-intent-for-offshore-hub-bornholm-energy-island-in-the-baltic-sea https://ens.dk/en/our-responsibilities/wind-power/energy-islands/denmarks-energy-islands https://en.energinet.dk/Green-Transition/Energy-Islands |  |  |  | Germany - - 5000 - 10000 Denmark - - <1000 | DE00-BolEnergy BolEnergy-DKE1 | 2000 1200 | 2000 1200
1109 | Basilicata - Campania reinforcements | New 400 kV lines between Basilicata and Campania and in the northern area of Benevento will increase the southern/northern artery, will reduce congestions by increasing NTC between market zones and will integrate new RES power attended in the South of Italy. | Terna SpA | IT | Piano di Sviluppo 2023 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Centro Sud (pag.172-184) https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete | 2035 | 2 | False | True | New | False |  | New 400 kV lines between Basilicata and Campania and in the northern area of Benevento will increase the southern/northern artery, will reduce congestions by increasing NTC between market zones and will integrate new RES power attended in the South of Italy. | TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase RES integration |  |  | ITCS-ITS1 | 500 | 500
1110 | Sicily - Calabria | New 400 kV subsea cable between Sicilia and Calabria will increase NTC between market zones and will integrate new RES power attended in Sicily and reduce dispatching cost for the system. | Terna SpA | IT | Piano di Sviluppo 2023 - Avanzamento Piani di Sviluppo Precedenti - Avanzamento Centro Sud (pag 181) https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete | 2027 | 3 | False | True | New | False |  |  | TYNDP 2022 ;TYNDP 2024 | False | False | Piano di Sviluppo 2023 - Avanzamento Piani di Sviluppo Precedenti - Avanzamento Centro Sud (pag 181) https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase RES integration |  |  | ITCA-ITSI | 500 | 500
1112 | GRITA 2 | The project concerns a new interconnection between Italy and Greece, strengthening the GR-IT border by the development of a new HVDC link that will operate along with the existing HVDC link between the two countries. The project consists of a new HVDC terrestrial and submarine link of 1000 MW between the Italian and Greek transmission systems. The presence of two interconnections will increase transfer capabilities and guarantee higher reliability in terms of power exchanges between Italy and Greece in order to address future challenges and EU targets set. | TERNA; IPTO | GR ;IT | Italian NDP 2023- Piano di Sviluppo / page 36/https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete / NDP 2024-2033, Greece, 2023, 24.4, p. 305-307, https://www.admie.gr/sites/default/files/2023-10/%CE%94%CE%A0%CE%91%202024-2033%20%CE%A4%CE%B5%CF%8D%CF%87%CE%BF%CF%82%20%CE%88%CF%81%CE%B3%CF%89%CE%BD.pdf | 2031 | 2 | True | False | New | False |  |  | TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project contributes in reducing price differentials indicated between Italy and Greece in the future due to the generation shift, enabling lower and more balanced wholesale prices. TYNDP IoSN study indicates infrastructure opportunities at the specific border. The project, as a new interconnector between Italy and Greece, will provide balancing flexibility to the Greek and Italian power systems. The project will allow the exploitation of RES potential located in west Greece and south Italy and will reduce future RES curtailments in Italy and Greece. | Greece - Italy - 1500 | Greece - Italy - 500 - Italy - - 1000 - 5000 | ITS1-GR00 | 1000 | 1000
1121 | 220-kV Hessenberg (AT) - Weißenbach (AT) | Increase of Renewables is political and societal goal. This project is needed to connect wind and PV generation in the relevant areas to the transmission system and brings also an increase of the security of supply as the capacities increase. | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, 19-4, 75, https://www.apg.at/en/power-grid/grid-expansion/ | 2030 | 2 | False | True | Upgrade | False |  |  | TYNDP 2022 ;TYNDP 2024 | False | True | https://www.apg.at/en/power-grid/grid-expansion/ | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) | Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. The project provides the opportunity to integrate additional electrolysers in the region. Through the project, there is an opportunity to decarbonize and integrate additional energy intensive industry in the region. |  |  | ATInternal | 600 | 600
1122 | Offshore Wind farm connection Centre Manche 1 | 320 kV HVDC hub in Normandy, connecting a 1 GW offshore wind project (Centre Manche 1) and 250 MW from a second offshore wind project (Centre Manche 2) to the onshore 400 kV substation of Menuel. | RTE | FR |  | 2032 | 3 | False | True | New | True | 4.3 | na | TYNDP 2022 ;TYNDP 2024 | False | False | https://www.rte-france.com/projets/nos-projets/projet-deolien-en-mer-au-large-de-la-normandie | Infrastructure to address system adequacy deficiencies Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection Centre Manche 1 is needed to connect future offshore windfarms and therefore contribute to the increase of renewable energy share in the generation mix. An HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. The offshore Wind Connection Centre Manche 1 is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the NSOG Offshore Grid Corridor (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 GW of offshore wind installed capacity. |  |  | FROffshore | 1250 | 0
1123 | Offshore Wind farm connection Centre Manche 2 | 320 kV HVDC hub in Normandy, connecting a 1250 MW offshore wind project (Centre Manche 2) to the onshore 400 kV substation Tourbe. | RTE | FR |  | 2033 | 2 | False | True | New | True | 4.4 | na | TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection Centre Manche 2 is needed to connect future offshore wind farms and therefore contribute to the increase of renewable energy share in the generation mix. An HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. The offshore Wind Connection Centre Manche 2 is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the NSOG Offshore Grid Corridor (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 GW of offshore wind installed capacity. |  |  | FROffshore | 1250 | 0
1124 | Offshore Wind Connection South Britanny | 750 MW Offshore HVAC wind hub connecting two different floating windfarms | RTE | FR |  | 2031 | 2 | False | True | New | True | 8.1 | na | TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection South Britanny is needed to connect future offshore windfarms and therefore contribute to the increase of renewable energy share in the generation mix. The offshore Wind Connection South Britanny is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the Atlantic Offshore Grids (AOG) Corridor (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 GW of offshore wind installed capacity. |  |  | FROffshore | 750 | 0
1125 | Offshore Wind Connection Occitanie | 750 MW offshore wind connection hub, connecting two different floating windfarms | RTE | FR |  | 2031 | 2 | False | True | New | True | 6.1 | na | TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection Occitanie is needed to connect future offshore wind farms and therefore contribute to the increase of renewable energy share in the generation mix. The offshore Wind Connection Occitanie is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the South and West Offshore Grids (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 GW of offshore wind installed capacity. |  |  | FROffshore | 750 | 0
1126 | Offshore Wind Connection PACA | 750 MW offshore wind connection hub, connecting two different floating windfarms | RTE | FR |  | 2032 | 2 | False | True | New | True | 6.2 | na | TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection PACA is needed to connect future offshore wind farms and therefore contribute to the increase of renewable energy share in the generation mix. The offshore Wind Connection PACA is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the South and West Offshore Grid Corridor (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 GW of offshore wind installed capacity. |  |  | FROffshore | 750 | 0
1127 | Offshore Wind Connection South Atlantic Oléron 1 | 320 kV HVDC connecting a 1 200 MW offshore wind project to the 400kV existing network | RTE | FR |  | 2033 | 2 | False | True | New | True | 8.2 | Investment needed to minimise offshore wind spillage | TYNDP 2022 ;TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection South Atlantic Oléron 1 is needed to connect future offshore wind farms and therefore contribute to the increase of renewable energy share in the generation mix. An HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. The offshore Wind Connection South Atlantic Oléron 1 is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the Atlantic Offshore Grid Corridor (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 GW of offshore wind installed capacity. |  |  | FROffshore | 1250 | 0
1134 | GiLA | GiLA is a 2 x 1200 MW, 320 kV HVDC project which is designed to reduce unsustainable network constraints on RTE assets between Bordeaux area and Nantes area at the 2034 horizon. It is also designed as a dual purpose (internal hybrid) project, allowing the connection of two offshore wind farms of up to 1,2 GW each. | RTE | FR |  | 2034 | 1 | False | True | New | False |  | 1 | TYNDP 2024 | False | False |  | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project contributes to the development of transfer capacity between Spain and France by alleviating internal congestions close to the border The project is designed to reduce unsustainable network constraints on RTE assets between Bordeaux area and Nantes area. An HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. The project allows the connection of two offshore wind farms of up to 1,2 GW each (TYNDP2024 projects 1161 and 1665). |  |  | FR00Internal | 0 | 0
1138 | 400 kV OHL Suceava (RO) - Balti (MD) | The project consists of a 400kV single circuit OHL Suceava (Romania) - Balti (Moldova), a new 400kV OHL Suceava (RO) - Gadalin (RO) and a 400/330 kV substation in Balti (Moldova). The project will increase transmission capacity between Romania and Republic of Moldova, allowing creating the necessary premises for the development of electricity production from renewable sources in both countries, through the development of the energy infrastructure necessary for the integration of renewable energy into the national energy systems, the expansion of the electricity market at the EU level and the reduction of bottlenecks in the energy infrastructure, through greater flexibility and sustainability of the two energy systems. | Transelectrica | MD ;RO | Planul de dezvoltare a RET perioada 2022-2031 - submitted in June 2022 for approval to the Romanian NRA , https://web.transelectrica.ro/noutati/noutati/55_2020.08.17_14-30-42.pdf; Plan razvoja prenosnog sistema Republike Srbije za period 2019 - 2028, Serbia, 2019-2027, page 115 | 2030 | 2 | True | False | New | False |  | It would not be possible to put the 400kV Suceava - Balti interconnection into operation without the new substation 400/330kV in Balti (MD) and the new 400kV OHL Suceava - Gadalin in Roamania. | TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to offer more supply options to isolated areas | It will eliminate overloads currently occurring in the transmission and distribution sections of National Power System. It will reduce the power losses in Power Transmission Grid and in 110kV Distribution Grid with 4MW and will increase the security of supply for consumers in the region It will increase with 600MW the capacity of the Romanian PS to integrate the new RES capacities to be installed in the N-E region of Romania. Currently, in this region the renewable power plants have a disadvantageous connection solution due to the long distance to the transmission network The new 400 kV OHL will increase the transfer capacity between ENTSO-E/Romania and the Republic of Moldova with 400 MW. It also has a positive impact for the interconnected operation of the Continental European System on the interface between Romania – Hungary – Slovakia – Poland and Republic of Moldova – Ukraine. It will increase the safety of the Republic of Moldova power supply and allow an efficient transfer of electricity between ENTSO-E/Romania and Moldova, eliminating the current disadvantages due to the existence of a single interconnection line of 400kV, OHL Isaccea(RO)-Vulcănești(MD), which spans 57 km, with 51 km traversing through Ukraine. |  |  | MD00-RO00 | 350 | 350
1139 | 380-kV Westtirol (AT) – Zell/Ziller (AT) | Reinforces a structural bottleneck in the Austrian transmission grid and enables the integration and interaction of new pumped storage power plants, and PV in the Alps. | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, Chapter 3.2, 33, https://www.apg.at/en/power-grid/grid-expansion/ | 2037 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False | APG NDP: https://www.apg.at/en/power-grid/grid-expansion/ Austrian integrated network infrastructure plan: https://www.bmk.gv.at/themen/energie/energieversorgung/netzinfrastrukturplan.html | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | The project improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. Facilitation and optimisation of pump storage connections in the western part of Austria and therefore increasing flexibility. Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. The project allows additional RES integration, which will also decarbonize the hydrogen sector with increased usage of electrolysers. |  |  | ATInternal
1140 | 380-kV St. Peter (AT) - Dürnrohr (AT) | Increases in east-west transportation possibilities. Integration of RES (mainly PV). Integration of new industrial load centers to achieve climate targets in Austria. | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, Chapter 3.2, 33, https://www.apg.at/en/power-grid/grid-expansion/ | 2037 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False | APG NDP: https://www.apg.at/en/power-grid/grid-expansion/ Austrian integrated network infrastructure plan: https://www.bmk.gv.at/themen/energie/energieversorgung/netzinfrastrukturplan.html | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | Increase of Austrian German interconnection level The project improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. The project allows additional RES integration, which will also decarbonize the hydrogen sector with increased usage of electrolysers. |  |  | AT00-DE00 | 500 | 600
1145 | 380-kV Obersielach (AT) - Hessenberg (AT) | Integration of large amounts of RES in the federted states of Styria and Carinthia. | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, Chapter 3.2, 33, https://www.apg.at/en/power-grid/grid-expansion/ | 2035 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False | APG NDP: https://www.apg.at/en/power-grid/grid-expansion/ Austrian integrated network infrastructure plan: https://www.bmk.gv.at/themen/energie/energieversorgung/netzinfrastrukturplan.html | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | The project improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. The project allows additional RES integration, which will also decarbonize the hydrogen sector with increased usage of electrolysers. |  |  | ATInternal | 0 | 0
1153 | PST romands | new or substituted PSTs in the following substations: Verbois, St Triphon, Riddes, Châtelard | Swissgrid | CH |  | 2030 | 1 | False | True | New | False |  | timely and electric vicinity to the other investments | TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to address system adequacy deficiencies | This project contributes to lowering the price differential between Switzerland and France. The project enhances flexibility in the distribution of flows between Switzerland, France and neighbouring countries. Project has positive impact on SoS indicator. |  |  | CH00-FR00 | 800 | 800
1155 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT) | Integration of large amounts of RES im east of Austria. | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, 23-16, 107, https://www.apg.at/en/power-grid/grid-expansion/ | 2032 | 2 | False | True | New | False |  |  | TYNDP 2024 | False | False | APG NDP: https://www.apg.at/en/power-grid/grid-expansion/; | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | The project improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. The project allows additional RES integration, which will also decarbonize the hydrogen sector with increased usage of electrolysers. |  |  | ATInternal
1156 | 380-kV Greater Vienna (AT) - Hessenberg (AT) | Integration of large amounts of industry and RES in the federal states of Styria, Lower Austria and Vienna. | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, Chapter 3.2, 33, https://www.apg.at/en/power-grid/grid-expansion/ | 2033 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False | APG NDP: https://www.apg.at/en/power-grid/grid-expansion/; Austrian integrated network infrastructure plan: https://www.bmk.gv.at/themen/energie/energieversorgung/netzinfrastrukturplan.html | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | The project improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. The project allows additional RES integration, which will also decarbonize the hydrogen sector with increased usage of electrolysers. |  |  | ATInternal
1157 | HG North Tyrrhenian Corridor | The project consists of a new 500kV HVDC link between Italy's Central South and the North market areas, particularly between the Lazio and Lombardy regions. The new HVDC is characterized by marine cables from the Montalto node to Avenza, where a DC OHL-underground cable transition is expected. | Terna | IT |  | 2032 | 2 | False | True | New | False |  |  | TYNDP 2024 | False | False |  | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase of security of supply increase RES integration |  |  | ITCS-ITN1 ITCS-ITCN | 2000 800 | 2000 0
1158 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT) | To allow the grid integration of the planned renewable energy generation (mainly wind power and PV) in the north-eastern part of Austria ("Weinviertel") the transmission grid infrastructure has to be enforced and new substation for the connection needs to be erected. | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, Chapter 3.2, 33, https://www.apg.at/en/power-grid/grid-expansion/ | 2037 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False | APG NDP: https://www.apg.at/en/power-grid/grid-expansion/; Austrian integrated network infrastructure plan: https://www.bmk.gv.at/themen/energie/energieversorgung/netzinfrastrukturplan.html | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | The project improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. The project allows additional RES integration, which will also decarbonize the hydrogen sector with increased usage of electrolysers. |  |  | ATInternal
1159 | 220-kV Bisamberg (AT) – Wien Südost (AT) | Increase of Renewables is political and societal goal. This project is needed to connect wind and PV generation in the relevant areas to the transmission system and brings also an increase of the security of supply as the capacities increase. | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, 23-4, 65, https://www.apg.at/en/power-grid/grid-expansion/ | 2033 | 2 | False | True | MostlyUpgrade | False |  |  | TYNDP 2024 | False | False | APG NDP: https://www.apg.at/en/power-grid/grid-expansion/; | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | The project improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. The project allows additional RES integration, which will also decarbonize the hydrogen sector with increased usage of electrolysers. |  |  | ATInternal
1161 | Offshore Wind Connection South Atlantic Oléron 2 | Connection of 1200MW offshore wind project (Oléron 2) | RTE | FR |  | 2035 | 1 | False | True | New | True | 8.2 |  | TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection South Atlantic Oléron 2 is needed to connect future offshore wind farms and therefore contribute to the increase of renewable energy share in the generation mix. An HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. The offshore Wind Connection South Atlantic Oléron 2 is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the Atlantic Offshore Grid Corridor (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 MW of offshore wind installed capacity. |  |  | FR00Internal | 1200 | 0
1162 | Offshore Wind Connection Fécamp-Grand Large 1 | Connection of 2 GW offshore wind project (Le Havre 1) to the French onshore grid. | RTE | FR |  | 2035 | 1 | False | True | New | False |  | na | TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection Le Havre 1 is needed to connect future offshore windfarms and therefore contribute to the increase of renewable energy share in the generation mix. An HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. The offshore Wind Connection Le Havre 1 is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the NSOG Offshore Grid Corridor (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 GW of offshore wind installed capacity. |  |  | FR00Internal | 2000 | 0
1163 | Offshore Wind Connection Fécamp-Grand Large 2 | Connection of 2 GW offshore wind project (Le Havre 2) to the French onshore grid. | RTE | FR |  | 2037 | 1 | False | True | New | False |  | na | TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection Le Havre 2 is needed to connect future offshore windfarms and therefore contribute to the increase of renewable energy share in the generation mix. An HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. The offshore Wind Connection Le Havre 2 is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the NSOG Offshore Grid Corridor (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 GW of offshore wind installed capacity. |  |  | FR00Internal | 2000 | 0
1164 | Offshore Wind Connection Golfe de Lion Centre | Connection of 2GW of offshore wind to the French onshore grid in the area of Fos-sur-mer. | RTE | FR |  | 2037 | 1 | False | True | New | False |  | na | TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection Fos is needed to connect future offshore wind farms and therefore contribute to the increase of renewable energy share in the generation mix. An HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. The offshore Wind Connection Fos is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the South and West Offshore Grid Corridor (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 GW of offshore wind installed capacity. |  |  | FR00Internal | 2000 | 0
1165 | Offshore Wind Connection Golfe de Gascogne Sud | Connection of 1200MW offshore wind project (Charente Maritime) | RTE | FR |  | 2037 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection Charente Maritime is needed to connect future offshore wind farms and therefore contribute to the increase of renewable energy share in the generation mix. An HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. The offshore Wind Connection Charente Maritime is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the Atlantic Offshore Grid Corridor (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 GW of offshore wind installed capacity. |  |  | FR00Internal | 1200 | 0
1166 | HG Adriatic Corridor | The project foresees the development of DC links between Puglia and Emilia-Romagna regions. Specifically, the new HVDC will be realised thanks to the reuse of future existing routes converted into DC and two new conversion stations in the nodes of Forlì and Foggia, on the basis of the most suitable and available sites for construction. The first part of the project, from Foggia to Fano will be commissioned in 2032. | Terna | IT |  | 2036 | 2 | False | True | New | False |  |  | TYNDP 2024 | False | False |  | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase of security of supply increase RES integration |  |  | ITCS-ITCN ITCS-ITS1 ITCN-ITN1 | 500 600 2000 | 500 600 2000
1167 | HG Central link | The Central Link, from Umbria to Tuscany regions, will allow a transmission capacity increase through the existing 220 kV backbone between Villavalle and S. Barbara thanks to the use of innovative pylons with low electromagnetic impact called "5F", without exceeding the limitations of the magnetic field. The project involves the reconstruction of the current 220 kV AC backbone from Villavalle to S.Barbara, through the use of new technologies, which involve the reconstruction of existing assets with more efficient capabilities in order to achieve an increase in exchange power of 600 MW between the ITcs and ITcn market areas. Furthermore, with the aim of optimizing the management of energy exchanges along the 220 kV backbone, reactive compensation devices and machines for managing power flows (PST) will be appropriately installed. | Terna | IT | Piano di Sviluppo 2023: https://www.terna.it/en/electric-system/grid/national-electricity-transmission-grid-development-plan | 2031 | 2 | False | True | New | False |  |  | TYNDP 2024 | False | False | [5 empty] | ITCS-ITCN | 600 | 600
1168 | HG Ionian-Tyrrhenian Corridor | The project consists in the reuse of existing AC backbones and converted in DC through a set of new conversion stations in the Priolo, Rossano and Latina nodes based on the availability of the most suitable sites for construction, giving priority to existing assets and dismissed industrial areas. The project will allow the increase of the current the exchange limit between three sections: ITsi-ITca, ITca-ITs, and ITs-ITcs, favouring greater bidirectional transits between themselves. | Terna | IT | Piano di Sviluppo 2023: https://www.terna.it/en/electric-system/grid/national-electricity-transmission-grid-development-plan | 2035 | 2 | False | True | New | False |  | The project will allow to increase the exchange limit on the Italian Ionian-Tyrrhenian corridor with a contribute of 2GW for each investment across the following sections: ITsi - ITca, ITca - ITs, ITs - ITcs | TYNDP 2024 | False | False | [5 empty] | ITSI-ITCA ITS1-ITCA | 2000 2000 | 2000 2000
1169 | SAPEI 2 | The Sardinian cluster consists of two main works, the first involves a new direct current submarine link between Sardinia and the Italian peninsula, while the second work consists of modernisation of the 220 kV grid within Sardinia, through the use of innovative low electromagnetic impact supports called '5F', without exceeding the limitations of the magnetic field. The new direct current submarine link called SAPEI 2, in VSC technology, will connect the existing Fiumesanto station in Sardinia and the Montalto station in Lazio. The new link will have a capacity of 1000 MW and will provide for the expansion of the existing node of Fiumesanto through the construction of a new conversion station and the construction of a new submarine connection link that will be located at the DC bus bar of the future Montalto conversion station. In addition to the new marine connection, the reconstruction of the internal 220 kV backbone of the Sardinian grid from Codrongianos to Sulcis and Selargius, by new technologies, which envisage the reconstruction of existing assets with more efficient capacities. | Terna |  | Piano di Sviluppo 2023 Il progetto Hypergrid e necessità di Sviluppo infrastrutturale (pag 69-74) https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete | 2040 | 2 | False | True | New | False |  |  | TYNDP 2024 | False | False | Piano di Sviluppo 2023 Il progetto Hypergrid e necessità di Sviluppo infrastrutturale (pag 69-74) https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete |  |  |  |  | ITSA-ITCS | 1000 | 1000
1171 | Interconnection IT-CH | New Interconnection 400kV on Italy-Switzerland border | Terna; Swissgrid | CH ;IT | Piano di Sviluppo 2023 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Ovest, https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete; page 24 | 2038 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lower the price differentials between Italy North and Switzerland market areas. This project will contribute to reducing system adequacy deficiencies by increasing transmission capacity. This project will improve the integration of Italian RES generation. |  |  | CH00-ITN1 | 1000 | 1000
1182 | EHV S/S Thesprotias and its connection to the 400 kV System | The project includes the development of a new EHV S/S in Western Greece (EHV S/S Thesprotia) and its connection to the System of 400 kV. The new EHV S/S will be connected with a new 400 kV double circuit interconnection line of increased thermal limit to EHV S/S Arachtos and is to serve two new cross-border connections with Albania and Italy, while also contributing in strengthening the stability of the Transmission System in the area and increasing its transmission capacity to serve the growing penetration of RES units. | IPTO | GR | NDP 2024-2033, Greece, 2023, 24.2, p. 301-302, https://www.admie.gr/sites/default/files/2023-10/%CE%94%CE%A0%CE%91%202024-2033%20%CE%A4%CE%B5%CF%8D%CF%87%CE%BF%CF%82%20%CE%88%CF%81%CE%B3%CF%89%CE%BD.pdf | 2031 | 2 | False | True | New | False |  | Connection of new substation to the grid. | TYNDP 2024 | False | False |  | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure to reduce price differentials between EU and/or non-EU countries | The project is an internal reinforcement to serve two new cross-border connections with Albania and Italy, while also contributes to increasing transmission capacity in the area to serve the growing penetration of RES units. The project is a necessary internal reinforcement for the two new cross-border connections with Albania and Italy. The TYNDP IoSN study indicates infrastructure opportunities at the AL-GR and GR-IT borders. The project, as a necessary reinforcement to support the new interconnections with Albania and Italy, will provide balancing flexibility to the Greek and neighboring power systems. The project, as a necessary reinforcement to support the new interconnections with Albania and Italy, will contribute in reducing price differentials between Greece - Italy and Greece - Albania. |  |  | AL00-GR00 | 1200 | 1200
1183 | New interconnection line 400 kV Greece - Albania | The new interconnection will be developed with a single circuit OHL 400 kV that will be connected to the new EHV SS Thesprotia in Western Greece and to the new Substation Fier in Southern Albania. The project is expected to increase the transmission capacity between the two countries by at least 200 MW in both directions, facilitate the penetration of more RES into the two Systems, enhance market price coupling and contribute to the achievement of the goals for the transition towards a climate neutral Europe. | IPTO, OST | AL ;GR | NDP 2024-2033, Greece, 2023, 24.3, p. 303-304, https://www.admie.gr/sites/default/files/2023-10/%CE%94%CE%A0%CE%91%202024-2033%20%CE%A4%CE%B5%CF%8D%CF%87%CE%BF%CF%82%20%CE%88%CF%81%CE%B3%CF%89%CE%BD.pdf | 2030 | 2 | True | False | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project contributes in reducing price differentials indicated between Albania and Greece in the future due to the generation shift, enabling lower and more balanced wholesale prices. TYNDP IoSN study indicates infrastructure opportunities at the specific border. The project, as a new interconnector between Albania and Greece, will provide balancing flexibility to the Greek and Albanian power systems. The project will allow the exploitation of RES potential located in west Greece and south Albania and will reduce future RES curtailments in Albania and Greece. |  |  | AL00-GR00 | 200 | 200
1185 | South Coast Offshore Transmission Project | South Coast Offshore Transmission (SCOT) Project includes the development of two new offshore substations to be located within Maritime Area A (Tonn Nua) of the south coast designated maritime area plan, new onshore and offshore electricity cables, onshore transmission equipment as required to accommodate connection to the existing onshore transmission system. This infrastructure will facilitate up to 900MW of power generated by wind farms in Irish waters. In March 2023, the Irish Government published the "Accelerating Ireland’s Offshore Energy Programme; Policy Statement on the Framework for Phase Two Offshore Wind". This policy identified EirGrid as the developer of new offshore grid transmission infrastructure. On the basis of the policy, EirGrid has initiated SCOT Project, this will be the first state led offshore renewable electricity connection in Ireland. North Seas Energy Corporation published the tendering and construction target plan for NSEC countries’ offshore projects including Ireland’s ORESS 2.1 project in south coast in November 2023. EirGrid is advancing this project and the most up to date information can be found here: https://www.eirgrid.ie/community/projects-your-area/shaping-our-offshore-energy-future | EirGrid PLC | IE | The map provided shows the proposed South Coast Designated Maritime Area Plan (DMAP) as identified by the Irish Government. This DMAP is a proposed geographical area within which future offshore renewable energy development may take place. The South Coast Offshore Transmission project will be located within this DMAP area and will facilitate the connection of new offshore generation. In March 2023, Government adopted the "Accelerating Ireland’s Offshore Energy Programme", Policy Statement on the Framework for Phase Two Offshore Wind. This policy states that "To expedite delivery, EirGrid will proactively develop offshore grid transmission infrastructure, which will connect offshore projects to onshore nodes on the South coast, including offshore substations and submarine cable connecting offshore substations to the onshore grid". This policy also states that the location of the Phase 2 offshore wind aligns with the availability of onshore grid capacity identified by EirGrid in the Shaping Our Energy Future v1.1 - Technical Roadmap Report document published in 2023 which can be found here: https://www.eirgridgroup.com/site-files/library/EirGrid/Shaping-Our-Electricity-Future-Roadmap_Version-1.1_07.23.pdf This study demonstrates that the indicated generation amount in the South Coast Offshore Transmission Project can be accommodated into the Irish transmission system. In particular, Table 13 showing the regional disposition of offshore wind including generation in the study areas IE Area H2 and IE Area I which encompass the South Coast (The study areas are illustrated geographically in Figure 14 on page 84). Also, Figure 15 (page 88) illustrates the generation spatial distribution including generation off the south coast of Ireland. The results of the overall Transmission Analysis are discussed in Section 6.4 (pages 94 to 104). | 2030 | 1 | False | True | New | False |  | n/a | TYNDP 2024 | False | False | The project was launched in 2023 after the publication of the National Policy and this is the first application for TYNDP. A letter of support from Government Department of Environment, Climate and Communications is attached to the application. EirGrid have conducted studies to assess possible connection methods for these offshore generation projects on the South Coast of Ireland. The exact connection methods are subject to further optioneering, environmental assessment and public consultation as the development is at a very early stage. EirGrid has publicly launched the project and has commenced engagement with the local communities. The public website for the project is available here: https://www.eirgridgroup.com/the-grid/offshore/ | Mitigate the risk of power failures Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The connection of additional generation in the South Coast would mitigate power failures STATCOMs will be installed at Onshore Compensation Compound, they are available for both reactive power support during offshore export, and for general system support. STATCOMs are by default meant to improve reactive power/voltage controlability SCOTP will connect offshore wind farms which are successful in the ORESS Tonn Nua auction to the national grid. This RES will contribute to the target of generating at least 5GW of offshore wind energy by 2030 as contained in Ireland’s National Energy and Climate Plan. The South Coast Offshore Transmission Project will support Ireland’s non-binding agreement on offshore renewable generation goals for the priority offshore grid corridor, Northern Seas Offshore Grids (NSOG), in accordance with Article 14(1) of the TEN-E Regulation (EU) 2022/869 |  |  | IE00Internal | 800 | 800
1192 | HansaLink - Phase 1 | The hybrid interconnector project comprises two onshore HVDC converter stations and an offshore multi-terminal HVDC converter station able to accommodate 2GWs of offshore wind generation located in UK Waters. The two onshore converter stations will be located in Scotland and Germany, respectively. The HVDC converters are a rigid bi-pole design, each rated at 2GW and operating at +/- 525kV. The HVDC subsea/onshore cable circuit has an indicative route length of approximately 800km - to be finalised once the offshore platform location has been determined and the onshore/subsea cable routing confirmed. Analysis undertaken by WindGrid shows that project yields a positive CBA and provides multiple social economic welfare benefits, including enhanced security of supply, reduced curtailment, increased RES integration, and reduced CO2. | WindGrid | DE ;GB |  | 2033 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False | https://www.eliagroup.eu/en/windgrid |  |  |  |  | DE00-UK00
1193 | HansaLink - Phase 2 | The hybrid interconnector comprises an offshore multi-terminal HVDC converter station able to accommodate an additional 2GWs of offshore wind generation located in UK Waters. The HVDC converter is a rigid bi-pole design, rated at 2GWs and operating at +/- 525kV. This Phase 2 project follows-on from the Germany-UK Hybrid Interconnector Phase 1 project (#1192) and utilises the HVDC subsea cabling system installed during Phase 1. Analysis undertaken by WindGrid shows that project yields a positive CBA and provides multiple social economic welfare benefits, including enhanced security of supply, reduced curtailment, increased RES integration, and reduced CO2. | WindGrid | DE ;GB | no | 2035 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False | https://www.eliagroup.eu/en/windgrid |  |  |  |  | DE00-UK00
1197 | NU-Link Interconnector | The NU-Link interconnector project is a proposed 1200MW High Voltage Direct Current (HVDC) subsea interconnector between Great Britain and the Netherlands. | Frontier Power International Limited, Kansai Electric Power Company, TEPCO Power Grid Inc, Transnet BW | GB ;NL |  | 2031 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False | [5 empty] | NL00-UK00 | 1200 | 1200
1200 | Hybrid interconnector Norway-Sørvest F Windfarm-Continent (DK, DE or BE) | Statnett was in 2023 by the Norwegian Ministry given the task to plan for one or more hybrid interconnectors connecting the Sørvest F windfarm area to Norway as well as to other country/countries around the North Sea. MoUs have been signed between Statnett and TSOs of Denmark, Germany, Netherland and Belgium aiming to develop one or more hybrid interconnectors. In the first phase we are planning for a 1400 MW hybrid interconnector, but a 2000 MW interconnector might as well be evaluated. At this stage all the alternatives are considered equal. Step 1 (1500 MW) of Sørvest F windfarm was awarded in Q1/2024 and is planned radial connected. Step 2 is planned awarded in 2025 and will potential be hybrid connected. Further steps might be expected, as the potential of Sørvest F windfarms is in the range 6-12 GW. The motivation of the project is both to develop Norwegian offshore wind as well as to increase flexibility and energy-exchange between hydro- and wind-dominated areas. | Statnett together with Energinet, TenneT Germany, Amprion and Elia | BE ;DE ;DK ;NO | The project is included in the last version of Norwegian System Development Plan, to be published 1st of November 2023. https://www.statnett.no/for-aktorer-i-kraftbransjen/planer-og-analyser/systemutviklingsplan/ (The publication is in Norwegian only and a translation of the project will be uploaded after 1st of November) | 2035 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Mitigate the risk of power failures Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | In periods of windy/sunny weather, the European price level might be very low, indicating power-flow from the Continental system to Norway. In periods of low wind/sun and cold temperatures the European prices might get very high, indicating power-flow from Norway to the Continental system. Both will reduce price differentials between EU and non-EU countries. The future European energy system will be more and more weather-dependent. Flexibility between hydro-dominated and wind/solar-dominated areas and between different synchronous systems will be very important to solve the challenge, hence mitigating the risk of power failures. The project will facilitate both windfarms of the area Sørvest F, as well as facilitate more renewable production both in the Nordic and the Continental synchronous system. Hence, the conceptual hybrid interconnector is supposed to enable cost-efficient grid connection of high volumes of RES and reduce RES curtailment. The project is covering one of the analysed corridors of ENTSO-E's ONDP 2024 showing positive cost/benefit. This both in the 2040- and the 2050-horizon. |  |  | DE00-NO00 | 1400 | 1400
1201 | Reinvestment of Skagerrak 1 and 2 | The existing interconnectors Skagerrak 1 and 2 (500 MW in total) were commissioned in 1976 and 1977 and are at the end of their technical life. The cables are expected to be in operation until 2026 with normal maintenance. The risk of failures is increasing and major repairs will be less and less rational with time. The Norwegian TSO (Statnett) and the Danish TSO (Energinet) are considering to build a new 700 MW interconnector as a replacement of the ones that soon are expected to be decommissioned. MoU has been signed between Statnett and Energinet. More changes of capacity are expected in the next decades, as the technical lifetime of Skagerrak 3 is estimated to the year 2042. The capacity NO-DK is therefore calculated to 1700 MW (2023) - 1200 MW (2027 - dependent on decommissioning of Skagerrak 1 and 2) – 1900 MW (2035) – 1400 MW (2043). The motivation of the project is both to secure necessary flexibility between Denmark and Norway as well as keep the necessary energy-exchange between hydro- and wind-dominated areas. | Statnett and Energinet | DK ;NO | The project is included in the last version of Norwegian System Development Plan, to be published 1st of November 2023. https://www.statnett.no/for-aktorer-i-kraftbransjen/planer-og-analyser/systemutviklingsplan/ (The publication is in Norwegian only and a translation of the project will be uploaded after 1st of November) | 2035 | 2 | True | False | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Mitigate the risk of power failures Infrastructure to address system adequacy deficiencies Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | In periods of windy/sunny weather, the European price level might be very low, indicating power-flow from the Continental system to Norway. The opposite in periods of low wind/sun and cold temperatures. Both will reduce price differentials between EU and non-EU countries. The future European energy system will be more and more weather-dependent. Flexibility between hydro-dominated and wind/solar-dominated areas and between different synchronous systems will be very important to solve the challenge, hence mitigating the risk of power failures. The future European energy system will be more and more weather-dependent. Flexibility between hydro-dominated and wind/solar-dominated areas and between different synchronous systems will be very important to solve the challenge, hence mitigating the adequacy deficiencies. The project facilitates more renewable production both in the Nordic and the Continental synchronous system. This due to the increase of transmission capacity and then the increased flexibility between the countries. Hence, the project will enable cost-efficient grid connection and reduce RES-curtailment. |  |  | DKW1-NOS0 | 700 | 700
1202 | Increased capacity Norway-Finland, Back-to-Back | By installing a Back-to-Back converter or similar technical solution in the new Seidafjellet station (planned to replace the current Varangerbotn station) on the 220 kV line between Norway and Finland, the power flow will be better controlled and by this the cross-border capacity on existing 220 kV line Varangerbotn-Ivalo will be better utilised. Motivation for the project is both to take benefits of the possible increase of cross-border market-capacity, facilitate green transition (increased wind-production and demand-electrification) as well as to increase the system-reliability. From a European energy-perspective the project is important as it contributes to a more reliable LNG-production in northern Norway. | Statnett and Fingrid | FI ;NO | The project is included in the last version of Norwegian System Development Plan, to be published 1st of November 2023. https://www.statnett.no/for-aktorer-i-kraftbransjen/planer-og-analyser/systemutviklingsplan/ (The publication is in Norwegian only and a translation of the project will be uploaded after 1st of November) | 2030 | 2 | True | False | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Mitigate the risk of power failures Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | In periods of high wind/sun/nuclear production, the Finnish price level might be very low, indicating power-flow from the Finland to Norway. The opposite in periods of low wind/sun and cold temperatures or wet/windy periods in north of Norway. All situations will reduce price differentials The future European energy system will be more and more weather-dependent. Flexibility between hydro-dominated and wind/solar-dominated areas and between different countries will be very important to solve the challenge, hence mitigating the risk of power failures. The project improves voltage stability by offering reactive power controllability of converters. This will both lead to increased capacity between Norway and Finland in both directions, facilitate new RES-production and increase the security of supply of the region in both countries. The project will increase capacity between NO-FI and based on this both facilitate more RES which helps decarbonizing other sectors. Among them also the LNG-production in northern Norway, which from a European perspective is important as it contributes to a more reliable LNG-production. |  |  | FI00-NON1 | 150 | 150
1203 | Offshore Wind Connection Bretagne Nord-Ouest | Connection of 1,2 GW offshore wind project (North Atlantic) to the French onshore grid. | RTE | FR |  | 2040 | 1 | False | True | New | False |  | na | TYNDP 2024 | False | False |  | Infrastructure to address system adequacy deficiencies Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The offshore Wind Connection North Atlantic is needed to connect future offshore wind farms and therefore contribute to the increase of renewable energy share in the generation mix. An HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. The offshore Wind Connection North Atlantic is needed to connect future offshore wind farms and is designed to optimize the evacuation of the produced energy. This project is part of the Atlantic Offshore Grid Corridor (TEN-E Priority Offshore Grid Corridor). The project will contribute to reach the French 2050 target of 45GW and the European target of >300 GW of offshore wind installed capacity. |  |  | FR00Internal | 1200 | 0
1207 | 380kV Niederstedem-Bertrange/Bofferdange | This project comprises the replacement of the 220 kV cross border line between Niederstedem (DE) and Bertrange/Bofferdange (LU) by an 380 kV overhead line. | Amprion, Creos | DE ;LU | NEP_2037_2045_V2023_2_Entwurf_Teil2,Germany,2023,P601,p813,https://www.netzentwicklungsplan.de/ | 2037 | 2 | True | False | Upgrade | False |  |  | TYNDP 2024 | False | False | [5 empty] | DE00-LUG1 | 1200 | 1200
1208 | Medlink | Medlink is a 4000MW HVDC modular transmission project between Italy and Northern Africa with integrated RES generation. The project consists of two links, respectively between Northern Italy (La Spezia) and Algeria (Annaba) and between Central-Northern Italy (Suvereto) and Tunisia (Marsa Dhib), allowing integration with Italian system without requirements for any network upgrade. The interconnector is configured for bidirectional power flow and for renewable generation being injected into the grid of the host countries and exported, therefore an "off-shore hybrid" set-up. The total route length of the project is 1575km of which: 975km for the link with Algeria and 600 km with Tunisia. The power size of each link is 2000MW (in bipoles) while the DC voltage is +/- 52kV DC. The HVDC-VSC technology will be adopted for the four converter stations. The project will allow a total of about 25TWh of new renewable energy (a mix of wind, solar and BESS) to be injected into the host countries energy market and exported into the European electricity system, substantially contributing to the Italian and EU's decarbonization target, decongesting | Zhero Europe B.V | DZ ;IT ;TN |  | 2030 | 1 | True | False | New | False |  | Medlink is a modular and scalable system of 4GW in total which comprises of two links (Algeria-Italy and Tunisia-Italy) of 2GW of capacity each. Being an integrated project with new RES generation, the project is also expected to include new AC lines to connect generation sites with new conversion station in both Algeria and Tunisia. The length of the AC lines has currently been estimated in accordance with the most accurate information available and could be subject to further review once site investigation and onshore routing surveys will be completed. | TYNDP 2024 | False | False | www.medlinks.net |  |  |  |  | ITCN-TN00Isolated DZ00Isolated-ITN1 | 2000 2000 | 2000 2000
1209 | Latvia and Lithuania cross-border strengthening project | The Latvia and Lithuania cross-border strengthening project includes new cross-border OHL constructions between existing substation in Latvia (Broceni) and new substation in Lithuania (Varduva). The project includes existing interconnection reconstruction from Grobina substation in Latvia to Derbenai substation in Lithuania to increase the total amount of cross-border capacity up to 1000 MW on Latvia and Lithuania cross-border. The project includes additional substation reconstructions for new OHL connection. The specific preliminar study initiated by Lithuanian TSO (Litgrid) and Latvian TSO (AST) about a need of cross-border capacity increase and other benefits has been finished and it prooved that cpacity increase on LV-LT cross-border after 2035 is justified. | AS Augstsprieguma tikls and Litgrid AB | LT ;LV | It is included in the Latvian National Development plan of Transmission system, Latvia, 2023, Chapter 5.4, page 30-35 | 2035 | 2 | True | False | New | False |  | Both investments are increasing the total cross-border capacity on Lithuania and Latvia cross-border from 500 MW to 700 MW. More detailed study is between TSOs currently is going on. | TYNDP 2024 | False | False |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | According to high offshore and onshore RES developments in Baltic States internal grid strenghtening is valuable and beneficial. Increase capacity for reserve sharing among Baltic States countries. Project will help to distribute planned high amount of offshore and onshore RES in Baltic States, preparing for electrification of comming new technologys like Electrolysers. Project will help to distribute planned high amount of offshore and onshore RES in Baltic States, preparing for electrification of comming new technologys like Electrolysers. |  |  | LT00-LV00 | 1000 | 1000
1210 | APOLLO-LINK | 'APOLLO-Link - The Mediterranean Solar Bridge' is an electricity transmission project establishing a new interconnector between Spain and Italy. It will constitute the first direct bidding zone border between Spain and Italy North with a capacity of 2,000 MW. This interconnector will promote European electricity market integration, boost the exchange of renewable energy and re-enforce the East-West connections of the EU's power sector by connecting Italy North's high-load zone with Spain's substantial renewable generation. The project is scheduled to be commissioned in 2032 and its design is based on Bipolar HVDC connection with VSC converters at 525kV with a thermal capacity of 2,091 MW. It is making use of the new 2GW HVDC transmission standard to promote the standardisation of transmission development projects in Europe. APOLLO-LINK also generates substantial annual net social welfare gains, estimated at well beyond 100 M€ p.a. after accounting for investment, maintenance and operation costs. It synergizes with planned Italian network developments, such as the Hyperlink extension to Milan and enhancing regional energy infrastructure efficiency. This initiative embodies sustainability and interconnectivity, contributing to Europe's renewable energy targets. | OMNIA GmbH | ES ;IT |  | 2032 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False | www.apollo-link.eu | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The interconnector will establish a new bidding zone border between Italy and Spain facilitating a decrease of the price spread between the two zones by enabling electricity to flow from the cheaper to the more expensive zone. The interconnector will enable cross-border balancing energy exchange including imbalance netting, thus reducing costs for balancing services for both connected TSOs. The interconnector is expected to reduce the need for curtailment of RES by helping to export the electricity that cannot be consumed domestically. |  |  | ES00-ITN1 | 2000 | 2000
1211 | Baltic WindConnector (BWC) | The Parties aim to establish a hybrid offshore interconnector between Germany and Estonia, Latvia by 2037. Referred to as the “Baltic WindConnector (BWC)”, the aim of the project is to integrate offshore wind with an installed capacity of 2 GW from Estonia and Latvia to all three countries, given the estimated large offshore wind potential. The project provides additional cross-border trading capacity between the Baltic States and Germany and hence contributes to the integration of Baltic States into the common EU wholesale electricity market. With BWC security of supply is increased in all three countries and the larger Baltic Sea region. This will be further investigated throughout the project development. Through efficiently integrating offshore wind and by reducing overall CO2 emissions in the European electricity system, the BWC project supports the EU Commission’s Green Deal and climate targets. Furthermore, the Parties will further investigate potential synergies between the BWC project and Latvia and Estonia Hybrid Offshore Interconnector (Project ID 1088). Related to this project are the EE-LV 4th connection and 330 kV grid on the EE island Saaremaa. | 50Hertz, Elering, AST | DE ;EE ;LV |  | 2037 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False | https://www.50hertz.com/en/News/FullarticleNewsof50Hertz/13472/50hertz-and-estonian-transmission-system-operator-elering-to-build-submarine-cable-between-estonia-and-germany https://www.elering.ee/en/elering-and-50hertz-explore-possibilities-build-submarine-electricity-cable-between-estonia-and | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) |  |  |  | EEOF-DE00 | 2000 | 700
1213 | Offshore hybrid Interconnector (DE-NL) | This project aims to investigate a hybrid interconnection between the two neighbouring countries Germany and The Netherlands in more detail to support the achievement of the ambitious offshore expansion targets of both countries. The Link is already mentioned in the Esbjerg expert paper. TenneT are currently investigating different option. Therefore the connection points are not fixed yet | TenneT TSO GmbH, TenneT TSO BV | DE ;NL | No | 2037 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False | [5 empty] | DE00-NL00 | 2000 | 2000
1214 | Hybrid Interconnector Denmark-Germany | This project describes the construction of a dual-purpose offshore hybrid HVDC interconnector between the Danish Energy Island (DEI) and Germany, which increases the transfer capacity between DK and DE with the purpose of integrating Danish offshore wind capacity to onshore markets. The project aims to integrate 2 GW of Danish offshore wind capacity to onshore markets. | Amprion, Energinet | DE ;DK |  | 2036 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | By increasing the transfer capacity between DK and DE, this project will help reduce price differences between the bidding zones DK1 and DE. This project facilitates cross-border flows by further increasing transfer capacity between DK and DE. The project aims to integrate 2 GW of additional Danish offshore wind capacity of the Danish Energy Island to onshore markets. ONDP identified up to 4 GW offshore corridor between German and Danish EEZ to integrate the offshore RES production. |  |  | DE00-DKW1
1215 | Xlinks Morocco - Germany | Xlinks Germany is a 2x 1.8 GW HVDC transmission system that will enable the delivery of up to 26 TWh per year of low-cost, firm, and reliable solar and wind power to over 7 million European consumers. The transmission project will connect solar and wind installations generating up to 15.2 GW of zero-carbon electricity supported by up to 8.6 TWh of battery storage in Morocco, where renewable resources are abundant, and the European grid through a connection point on TenneT’s German HV network. The HVDC transmission system is based on two bipolar 525 kV lines of 1.8 GW each. The HVDC converters are based on VSC technology, providing high reliability and efficiency of the transmission system. The project will allow for the integration of massive amounts of RES; enable significant reductions in carbon dioxide; improve security of supply; and support the European Green Deal. | Xlinks Ltd and Xlinks Germany GmbH | DE ;MA |  | 2032 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False | The relevant website url will be communicated once available. | Mitigate the risk of power failures Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | By providing renewable power uncorrelated with Northern-European wind and solar as well as 9.6 GWh of battery storage, the Xlinks project helps resolve the German/European “dunkelflaute” issue, thereby improving security of supply and reducing the risk of power failures. The Xlinks project will significantly contribute to system flexibility through direct access to battery storage capacity. Xlinks will also contribute to system stability by improving transient stability and helping to meet RoCoF system needs. Xlinks consists in infrastructure that will contribute to balancing flexibility by providing the European network with a new source of low-carbon dispatchable power. Additionally, the Xlinks project will deliver a 3600 MW power reserve through a new HVDC interconnection between Morocco and Germany. The Xlinks project will inject significant volumes of RES into the grid, which will make an important contribution to sustainability through a cost-efficient grid-connection. |  |  | DE00-MA00isolated | 3600 | 3600
1216 | High-Voltage Direct Current Interconnector Project Romania-Hungary | The High Voltage Direct Current interconnector (the Project) will connect the South-East region of Romania and the Black Sea offshore wind parks to Hungary. The project would also give continuity to the Green Energy Corridor between the European Union and Caspian Sea countries, establishing an energy corridor between Hungary, Romania, Georgia and Azerbaijan. In this context, the Project will enable and enhance massive import of green energy to the European Union. The Project consists of two interconnectors planned to be located along the corridor of the BRUA and the future Tuzla-Podișor gas pipelines. The preliminary design envisages multiterminal bipolar HVDC/VSC at 525kV voltage level and 2.5GW rated capacity each, with converter stations connected to 400kV substations of Constanta South, Arad and Albertirsa (in Hungary). One link will have additional converter station at Bucharest-South. The 400kV substation Constanta South will be connected in-out in planned 400kV double circuit OHL Constanta North-Medgidia South and is not included in this Project. | Transelectrica; MAVIR | HU ;RO |  | 2030 | 1 | True | False | New | False |  | The power from Black Sea coast and from Caspian countries will be evacuated to Arad and Hungary | TYNDP 2024 | False | False |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) Infrastructure to address system adequacy deficiencies Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | The project involves increasing capacity in Dobrogea, exporting energy to Hungary and beyond, and focusing on offshore wind and renewable energy sources in Dobrogea and Cernavoda. It will be phased to align with future TYNDP scenarios. The project offers reduced losses compared to AC alternatives and has the potential to export renewable energy to Central Europe, which faces constraints in renewable energy production. The project aims to mitigate future system failures, addressing recent near failures in the region, while resolving transmission constraints that currently prevent the full utilization of renewable energy sources in Dobrogea. Converters in Bucharest and Arad support the largest consumption nodes in Romania. As renewable energy sources (RES) increase, active system control is required to ensure stability and efficiency. |  |  | HU00-RO00 | 2500 | 2500
1217 | Further Development of Offshore Renewables (MOG 3) | Conceptual project with the goal of investigating the techno-economic feasibility and possibilities of developing 2GW of additional renewable energies in the Belgian part of the North sea, totaling the amount of renewables energies in the Belgian part of the North Sea to 8.000MW. This project may also become part of a hybrid project or an offshore grid. | Elia | BE |  | 2040 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False | https://www.elia.be/en/infrastructure-and-projects/investment-plan/federal-development-plan-2024-2034 | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The project aims at integrating a next wave of offshore renewables in the Belgian part of the North Sea. The project aims at integrating a next wave of offshore renewables in the Belgian part of the North Sea. |  |  | BE00Internal
1218 | Hybrid HVDC Interconnector BE-NL | Conceptual hybrid interconnector between Belgium and the Netherlands. The goal of this project is to create an HVDC link between a in the future radially connected offshore wind farm in the Netherlands and the Belgian onshore grid. Other topologies may also be possible. | Elia and TenneT-NL | BE ;NL | NDP, Belgium, 2024-2034, 67, p186 | 2040 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False | https://www.elia.be/en/infrastructure-and-projects/investment-plan/federal-development-plan-2024-2034 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | The project increases the crossborder capacity between Belgium and the Netherlands. The project increases the crossborder capacity between Belgium and the Netherlands. Due to its hybrid character, the project also integrates a significant amount of offshore renewables in an efficient way. Due to its hybrid character, the project also integrates a significant amount of offshore renewables in an efficient way. |  |  | BE00-NL60 | 2000 | 2000
1219 | Bofferdange- Bertrange | The project comprises an upgrade to 380 kV of the existing 220 kV OH-Line between substation Bofferdange to the existing 220 KV substation Bertrange and an upgrade of the 220 kV substation Bertrange to 380 kV to prepare for the expected rising electricity demand in the south and central part of Luxembourg. To supply the future 380kV station in Bertrange and to guarantee the security of supply, it is necessary to expand the 380kV grid connection ‘Aach – Bofferdange’ to Bertrange. The 380 KV OH-Line will replace an existing 220 kV OH-Line between Heisdorf and Bertrange built in the 1960's. | Creos Luxembourg | DE ;LU | NDP Luxembourg 2040 Version 2024, Projects L4602 + P4203 p.39-42 | 2035 | 2 | False | True | Upgrade | False |  | TR 328 - Aach-Bofferdange Project is part of the 380 kV upgrade of existing 220 kV grid infrastructure of Luxembourg to increase the interconnection capacity in the long term with neighboring countries. | TYNDP 2024 | False | False | [5 empty] | DE00-LUG1 BE00-LUG1 | 2400 300 | 2400 180
1220 | Offshore Wind Connection Viana do Castelo | Connection of 2 GW offshore Wind projects in the Viana Castelo region. Project under consideration. Commissioning date 2030-2040. CAPEX, OPEX and Type of element\technology to be confirmed.. | REN | PT |  | 2030-2040 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | Radial connection for Offshore Wind integration |  |  | PT00Internal | 2000 | 2000
1221 | Offshore Wind Connection Leixões | Connection of 1.5 GW offshore Wind projects in the Leixões region Project under consideration. Commissioning date 2030-2040. CAPEX, OPEX and Type of element\technology to be confirmed. | REN | PT |  | 2030-2040 | 1 | False | True | None | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | Radial connection for Offshore Wind integration |  |  | PT00Internal | 1500 | 1500
1222 | Offshore Wind Connection Figueira da Foz (North) | Connection of 2 GW offshore Wind projects in the Figueira da Foz region Project under consideration. Commissioning date 2030-2040. CAPEX, OPEX and Type of element\technology to be confirmed. | REN | PT |  | 2030-2040 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | Radial connection for Offshore Wind integration |  |  | PT00Internal | 2000 | 2000
1223 | Offshore Wind Connection Figueira da Foz (South) | Connection of 2 GW offshore Wind projects in the Figeuria da Foz region Project under consideration. Commissioning date 2030-2040. CAPEX, OPEX and Type of element\technology to be confirmed. | REN | PT |  | 2030-2040 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | Radial connection for Offshore Wind integration |  |  | PT00Internal | 2000 | 2000
1224 | Offshore Wind Connection Ericeira | Connection of 1 GW offshore Wind projects in the Ericeira region Project under consideration. Commissioning date 2030-2040. CAPEX, OPEX and Type of element\technology to be confirmed. | REN | PT |  | 2030-2040 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | Radial connection for Offshore Wind integration |  |  | PT00Internal | 1000 | 1000
1225 | Offshore Wind Connection Sines | Connection of 1.5 GW offshore Wind projects in Sines region Project under consideration. Commissioning date 2030-2040. CAPEX, OPEX and Type of element\technology to be confirmed. | REN | PT |  | 2030-2040 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to fulfil the optimal offshore corridors and integrate the offshore RES production (ONDP) | Radial connection for Offshore Wind integration |  |  | PT00Internal | 1500 | 1500
1226 | North-South Electricity Corridor in Eastern Europe | Throughout the synchronous areas of Europe, fast growth of RES with reduced participation of synchronous generators leads already today to challenging operational situations in terms of stability (angular stability). Operational measures can only remedy the situation and prevent large disturbances – for that, besides WAMS / EAS integration, a new family of „short-term stability ancillary services“ might be needed. Stronger and adequate infrastructure – new transmission lines across the continent and especially in the regions like SEE where weeker grid and interconnections have already been identified in analyses of system disturbances in the past – is not just a pre-requisite for RES integration by creation of “electrical energy corridors”, but for maintaining operational security and system stability. To accelerate renewables not only large scale of RES generation has to be put in place on time but also necessary infrastructure and flexibility resources to integrate this additional electricity into the European energy system. | ESO, IPTO, MEPSO, TEL, PSA, MAVIR, SEPS, CEPS | BG ;CZ ;GR ;HU ;MK ;PL ;RO ;SK |  | 2036 | 1 | True | False | New | False |  | Stronger and adequate infrastructure – new transmission lines across the continent and especially in the regions like SEE where weaker grid and interconnections have already been identified in analyses of system disturbances in the past – is not just a pre-requisite for RES integration by creation of “electrical energy corridors”, but for maintaining operational security and system stability. | TYNDP 2024 | False | False | [5 empty] | BG00-GR00 BG00-RO00 HU00-RO00 HU00-SK00 CZ00-PL00 | 2000 2000 2000 2000 2000 | 2000 2000 2000 2000 2000
1229 | Rhine-Main-Link | This project consists of two new HVDC cable from Ovelgönne/Rastede/Wiefelstede/Westerstede to Bürstadt and to Marxheim (Taunus). The HVDC have a transfer capacity of 2 GW each. In Ovelgönne/Rastede/Wiefelstede/Westerstede, a DC multiterminal converter station is to be built together with offshore projects. This project is a grid expansion project for low-loss transmission of high power over long distances from Northern Germany to the Rhine-Main-Area. Northern Germany is characterized by a large number of regenerative onshore and offshore energy sources which exceed the demand of Northern German loads. The Rhine-Main-Area, however, is characterised by a high load due to the local industry and the high population density. This will increase significantly in the next years due to the establishment and expansion of data centres and the decarbonisation efforts of industry. | Amprion | DE | NDP, Germany, Netzentwicklungsplan 2037 Version 2023, Project DC34/DC35, p. 468 | 2033 and 2035 | 3 | False | True | New | False |  | implementation as an energy corridor | TYNDP 2024 | False | False | Further information of the project, its investments and their necessity particularly for the German Energiewende can be found in the German grid development plan (mostly in German): http://www.netzentwicklungsplan.de/en/front Bundesbedarfsplan 2022 (BBPIG): https://www.netzausbau.de/Vorhaben/ansicht/de.html?cms_gruppe=bbplg&cms_nummer=82 More detailed information can be found on the project website (in German): https://www.amprion.net/Netzausbau/Aktuelle-Projekte/Rhein-Main-Link/ Link to the website of the project: https://rhein-main-link.amprion.net/ Link to second corridor: https://www.netzausbau.de/Vorhaben/ansicht/de.html?cms_nummer=82a&cms_gruppe=bbplg Link tot he current NDP: https://www.netzentwicklungsplan.de/sites/default/files/2024-04/NEP_2037_2045_V2023_Anhang_2E_Aktualisierung_April_2024.pdf |  |  |  |  | DE00-NL00 DE00-FR00 internalDE00 | 1030 0 1030 | 220 700 220
1230 | TuNur Malta | TuNur Malta is an integrated cross-border renewable energy and transmission project. It consists of a hybrid renewable energy facility coupled with storage located on a 4,000hc site in Southern Tunisia; and a dedicated 500MW HVDC line from the power plant to Malta. The project will deliver 3.5TWh/yr of dispatchable, competitively priced, carbon-free power to Europe, supporting the energy transition, REPowerEU and EU Green Deal. The transmission system consists of a 320kV HVDC system with an overhead line from the power plant to the eastern coast of Tunisia, and a 460km submarine line to the Maltese network where multiple connection points are under evaluation. The system will include one VSC HVDC converter station in Tunisia and one in Malta. The project provides a robust connection in the central Mediterranean corridor in line with the initiative for developing the region into a Green Energy Hub. This new energy highway reinforcement will enable significant investment, economic development, and technology transfer in Tunisia. The delivery of high quantities of low-cost dispatchable power to Europe will support Malta and Europe’s energy and climate policy objectives, specifically the demand for low carbon power and diversification of supply | TuNur Ltd | MT ;TN |  | 2032 | 1 | True | False | New | False |  | To connect to the Maltese grid, the main investment (DC cable) requires a short AC cable. The AC cable has no standalone purpose without the main investment. | TYNDP 2024 | False | False | The website is pending and will be shared with ENTSO-E once available. | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to offer more supply options to isolated areas Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | The TuNur Malta project will contribute to improving market integration and reducing price differentials between EU and non-EU countries by providing an additional 500 MW of low cost and low carbon available capacity, through a new connection between a non-EU (Tunisia) and EU (Malta) country. The TuNur Malta project will bring high volumes of RES load at competitive prices to the Maltese market, thereby increasing the supply options of Malta. The TuNur Malta project will provide dispatchable low-carbon power and will contribute to system adequacy deficiencies by increasing transmission capacity. This power source will improve security of supply by reducing Loss of Load durations across EU networks, making a significant contribution to system stability. The TuNur Malta project will significantly contribute to system flexibility through direct access to a new source of renewable energy. TuNur will also contribute to system stability by improving transient stability and helping to meet RoCoF system needs. TuNur will provide flexible power with black-start capacity. |  |  | TN00Isolated-MT00 | 500 | 500
1231 | Green Aegean Interconnector | The project concerns a new interconnection between Greece and Germany, by the development of a new HVDC link. It consists of a new HVDC link of 3000 MW, via submarine and land HVDC cables, between the Greek and German transmission systems. The transmission link will start in a substation in northern Greece and connects to Germany going through the Adriatic Sea, landing in Slovenia and through Austria to southern Germany. The new interconnection aims to enhance the energy infrastructure and decarbonization in Europe by interconnecting Greece with Germany and allowing the full exploitation of the seasonal complementarity between solar and wind output by connecting the windy north with the sunny south, thus allocating cost-optimal renewable energy and ensuring the security of supply throughout the continent. | IPTO | DE ;GR |  | 2036 | 1 | True | False | New | False |  |  | TYNDP 2024 | False | False |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project aims to enhance the energy infrastructure and decarbonization in Europe, thus help in achieving the Green Deal objective of climate neutrality by 2050. The project, as a new interconnector between Greece and Germany, will provide balancing flexibility to the Greek and German power systems. The project will allow the further exploitation of RES potential and reduce future RES curtailments in both Greece and Germany. |  |  | DE00-GR00 | 3000 | 3000
1233 | Laufenburg - Beznau - Breite | This project * increases the capacity between Switzerland and its northern neighbours. This enables to connect large renewable generation in Northern Europe to pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. * comprises the optimization of the existing route by voltage conversion to 380 kV and a partial reinforcement. | Swissgrid | CH |  | 2035 | 1 | False | True | New | False |  | timely and electrical vicinity | TYNDP 2024 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to address system adequacy deficiencies | This project contributes to lowering the price differentials between Switzerland, Germany and Austria. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. |  |  | CH00-DE00 | 0 | 1500
1234 | 220-kV Reitdorf (AT) - Weißenbach (AT) | Increase of Renewables is political and societal goal. This project is needed to connect wind and PV generation in the relevant areas to the transmission system and brings also an increase of the security of supply as the capacities increase. | Austrian Power Grid | AT | APG Network Development Plan 2023, AT, 2023, 19-2, 73-74, https://www.apg.at/en/power-grid/grid-expansion/ | 12-2028 | 3 | False | True | Upgrade | False |  |  | TYNDP 2024 | False | False | Project Hompepage: https://www.apg.at/en/projects/enns-valley-line/ APG NDP: https://www.apg.at/en/power-grid/grid-expansion/ | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | The project improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. The project allows additional RES integration, which will also decarbonize the hydrogen sector with increased usage of electrolysers. |  |  | ATInternal | 0 | 0
1235 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | The project involves the installation of the second circuit on existing 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK), which was commissioned in 2020, and built with double circuit towers. | MAVIR, SEPS | HU ;SK |  | 2027 | 1 | True | False | Upgrade | False |  |  | TYNDP 2024 | False | False | [5 empty] | HU00-SK00 | 100 | 760
1236 | Power-to-Gas for Austria (P2G4A) | Power-to-Gas-for-Austria (P2G4A) features a 50 MW electrolyser and related infrastructure near an APG substation. This initiative strives to support the transition to renewable energy by offering grid stability, enabling seasonal energy storage, and reducing gas imports. While owned by TSOs, the project fosters technology development while ensuring non-discriminatory access for all market players. Importantly, energy ownership remains with market participants, not network operators. | Austrian Power Grid | AT | https://www.bmk.gv.at/themen/energie/energieversorgung/netzinfrastrukturplan.html | 12-2029 | 1 | False | True | New | False |  |  | TYNDP 2024 | False | False | ENTSO-G TYNDP 2022 Annex A: https://www.entsog.eu/sites/default/files/2023-09/ENTSOG_TYNDP_2022_Annex_A_Project_Details_230411.xlsx https://www.bmk.gv.at/themen/energie/energieversorgung/netzinfrastrukturplan.html | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | The project provides the opportunity to integrate additional electrolysers in the region, which are essential for decarbonization in future scenarios. The project provides the opportunity to integrate additional electrolysers in the region. |  |  | AT00
1239 | Interconnection Ukraine-Slovak Republic | The Slovak transmission system is interconnected with Ukraine transmission system by a single 400 kV overhead line from subst. Veľké Kapušany (SK) to subst. Mukacheve (UA), which SEPS envisages to operate until 2030 without significant investment interventions. It is very loaded cross-border line whose importance is multiplied in case of maintenance/fault conditions on one of the existing interconnections between Slovakia and Hungary. The project of the reconstruction of this 400 kV cross-border interconnection between Mukacheve (UA) - Veľké Kapušany (SK) is included in the European list of Projects of Mutual Interest. | NPC Ukrenergo, SEPS | SK ;UA | “Ten-year network development plan for the years 2024 - 2033” (https://www.sepsas.sk/engine/wp-content/uploads/2024/03/DPRPS_2024-2033.pdf) has been prepared in April 2023, published after NRA’s consultation in March 2024. It is necessary to take information in it with having this time stamp in mind. In connection with the imposition of martial law on the territory of Ukraine, the Ministry of Energy of Ukraine and the national regulator have issued a series of orders and directives in the energy sector regarding the closure of public access to information. The development plan for Ukraine’s transmission system for 2024-2033 has been approved by the regulator’s resolution No. 2634 of December 29, 2023. This development plan contains information that public access to it could harm the identification and perception of the potential of the transmission system object. In the development plan for Ukraine’s transmission system for 2024-2033, the project ‘Reconstruction of the 400 kV OHL Mukacheve - Kapushany section from the 400 kV SS Mukacheve to the state border in Zakarpattia region’ is reflected in section 2.3 of subsection 2, chapter 5.3, on pages 117-118. This information is provided separately in Appendix No. 1 | 2032 | 2 | True | False | Upgrade | False |  | The implementation of the project will allow replacing outdated equipment from 1962 with new equipment while simultaneously doubling the capacity of this interconnector through the construction of a second circuit. | TYNDP 2024 | False | False | TYNDP 2020-2029, 2021-2030, 2022-2031, 2023-2032 and 2024-2033 years | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | Ukrainian and European energy companies will increase cross-border trade and will be able to optimize the operation of their generating assets. Optimized asset performance, combined with increased competition and higher market liquidity, will reduce prices for consumers in both countries, as well as strengthen the energy security of both countries. Currently, the energy system of Ukraine is inadequate in terms of covering the load with its own generating capacities, which were destroyed as a result of the military aggression of the Russian Federation. The implementation of the project will cover peak electricity consumption in the context of daily and seasonal fluctuations in the medium and long term. The implementation of the project to expand cross-border network capacity will enhance the reliability of electricity supply to the western regions of Ukraine and Slovakia. Given the limited flexibility of Ukraine's energy system, partly due to the destruction of balancing capacities caused by military aggression from the Russian Federation, the project will enable increased system flexibility by utilizing regulatory capacities from outside Ukraine. With the expansion of cross-border trade, Ukrainian TSO NPC Ukrenergo and Slovakia's TSO SEPS will receive additional revenues from cross-border capacity allocation auctions, increase grid utilization, gain access to additional flexibility and balancing options, as well as frequency regulation, while renewable energy producers will face fewer constraints.
1240 | Interconnection Ukraine-Romania | The implementation of this project will allow to restore the Ukraine-Romania interconnector of the 750 kV voltage class, which was destroyed in 1998, to the lower voltage class of 400 kV. | Transelectica and NPC Ukrenergo | RO ;UA |  | 2028 | 2 | True | False | New | False |  |  | TYNDP 2024 | False | False | TYNDP 2020-2029, 2021-2030, 2022-2031, 2023-2032 and 2024-2033 years | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to address system adequacy deficiencies | Ukrainian and European energy companies will increase cross-border trade and will be able to optimize the operation of their generating assets. Optimized asset performance, combined with increased competition and higher market liquidity, will reduce prices for consumers in both countries, as well as strengthen the energy security of both countries. With the expansion of cross-border trade, Ukrainian TSO NPC Ukrenergo and Romania's TSO Transelectrica will receive additional revenues from cross-border capacity allocation auctions, increase grid utilization, gain access to additional flexibility and balancing options, as well as frequency regulation, while renewable energy producers will face fewer constraints. The implementation of the project will remove restrictions on the output of RES generation capacity in the south of Ukraine and eastern Romania and will provide an opportunity for additional development of RES in these regions. Currently, the energy system of Ukraine is inadequate in terms of covering the load with its own generating capacities, which were destroyed as a result of the military aggression of the Russian Federation. The implementation of the project will cover peak electricity consumption in the context of daily and seasonal fluctuations in the medium and long term.

## Trans.Investments
TYNDP 2024 Transmission projects - General information on transmission investments | [8 empty] | Technical characteristics of the investment | [10 empty] | Costs of the investment |  |  |  | CBA indicators at investment level – B8.0 Stability (Transient, voltage and frequency stability) |  |  | Residual environmental impact |  |  | Residual social impact |  |  | Other residual impact
Investment number | Investment Name | This investment belongs to project number… | Description of the investment | Commissioning Year | Status ID 1 : Under Consideration, 2 : In Planning but not permitting, 3 : In permitting, 4 : Under Construction | Is Main Investment(s) | Progress of the investment since TYNDP2022 | Explanation in case of delay or reclustering | Type of Element | Substation From | Substation To | Technology | Type of HVDC | Total route length (km) | Nominal voltage (kV) | Capacity of the investment (MW) | MVA | Type of converter | Mvar | Estimated CAPEX (MEUR) | Sustaining CAPEX (Meuro) | Estimated OPEX (MEUR) | Cost Uncertainty Range | Transient stability | Voltage stability | Frequency stability | Distance (km) | Type of sensitivity | Additional information | Distance (km) | Type of sensitivity | Additional information | Other residual impact
4 | V.Minho -R.Pena-Feira | 1 | New double-circuit 400kV OHL Vieira do Minho (PT) - Ribeira de Pena (PT) - Feira (PT). | 06-2024 | 4 | TRUE | Delayed | Although the construction started on the section Feira-Ribeira de Pena, there is a public opposition to the project that is delaying the construction. Section V.Minho-Ribeira de Pena was comissioned in 2021. | ACTransmissionLine | V.Minho (by Ribeira de Pena) | Feira (by Ribeira de Pena) | AC | None | 138.58 | 400 | 0 | 2083 |  |  | 56.6 | 0 | 0.153 | ±10%% | ++ | ++ | 0 | 13 7 | Other Other | Habitats Directive Birds Directive Habitats Directive IUCN key biodiversity áreas | 10 | Other | Globally Important Agricultural Heritage Systems (GIAHS)
474 | Substation Ribeira de Pena | 1 | New 400/60kV substation in Ribeira de Pena. | 12-2021 | 5 | TRUE | Investment on time |  | OnshoreSubstation | Ribeira de Pena (PT) | - | AC | None | 0 | 400 | 0 |  |  |  | 10.867 | 0 | 0.054 | ±10%%
18 | Beariz (ES) - Fontefria (ES) | 4 | New double circuit 400kV OHL between Beariz (ES) - Fontefria (ES). | 06-2024 | 3 | TRUE | Delayed | Delays in the Environmental Impact Assessment process | ACTransmissionLine | Beariz (ES) | Fontefria (ES) | AC | None | 30 | 400 | 0 |  |  |  | 26.53 | 0 | 0.45 | 10%% | ++ | ++ | 0
496 | Fontefria (ES) - Vila Nova de Famalicão (PT) | 4 | New 400kV OHL Fontefria (ES) - Ponte de Lima (PT) - Vila Nova de Famalicão (PT). | 12-2024 | 3 | TRUE | Delayed | Delays in the Environmental Impact Assessment process. Section Vila Nova de Famalicão-Ponte de Lima was comissioned in 2021. | ACTransmissionLine | Fontefria (ES) | Vila Nova de Famalicão (PT) (By Ponte de Lima) | AC | None | 94.71 | 400 | 0 | 1499 |  |  | 50.6 | 0 | 0.161 | 10%% | ++ | ++ | 0 | 0.5 29 3 | HabitatsDirective None HabitatsDirective |  | 1 | HabitatsDirective
498 | SE Fontefria 400/220kV | 4 | New 400kV substation Fontefria (ES), previously O Covelo. | 06-2024 | 3 | TRUE | Delayed | Delays in the Environmental Impact Assessment process | Transformer | Fontefria (ES) | REE | AC | None | 0 | 400 | 0 |  |  |  | 9.04 | 0 | 0.22 | 10%%
499 | Beariz 400kV (ES) | 4 | New 400kV substation Beariz (ES), previously Boboras | 06-2024 | 3 | TRUE | Delayed | Delays in the Environmental Impact Assessment process | OnshoreSubstation | Beariz (ES) | Beariz (ES) | AC | None | 0 | 400 | 0 |  |  |  | 5.01 | 0 | 0.16 | 10%%
500 | Substation Ponte de Lima (PT) | 4 | New 400/150kV substation Ponte de Lima (PT), previously V. Castelo. | 12-2024 | 3 | TRUE | Delayed | Delays due to correlation with other delayed infrastructure investments. | OnshoreSubstation | Ponte de Lima (PT) | Ponte de Lima (PT) | AC | None | 0 | 400 | 0 |  |  |  | 20 | 0 | 0.054 | 10%%
38 | HVDC Gatica-Cubnezais | 16 | New HVDC interconnection in the western part of the border via DC subsea cable in the Biscay Gulf (cable and converters at the end). | 12-2028 | 4 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Gatica (ES) | Cubnezais (FR) | DC | None | 394 | 400 | 2000 |  | VCS |  | 3100 | 0 | 10.5 | 0% | ++ | ++ | + (between sync areas) | 11 | Other |  | 0.269 | HabitatsDirective
1503 | Second HVDC pole of the IT-ME interconnection (600 MW) | 28 | Second HVDC pole of the interconnection between Italy and Montenegro (600 MW) via 445 km 500kV DC subsea cable | 12-2027 | 4 | TRUE | Investment on time | - | OffshoreDCTransmissionCable | Villanova (IT) | Lastva (ME) | DC | Bipolar | 445 | 500 | 600 |  | LCC |  | 424 | 0 | 0.8 | 10% | ++ | ++ | + (between sync areas) | 0 | None |  | 2 | Other | -
635 | Elmed Project | 29 | New interconnection between Italy and Tunisia - New HVDC submarine cable and conventer stations at both ending points | 01-2028 | 3 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Partanna (IT) | Mlaabi (TN) | DC | Monopolar | 220 | 500 | 600 |  | VCS |  | 850 | 0 | 2.97 | 10% | ++ | ++ | + (between sync areas) | 13 | Other | - | 0 | None
90 | Voltage upgrade of the existing 80km Calenzano-Colunga 220kV OHL to 400kV | 33 | Voltage upgrade of the existing 80km Calenzano-Colunga 220kV OHL to 400kV, providing in and out connection to the existing 220/150kV substation of S. Benedetto del Querceto (which already complies with 400kV standards). | 12-2025 | 4 | TRUE | Investment on time |  | ACTransmissionLine | Calenzano (IT) | Colunga (IT) | AC | None | 80 | 400 | 0 | 1850 |  |  | 277 | 0 | 0.3 | 10% | ++ | ++ | 0 | 27 | Other | - | 3 | Other
1041 | Removing limitations in Central Italy | 33 | Removing limitations on existing 220 kV grid between Villanova e S.Barbara | 12-2023 | 4 | FALSE | Investment on time |  | ACTransmissionLine | Villanova (IT) | S. Barbara (IT) | AC | None | 350 | 220 | 0 | 495 |  |  | 74 | 0 | 0.5 | 10% | ++ | ++ | 0 | 34 | Other | - | 6 | Other | -
313 | Kocin-Mirovka | 35 | Connection of 2 existing 400 kV substations with new double circuit OHL having 120.5 km length and a transmission capacity of 2 x 2445 A. | 10-2029 | 3 | TRUE | Delayed | Delays due to other permit granting reasons | ACTransmissionLine | Kocin (CZ) | Mirovka (CZ) | AC | None | 120.5 | 400 | 0 | 1694 |  |  | 263.943 | 0 | 0.01 | -10%, +15%% |  |  |  | 0.5 | HabitatsDirective None |  | 0.5 | IUCNKeyBiodiversityAreas None |  | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 313 and 315) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environmental impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval opinion.
315 | Kocin-Prestice | 35 | Adding second circuit to the existing single circuit OHL with a total transmission capacity of 2 x 2445 A and 117 km length | 12-2028 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Kocin (CZ) | Prestice (CZ) | AC | None | 117 | 400 | 0 | 1694 |  |  | 201.086 | 0 | 0.01 | -10%, +15%% |  |  |  |  | None |  |  |  |  | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 313 and 315) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environmental impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval opinion.
650 | BE-LUX-DE Long-Term perspective | 40 | The technical solution is subject to further studies | 12-2040 | 1 | TRUE | Rescheduled |  | OnshoreACTransmissionCable | Aubange (TBC) | LUX-DE (TBC) | AC | None | 16 | 0 | 0 | 500 |  |  | 210 | 0 | 1.26 | 25%% | ++ | ++ | 0
689 | 689: Vöhringen (DE) - Westtirol (AT) | 47 | Upgrade of an existing over head line to 380 kV, extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. Transmission route Vöhringen (DE) -Westtirol (AT). This project will increase the current power exchange capacity between the DE, AT. | 12-2030 | 2 | TRUE | Delayed | Scope of the project changed due to technical reasons. | ACTransmissionLine | Vöhringen (DE) | Westtirol (AT) | AC | None | 157 | 380 | 0 | 1677 |  |  | 10.3 | 0 | 0.08 | 10%% | - | - | 0 |  | None
462 | 462 | 81 | A new 138 km single circuit 400 kV 1500 MVA OHL from Turleenan 400/275 kV in Northern Ireland to Woodland 400/220 kV in Ireland. This is a new interconnector project between Ireland and Northern Ireland. | 11-2025 | 3 | TRUE | Delayed | Investment delayed due to judicial reviews of planning consent in IE and delayed approval of planning consent in NI. | ACTransmissionLine | Woodland (IE) | Turleenan (NI) | AC | None | 138 | 400 | 0 |  |  |  | 363 | 0 | 0.95 | 20% | ++ | ++ | 0 |  | None |  |  | None
779 | F.Alentejo-Panóias-Ourique-Tavira | 85 | New double-circuit 400+150 kV OHL F. Alentejo-Panóias-Ourique-Tavira. The realization of this connection can take advantage of some already existing 150kV single lines, which can be reconstructed as double circuit line 400+150kV. | 12-2024 | 4 | TRUE | Delayed | Delays in permitting and construction | ACTransmissionLine | F. Alentejo (by Panóias\Ourique) | Tavira (by Panóias\Ourique) | AC | None | 126.441 | 400 | 0 | 1546 |  |  | 94.2 | 0 | 0.089 | ±10%% |  |  |  | 11 | RAMSARSite
1670 | Alqueva-Divor | 85 | New 75 km double-circuit (only one circuit installed initially) 400 kV OHL Alqueva-Divor . | 03-2025 | 3 | FALSE | Delayed | Delays in permitting | ACTransmissionLine | Alqueva | Divor | AC | None | 75 | 400 | 0 | 1546 |  |  | 27.7 | 0 | 0.066 | ±10%%
1965 | Substation Panóias | 85 | New 400/150 kV Substation | 03-2025 | 4 | TRUE | New Investment |  | OnshoreSubstation | Panóias | - | AC | None | 0 | 400 | 0 |  |  |  | 12.7 | 0 | 0.026 | 10%
1493 | PST Vierraden | 94 | Installation of new PSTs in Vierraden | 11-2025 | 4 | TRUE | Delayed | Due to a court case, an enforceable building permission for the Uckermark-line was delayed. As the court case was settled in July 2022 the upgrade of the Uckermark-line is proceeding. | PhaseShiftingTransformer | Vierraden | Vierraden | AC | None | 0 | 400 | 0 |  |  |  | 110.8 | 0 | 2 | 10%
810 | France Ireland Interconnector | 107 | A new HVDC subsea connection between Ireland and France | 03-2027 | 4 | TRUE | Rescheduled | delay due to COVID crisis and to time required for the contractualisation of the 2 main EPC contracts | OffshoreDCTransmissionCable | Knockraha (IE) | La Martyre (FR) | DC | Monopolar | 575 | 320 | 700 |  | VCS |  | 1623 | 0 | 6.5 | +/- 0%% | ++ | ++ | + (between sync areas) | 33.277 | Other | offshore and onshore sensitivity | 10.072 | Other | offshore and onshore sensitivity
396 | 3rd AC Finland-Sweden north | 111 | Third AC 400 kV overhead line interconnector between Finland north and Sweden SE1. | 12-2025 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Viitajärvi (Finland) | Messaure (Sweden, bidding area SE1) | AC | None | 226 | 400 | 0 | 2200 |  |  | 204 | 0 | 0.15 | +-10%% | ++ | ++ | 0 | 90 5.5 | HabitatsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 10 | MarinStrategyFrameworkDirective
1710 | Viitajärvi-Pyhänselkä | 111 | The investment is a 400 kV overhead line in North Finland. It is part of the 3rd AC cross border project between Finland and Sweden and will enable its full capacity to be utilized. The project will also allow integration of new RES generation at Bothnian bay. | 12-2024 | 3 | FALSE | Investment on time |  | ACTransmissionLine | Viitajärvi | Pyhänselkä | AC | None | 153 | 400 | 0 | 2200 |  |  | 66 | 0 | 0.15 | +-10%% | ++ | ++ | 0
1625 | AC-part of Princess Elisabeth Island | 120 | Construction of an artificial island including AC & DC assets to connect +-3,5GW of offshore wind and connect it to the onshore grid | 02-2029 | 3 | TRUE | Rescheduled | Reevaluation of the project's schedule | OffshoreSubstation | Princess Elisabeth Island | Onshore (TBD) | AC | None | 360 | 220 | 0 | 2100 |  |  | 950 | 0 | 20 | 35%% | ++ | ++ | 0 | 20 2 | HabitatsDirective BirdsDirective
1791 | DC-part of Princess Elisabeth Island | 120 | Construction of an artificial island including AC & DC assets to connect +-3,5GW of offshore wind and connect it to the onshore grid | 12-2030 | 3 | FALSE | Rescheduled | Reevaluation of the project's schedule | OffshoreSubstation | Princess Elisabeth Island | Onshore (TBD) | DC | Bipolar | 60 | 1050 | 1400 |  | VCS |  | 750 | 0 | 15 | 35% |  |  |  | 20 2 | HabitatsDirective BirdsDirective
934 | Nautilus multi purpose interconnection UK - BE | 121 | This investment item envisions the possibility of a second HVDC connection between UK and Belgian offshore substation (project 120) near the coast. | 12-2030 | 2 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Leiston (UK) | Princess Elisabeth Island | DC | Bipolar | 140 | 1050 | 1400 |  | VCS |  | 1000 | 0 | 25 | 25%% | ++ | ++ | + (between sync areas) |  | None
1783 | Nybro-Hemsjo | 124 | Second phase includes the internal network reinforcements in Sweden to be able to fully utilize the interconnector between Lithuania and Sweden. | 12-2026 | 4 | TRUE | Delayed | Permit recieved. | ACTransmissionLine | Nybro (SE) | Hemsjo (SE) | AC | None | 90 | 400 | 0 |  |  |  | 149 | 0 | 0.1 | +-10%% |  |  |  | 100 100 | BirdsDirective HabitatsDirective
1784 | Ekhyddan-Nybro | 124 | Second phase includes the internal network reinforcements in Sweden to be able to fully utilize the interconnector between Lithuania and Sweden. | 12-2027 | 3 | FALSE | Delayed | Permit denied. Appeal process ongoing | ACTransmissionLine | Ekhyddan (SE) | Nybro (SE) | AC | None | 98 | 400 | 0 |  |  |  | 135 | 0 | 0.1 | +-10%% |  |  |  | 100 100 | HabitatsDirective BirdsDirective
403 | Reinforcements SE2-SE3 in Sweden | 126 | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. The need for capacity is driven by RES integration in northern Sweden and nuclear decommission in southern Sweden. | 01-2035 | 2 | TRUE | Investment on time |  | ReactiveCompensationDevice | Ramsele (SE2) | Hamra (SE3) | AC | None | 1200 | 400 | 0 |  |  |  | 2800 | 0 | 28 | +-10%% | ++ | ++ | 0
86 | New 66km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations | 127 | New 66km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations | 12-2028 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Foggia (IT) | Villanova (IT) | AC | None | 178 | 400 | 0 | 2078 |  |  | 520 | 0 | 0.35 | 10% | ++ | ++ | 0 | 8 | Other | - | 0 | None
665 | Wolmirstedt-Isar | 130 | New DC-line to integrate new wind generation from control area 50Hertz especially Mecklenburg-Vorpommern, Brandenburg and Sachsen-Anhalt towards Central/south Europe for consumption and storage. | 12-2027 | 3 | TRUE | Investment on time |  | DCTransmissionLine | Wolmirstedt (DE) | Isar (DE) | DC | Bipolar | 539 | 525 | 2000 |  | VCS |  | 5250 | 0 | 42 | +-20%% | ++ | ++ | + (between sync areas) | 78 | OtherNatureProtectionAreasUnderNationalLaw |  | 45 | OtherNatureProtectionAreasUnderNationalLaw
661 | HVDC Line A-North | 132 | New HVDC line from Emden to Osterath to integrate new wind generation especially from North Sea towards Central Germany for consumption. | 12-2027 | 3 | TRUE | Investment on time |  | DCTransmissionLine | Emden East (DE) | Osterath (DE) | DC | Bipolar | 300 | 400 | 2400 |  | VCS |  | 3128 | 0 | 25 | 10%% |  |  |  | 3.5 16.1 11.0 3.9 2.6 | HabitatsDirective BirdsDirective RAMSARSite IUCNKeyBiodiversityAreas OtherNatureProtectionAreasUnderNationalLaw |  | 28.6 8 | HabitatsDirective MarinStrategyFrameworkDirective
273 | 400kV OHL Cernavoda-Stalpu | 138 | Reinforcement of the cross-section between the Western coast of the Black Sea (Eastern Romania) and the rest of the system. A new 400 kV AC OHL double circuit of 159 km shall be built between the 400 kV substation Cernavoda and the existing 220/110 kV Stalpu substation, which shall be replaced with a 400/110 kV substation (onshore). One of the two circuits shall be connected in-out to the 400 kV substation Gura Ialomitei, situated in the vicinity of the new line. | 12-2022 | 5 | FALSE | Investment on time |  | ACTransmissionLine | Cernavoda (RO) | Stalpu (RO) | AC | None | 159 | 400 | 0 | 1741 |  |  | 77.56 | 1.24 | 0.42 | -5%, +5%% | ++ | ++ | 0 | 1 | HabitatsDirective |  | 0 | None
275 | 400 kV OHL Smardan-Gutinas | 138 | Reinforcement of the cross-section between the Western coast of the Black Sea (Dobrogea area) and the rest of the system. New 400kV double circuit OHL (one circuit wired) between existing substations. Line length 140km. | 12-2024 | 4 | TRUE | Investment on time |  | ACTransmissionLine | Smardan (RO) | Gutinas (RO) | AC | None | 140 | 400 | 0 | 1741 |  |  | 50.1 | 0.84 | 0.25 | -5%, +5%% | ++ | ++ | 0 | 3 | HabitatsDirective |  | 0 | None
715 | 220kV Stalpu substation upgrade to 400 kV | 138 | The 220/110 kV substation Stalpu is upgraded to 400/110kV (1x250MVA). | 12-2026 | 4 | FALSE | Delayed | The contractor responsible for the construction has gone into insolvency | OnshoreSubstation | Stalpu (RO) | Stalpu (RO) | AC | None | 0 | 400 | 0 | 250 |  |  | 14.95 | 0 | 0.15 | -5%, +5%% |  |  |  | 0 | None |  | 0 | None
800 | 400 kV OHL Varna-Burgas | 138 | New 86 km single circuit 400kV OHL in parallel to the existing one. | 08-2021 | 5 | FALSE | Investment on time |  | ACTransmissionLine | Varna(BG) | Burgas(BG) | AC | None | 86 | 400 | 0 |  |  |  | 63 | 0 | 0.8 | +10%, -10%% | ++ | ++ | 0 | 7 | HabitatsDirective
238 | New_400 kV OHL RO-RS | 144 | New 131 km double circuit 400kV OHL between Romania and Serbia (63 km on Romanian (thermal limit 2513 A) side and 68 km on Serbian (thermal limit 1920 A) side). | 12-2025 | 4 | TRUE | Delayed | Due to some delays related to investments 701 and 269 the line is not operated | ACTransmissionLine | Resita (RO) | Pancevo (RS) | AC | None | 131 | 400 | 0 | 1741 |  |  | 47 | 1.02 | 0.23 | -5%, +5%% | ++ | ++ | 0 | 1 | HabitatsDirective |  | 0 | None
269 | 400 kV OHL Portile de Fier-Resita | 144 | New 116 km 400kV OHL single circuit between existing substation 400 kV Portile de Fier and new 400 kV substation Resita. | 12-2024 | 4 | FALSE | Investment on time |  | ACTransmissionLine | Portile de Fier (RO) | Resita (RO) | AC | None | 116 | 400 | 0 | 1741 |  |  | 30.08 | 0.7 | 0.15 | -5%, +5%% | ++ | ++ | 0 | 30 | HabitatsDirective |  | 0 | None
270 | Upgrade of the existing 220kV double circuit OHL Resita -Timisoara - Sacalaz to 400kV | 144 | Upgrade of an existing 220 kV AC double circuit line (OHL) between Resita - Timisoara (RO) to 400 kV double circuit line Resita-Timisoara/Sacalaz of which: 74 km from Resita to Timisoara and 92 km from Resita to Sacalaz , both overhead lines will be built on common towers up to Icloda on 58 km. | 12-2029 | 3 | FALSE | Rescheduled |  | ACTransmissionLine | Resita (RO) | Timisoara-Sacalaz (RO) | AC | None | 166 | 400 | 0 | 1741 |  |  | 59.96 | 0.75 | 0.36 | -5%, +5%% | ++ | ++ | 0 | 17.5 | HabitatsDirective |  | 0 | None
701 | 400 kV Substation Resita | 144 | New 400 kV substation Resita (T400/220 kV 400 MVA + T 400/110 kV 250 MVA), as development of the existing 220/110 kV substation. | 12-2025 | 4 | FALSE | Investment on time |  | OnshoreSubstation | Resita (RO) | Resita (RO) | AC | None | 0 | 0 | 0 | 0 |  |  | 30.38 | 0 | 0.3 | -5%, +5%% |  |  |  | 0 | None |  | 0 | None
705 | 400 kV Substation Timisoara | 144 | Completion of 220 kV substation Timisoara and partially replacement with 400 kV substation (2x250 MVA 400/110 kV) | 12-2028 | 4 | FALSE | Delayed | The execution contract is terminated | OnshoreSubstation | Timisoara (RO) | Timisoara (RO) | AC | None | 0 | 0 | 0 | 0 |  |  | 44.05 | 0 | 0.44 | -5%, +5%% |  |  |  | 0 | None |  | 0 | None
1827 | Upgrade of the existing 220kV double circuit OHL Arad -Timisoara - Sacalaz to 400kV | 144 | Upgrade of the existing 220 kV AC double circuit line (OHL) Arad-Timisoara/Sacalaz to 400 kV on 67 km of which: 14 km of line will be build single circuit between Sacalaz-C.Aradului-""connection point"", 11 km single circuit from Timisoara to ""connection point"" and the rest 42 km of the line will be double circuit from ""connection point"" to Arad. The investment contains the extension of substation 400kV Arad. | 12-2029 | 3 | FALSE | Rescheduled |  | ACTransmissionLine | Arad (RO) | Timisoara-Sacalaz(RO) | AC | None | 109 | 400 | 0 | 1741 |  |  | 37.73 | 0.48 | 0.25 | -5%,+5%% |  |  |  | 17 | HabitatsDirective
616 | Salgareda - Divaca | 150 | New HVDC link between Salgareda (IT) and Divaca (SI) including reinforcements of the existing grid | 12-2042 | 1 | TRUE | Delayed | Project under consideration on SI side (permitting not started yet in Slovenia) | DCTransmissionLine | Salgareda (IT) | Divaca (SI) | DC | Bipolar | 100 | 500 | 1000 |  | VCS |  | 755 | 0 | 4 | 15% | ++ | ++ | + (between sync areas) | 169 2 | OtherNatureProtectionAreasUnderNationalLaw Other | - | 174 2 | OtherNatureProtectionAreasUnderNationalLaw Other | -
987 | France-Alderney-Britain | 153 | France-Alderney-Britain (FAB) is a new 220km-long HVDC subsea interconnection between Exeter (UK) and Menuel (France) with VSC converter station at both ends. Expected rated capacity is 1250 MW. | 12-2031 | 3 | TRUE | Delayed | Delayed due to uncertainty of regulatory decisions | OffshoreDCTransmissionCable | Menuel (FR) | Exeter (GB) | DC | Monopolar | 220 | 320 | 1250 |  | VCS |  | 1343 | 0 | 21 | +/- 27%% | ++ | ++ | + (between sync areas) | 10 | HabitatsDirective |  | 0 | None
382 | New 330 kV OHL Vilnius-Neris | 170 | New 330 kV OHL Vilnius-Neris. 57,9 km will be constructed as new line and 22,8 km will be used part of exicting 330 kV OHL Vilnius-Molodecno (Vilnius-Molodecno will be disconnected until end of 2025). | 12-2025 | 4 | FALSE | Investment on time |  | ACTransmissionLine | Vilnius | Neris | AC | None | 80.7 | 330 | 0 | 943 |  |  | 56 | 0 | 0.56 | +5%, - 5%% | ++ | ++ | 0
1010 | 330 kV OHL Tartu-Valmiera | 170 | Reinforcement of existing 330 kV OHL. The investment is also a backbone for Baltics Synchronization with CESA. On Estonian territory parallel 110 kV lines will be installed on the common tower (approx. 51 km) to reduce social and environmental impact. | 12-2025 | 5 | FALSE | Ahead of time |  | ACTransmissionLine | Tartu (EE) | Valmiera (LV) | AC | None | 133 | 330 | 0 | 1772 |  |  | 30.66 | 0 | 0.094 | +5%, - 5%% |  |  |  | 0.3 | OtherNatureProtectionAreasUnderNationalLaw
1011 | Valmiera -Tsirguliina 330 kV | 170 | Reinforcement of existing 330 kV OHL. The investment is also a backbone for Baltics Synchronization with CESA | 12-2024 | 4 | FALSE | Investment on time |  | ACTransmissionLine | Tsirguliina (EE) | Valmiera (LV) | AC | None | 60 | 330 | 0 | 1770 |  |  | 22 | 22 | 0.13 | +5%, - 5%% | [6 empty] | 0.6 | HabitatsDirective
1012 | 330 kV OHL Tartu-Balti (L300) | 170 | Reinforcement of existing 330 kV OHL between Balti and Tartu 330 kV substations in Estonia. Old 330 kV line will be replaced with new one with a conductor 3x400 mm2 in phase. The thermal capacity of the line is planned 2400A @ wire max operating temperature 80 degrees celsius. The investment is also a backbone for Baltics Synchronization with CESA (project nr 170). Parallel 110 kV lines will be installed on the common towers along the whole length of the line corridor (approx. 132 km) to reduce social and environmental impact. | 05-2023 | 5 | FALSE | Ahead of time |  | ACTransmissionLine | Balti | Tartu | AC | None | 132 | 330 | 0 | 1770 |  |  | 51.2 | 0 | 0.11 | +5%, - 5%% |  |  |  | 1.4 3.3 | BirdsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 0.5 | HabitatsDirective
1013 | Viru-Tsirguliina 330kV OHL | 170 | Reinforcement of existing 330 kV OHL between Viru and Tsirguliina 330 kV substations in Estonia. Old 330 kV line will be replaced with new one with a conductor 3x400 mm2 in phase. The thermal capacity of the line is planned 2400A @ wire max operating temperature 80 degrees celsius. The investment is also a backbone for Baltics Synchronization with CESA (project nr 170). Parallel 110 kV lines will be installed on the common tower (approx. 14 km) to reduce social and environmental impact. To optimize line lenght and reactive power compensation a new 330 kV substation (named Mustvee) will be constructed in the middle of the power line. | 02-2025 | 4 | FALSE | Ahead of time | Due to accelerated synchronization of the Baltic States, the construction on Viru-Tsirguliina was accelerated. The construction on the line started in June 2023, the line will be energized in December 2024 and officially commissioned in February 2025. | ACTransmissionLine | Viru | Tsirguliina | AC | None | 244 | 330 | 0 | 1770 |  |  | 86.1 | 0 | 0.17 | +5%, - 5%% |  |  |  | 4.7 | OtherNatureProtectionAreasUnderNationalLaw |  | 0.6 | HabitatsDirective
1034 | New HVAC interconnector "Harmony Link" | 170 | New HVAC double-circuit three-phase 220 kV land cable connection between Gižai 110/10 kV substation in Lithuania and existing Elk Bis 400/110 kV substation in Poland. The scope of works of Elk Bis substation focuses in particular on the extension by 220 kV switchgear together with autotransformers and shunt reactors, modernization of primary and secondary equipment, together with control and protection systems and measurement equipment. The scope of works at Gižai substation is design and construction of the 330/220/110 kV substation together with autotransformers and shunt reactors, modernisation of primary and secondary equipment, together with control and protection systems and measurement. Two new 220/110 kV substations in Norki and Wigry will be constructed, together with autotransformers and shunt reactors. The existing Ostroleka-Elk 220 kV overhead line of will be modernized. The overall length of the interconnector is about 240 km. | 12-2030 | 2 | TRUE | Delayed | The main reason of delay is due to unsuccessful converter stations and HDVC cable tenders as in both cases the prices offered significantly exceeded the contracting authorities’ budgets. As a result of it the replanning of the project activities has been started. | OnshoreACTransmissionCable | Gižai | Elk Bis | AC | Bipolar | 330 | 220 | 700 |  | VCS |  | 687 | 0 | 1.0003 | +13%, - 4%% | ++ | ++ | + (between sync areas) | 15 | OtherNatureProtectionAreasUnderNationalLaw
1565 | Reconstruction of 330 kV OHL LE-Vilnius | 170 | Reconstruction of 330 kV OHL LE-Vilnius from single-circuit into double-circuit line. | 11-2020 | 5 | FALSE | Investment on time |  | ACTransmissionLine | Lietuvos E | Vilnius | AC | None | 40.9 | 330 | 0 | 789 |  |  | 18.212 | 0 | 0.18 | +5%, - 5%% | ++ | ++ | 0
1566 | Reconstructions in North Eastern Lithuania | 170 | Reconstruction of 330 kV Utenos and 330 kV Ignalinos AE substations. Relocation of HV equipment (from 330/110/10 kV Ignalinos AE substation to 330/110/10 kV Lietuvos E substation) and changing topology of 330 kV overhead lines. | 12-2021 | 5 | FALSE | Investment on time |  | OnshoreSubstation | Utena | Ignalinos AE | AC | None | 0 | 330 | 0 |  |  |  | 23.35 | 0 | 0.23 | +5%, - 5%%
1568 | Upgrades in Alytus substation (LT) | 170 | Construction of three new 400/330 kV autotransformers in Alytus substation, to connect Lithuania and Poland transmission systems in AC mode. | 12-2021 | 5 | FALSE | Investment on time |  | Transformer | Alytus | - | AC | None | 0 | 400 | 0 |  |  |  | 21.73 | 0 | 0.22 | +5%, - 5%%
1572 | Further infrastructure aspects related to the implementation of the synchronisation of the Baltic States’ system with the continental European network. | 170 | This generic project shall implement the first phase of improvements in system control and stability required for synchronous operation with Continental Europe, including: - development of Baltic AGC and frequency stability assessment systems with special protection schemes; - upgrades of SCADAs and other IT systems and their environment needed for real time operation and planning (WAMS and WAMPAC systems in Latvia, Lithuania and Estonia); - PMU system in Latvia; - upgrade control systems of HVDC connectors (Estlink1, Estlink2 and Nordbalt); - construction of three synchronous condensers, one in each country - in Püssi (Estonia), Ventspils (Latvia) and Alytus (Lithuania); - BESS (Battery Energy Storage System) in Latvia. Further infrastructure aspects ‘not-known-today’ related to the implementation of the synchronisation of the Baltic States’ system with the continental European Network arising from ongoing synchronisation studies. | 12-2025 | 4 | FALSE | Investment on time |  | OnshoreSubstation | - | - | AC | None | 0 | 0 | 0 |  |  |  | 286.11 | 0 | 2.86 | +5%, - 5%%
1632 | New 330 kV Musa substation | 170 | New 330 kV Musa substation. The new substation will create switching capability at the junction of overhead lines Siauliai-Kaunas, Siauliai-Viskali, and Siauliai-Telsiai, which will improve general availability, resilience and throughput of the grid to support synchronization. The project includes territorial planning, land acquisition, procurement, design and construction phases. | 12-2025 | 4 | FALSE | Investment on time |  | OnshoreSubstation | Musa | - | AC | None | 0 | 330 | 0 |  |  |  | 15.7 | 0 | 0.16 | +5%, - 5%%
1634 | New 330 kV OHL Kruonio HAE - Bitenai | 170 | New 330 kV OHL Kruonio HAE - Bitenai. One part of the new line will be constructed as second circuit on existing 330 kV OHL Bitenai-Jurbarkas (39 km), one part will be new line (63 km), and as third part of new line will be used part of exicting 330 kV OHL Kruonio HAE - Sovietsk (Kruonio HAE - Sovietsk will be disconnected until end of 2025). | 10-2025 | 4 | FALSE | Investment on time |  | ACTransmissionLine | KHAE | Bitenai | AC | None | 211 | 330 | 0 | 789 |  |  | 46.38 | 0 | 0.46 | +5%, - 5%% | ++ | ++ | 0
1659 | New 330 kV OHL Darbenai-Bitenai | 170 | New 330 kV OHL Darbenai-Bitenai. One part of the new line will be constructed as second circuit on existing 330 kV OHL Grobine-Klaipeda (45,5 km), second part will be new line (12,1 km), third part will be constructed as second circuit on existing 330 kV OHL Klaipeda-Sysa-Bitenai (79,5 km). | 07-2025 | 4 | FALSE | Investment on time |  | ACTransmissionLine | Darbenai | Bitenai | AC | None | 137 | 330 | 0 | 943 |  |  | 66.97 | 0 | 0.67 | +5%, -5%% | ++ | ++ | 0 | 10.38 | OtherNatureProtectionAreasUnderNationalLaw
1660 | New 330 kV Darbenai substation | 170 | A new 330 kV AC switchyard in Darbenai is part of cross-border interconnection between Lithuania and Poland. It is designed to be a connection point for 330 kV OHL Darbenai-Bitenai (PCI 3.3.10), which, together with 300 kV OHL Kruonio HAE-Bitenai (PCI 3.3.8.), will reinforce Western Lithuanian transmission network as necessary to assure better market integration. It will also enable full integration of 700MW cross-border interconnection between Poland and Lithuania facilitating security of supply criteria and removing existing bottlenecks in the Baltic power grid. The planned switchyard is designed according to 1.5 breaker-bus system. Commissioning of Darbenai switchyard is prerequisite to timely connection of 330 kV OHL Darbenai-Bitenai and cross-border interconnection. | 12-2025 | 4 | FALSE | Rescheduled | The end of construction of Darbėnai substation is expected to be delayed due to contractor’s delay to finalize technical design documentation of 330 kV Darbėnai switchyard. For this reason, the construction permit was received only on June 12th 2023 (initial plan was January 2023). Respectively, the preparation of detailed design and the construction works are being delayed. | OnshoreSubstation | Darbenai | - | AC | None | 0 | 330 | 0 |  |  |  | 16.89 | 0 | 0.17 | +5%, - 5%%
1661 | Construction of new 400kV line Dunowo-Zydowo Kierzkowo | 170 | Dunowo-Zydowo Kierzkowo 400kV line is necessary to assure that after commissioning of Harmony Link and offshore wind farms, full capabilities would be available on the Polish-Lithuanian interconnector. This project includes reconstruction of Dunowo substation with installation of 400/110 kV transformers and construction of new double-circuit 400 kV. | 12-2027 | 4 | FALSE | New Investment |  | ACTransmissionLine | Dunowo | Zydowo Kierzkowo | AC | None | 57.11 | 400 | 0 |  |  |  | 62.679 | 0 | 0.11 | +5%, -5%% | ++ | ++ | 0
1662 | Construction of new 400kV line Pila Krzewina-Zydowo Kierzkowo | 170 | Pila Krzewina-Zydowo Kierzkowo 400kV line is interrelated with project aiming in building Dunowo-Zydowo Kierzkowo line. This project includes reconstruction and modernization of Pila Krzewina electrical station with installation of 400/110 kV transformers and reactive power compensation devices and construction of new double-circuit 400 kV. | 12-2027 | 4 | FALSE | New Investment |  | ACTransmissionLine | Pila Krzewina | Zydowo Kierzkowo | AC | None | 119 | 400 | 0 |  |  |  | 166.085 | 0 | 0.22 | +5%, -5%% | ++ | ++ | 0
1663 | Modernization of 400kV OHL Krajnik-Morzyczyn | 170 | To allow effective energy flows in the north-west part of Poland after commissioning of Harmony Link, modernization of “North Line” (line between Krajnik and Gdansk Blonia) is necessary. The first project of North Line is modernization of Krajnik-Morzyczyn 400kV line. | 05-2023 | 6 | FALSE | New Investment |  | ACTransmissionLine | Krajnik | Morzyczyn | AC | None | 41.5 | 400 | 0 |  |  |  | 0.675 | 0 | 0.04 | +5%, -5%%
1664 | Modernization of 400kV OHL Morzyczyn-Dunowo-Slupsk-Zarnowiec | 170 | Modernisation of Morzyczyn-Dunowo-Slupsk-Zarnowiec 400kV line would be the longest part included in modernization of North Line. Because of its length this project consists of three sections: Modernization of Morzyczyn-Dunowo 400 kV, Modernization of Dunowo-Slupsk 400 kV, Modernization of Slupsk-Zarnowiec 400 kV. | 12-2027 | 4 | FALSE | New Investment |  | ACTransmissionLine | Morzyczyn | Zarnowiec | AC | None | 288.5 | 400 | 0 |  |  |  | 15.627 | 0 | 0.3 | +5%, -5%%
1665 | Modernization of 400kV OHL Zarnowiec-Gdansk/Gdansk Przyjazn-Gdansk Blonia | 170 | Modernisation of Zarnowiec-Gdansk/Gdansk Przyjazn-Gdansk Blonia 400kV line would be the last part included in modernization of North Line. | 12-2025 | 4 | FALSE | New Investment |  | ACTransmissionLine | Zarnowiec | Gdansk Blonia | AC | None | 77 | 400 | 0 |  |  |  | 3.806 | 0 | 0.1 | +5%, -5%%
1669 | Synchronous condensers in Lithuania, Latvia and Estonia | 170 | Synchronous condensers providing inertia, voltage stability,frequency stability and short-circuit power in Lithuania (Neris, Telsiai), Latvia (Grobina, Liksna) and Estonia (Kiisa and Viru). | 12-2025 | 4 | FALSE | Investment on time |  | ReactiveCompensationDevice | 330 kV substations in the Baltics | - | AC | None | 0 | 0 | 0 |  |  | -1170 | 181 | 0 | 1.81 | +5%, - 5%% | + | ++ | ++
1703 | Reconstruction of shunt reactors switchgears | 170 | Due to the synchronisation project the total length of the power lines will increase. Increase in the total length of power lines higher reactive power generation by these lines. In order to reduce the risk that the voltages will rise too high, sufficient amount of reactive power compensation is needed, which can be achieved with the existing shunt reactors. Nevertheless, the shunt reactors need reliable switchgear to help to minimise the risk induced by commutation errors. | 12-2025 | 4 | FALSE | New Investment |  | OnshoreSubstation | Aruküla, Balti, Harku, Kiisa, Paide, Rakvere, Sindi substations | Aruküla, Balti, Harku, Kiisa, Paide, Rakvere, Sindi substations | AC | None | 0 | 330 | 0 |  |  |  | 4.3 | 0 | 0.01 | +5%, - 5%%
1014 | Greenconnector | 174 | Greenconnector is an HVDC interconnector project between Italy and Switzerland for power transport using DC cables rather than overhead lines. The route length is about 165 km. The design power is 1000 MW (1200 MW in overload condition), while the DC voltage is +/- 400 kV DC. Two cables will be installed, working with a bipolar scheme. Great part of the cables route will exploit a section of an existing oil pipeline, no longer in service since January 1997. This pipeline crosses the Italian and Switzerland border at Splgenpass and is running close by the two end stations of the Greenconnector project (Bonaduz in Graubunden Canton and Verderio Inferiore, Lecco). The cables will be pulled inside the pipeline itself, reducing the amount of civil works required before and after cable laying and therefore limiting even temporary environmental impact. For about 47 km the cables will run across the Como lake. | 02-0296 | 3 | TRUE | Delayed | Negotiations with the Swiss authorities are in progress and advancing | DCTransmissionLine | Verderio | Bonaduz | DC | Bipolar | 165 | 400 | 1000 |  | VCS |  | 700 | 20 | 2 | -10 / +15 %% | ++ | ++ | + (between sync areas) | 7.9 4.4 | HabitatsDirective HabitatsDirective |  | 4.7 | IUCNKeyBiodiversityAreas |  | The project avoids the dismatling of about 80 km of an existing oil pipeline no longer in use. The pipeline crosses very sensitive environmental areas (In particular the protected areas mentioned for the Residual environmental and social impacts and mountain areas). Should the pipeline be dismissed, the estimated costs add up to about 25 million euros (supporting documents are available upon request). So our project generates a positive residual impact equal to such amount.
995 | Hansa PowerBridge I | 176 | New HVDC interconnector between Sweden (SE4) and Germany (50 Hertz) aiming to enhance the integration of the Nordic and the continental power market. Moreover the interconnector facilitates RES integration and increases the system adequacy in both systems. | 12-2029 | 3 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Hurva (SE4) | Guestrow (DE) | DC | Monopolar | 300 | 300 | 700 |  | VCS |  | 660 | 0 | 1 | +-15 %% | ++ | ++ | + (between sync areas) | 23 20 30 10 | HabitatsDirective OtherNatureProtectionAreasUnderNationalLaw OtherNatureProtectionAreasUnderNationalLaw BirdsDirective |  | 30 30 | IUCNKeyBiodiversityAreas MarinStrategyFrameworkDirective |  | Tourist area with protected biotopes, water protection areas: 4 km
997 | 997 Pleinting - St. Peter | 187 | new 380-kV-line Pleinting (DE) - St. Peter (AT) on exting OHL corridor | 12-2030 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Pleinting (DE) | St. Peter (AT) | AC | None | 60 | 380 | 0 | 4988 |  |  | 363 | 0 | 3 | 10% | [6 empty] | 2 | OtherNatureProtectionAreasUnderNationalLaw
308 | Vernerov-Vitkov | 200 | New 400 kV double circuit OHL with a transmission capacity of 2 x 2445 A and 83 km length. | 06-2024 | 4 | TRUE | Investment on time |  | ACTransmissionLine | Vernerov (CZ) | Vitkov (CZ) | AC | None | 83 | 400 | 0 | 1694 |  |  | 176.629 | 0 | 0.06 | -10%, +15%% |  |  |  | 35 9 | BirdsDirective HabitatsDirective None |  | 15 | IUCNKeyBiodiversityAreas None |  | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 308, 309 and 314) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environment impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval.
1380 | Würmlach (AT) - Somplago (IT) interconnection | 210 | "Wurmlach (AT) – Somplago (IT) Interconnection is a cross-border electrical line promoted by Alpe Adria Energia Srl. The project concerns a 220kV a.c. merchant line, 300 MW thermal capacity from Somplago substation to new Wurmlach substation, including a Phase Shifter Transformer located in Austria" | 09-2029 | 3 | TRUE | Delayed | PERMITTING - Due to the timing of the release of the exemption decision by the EC as preparatory to the start of the grid connection process in Austria. Furthermore, the commissioning of the line is linked to the construction of the new Wurmlach power station by the TSO and expected in 2029. | ACTransmissionLine | SOMPLAGO | WURMLACH | AC | None | 51 | 220 | 0 | 300 |  |  | 120.3 | 4.5 | 0.9 | 7%% | ++ | ++ | 0 | 2.2 2.2 | HabitatsDirective BirdsDirective None |  | 0.1 | BirdsDirective
1407 | Great Sea Interconnector | 219 | New VSC HVDC link between Cyprus and Israel. | 12-2029 | 4 | TRUE | Delayed | We are currently in discussions to finalize the Cyprus-Israel link and move towards the construction phase, focusing on the investment requirements | OffshoreDCTransmissionCable | Hadera Site | Kofinou Site | DC | Bipolar | 325 | 500 | 1040 |  | VCS |  | 1100 | 0 | 11 | 10% |  |  |  | 1.1 | HabitatsDirective
1409 | Great Sea Interconnector | 219 | New VSC HVDC link between Cyprus and Greece (Crete). | 12-2029 | 4 | TRUE | Investment on time | The National Regulatory Authorities of Greece and Cyprus approved the submitted Investment Request for the Project and agreed on the CBCA between them. The decision "Cross-Border Cost Allocation Between the Hellenic Regulatory Authority for Energy (RAE) and the Cyprus Energy Regulatory Authority (CERA)" provided on 10th of October 2017 concerned the implementation of PCIs 3.10.2 & 3.10.3. With the corresponding decision for PCI 3.10.1 not yet received, and to avoid delays in the implementation of the Project and to be in line with the obligations and commitments arising from the CBCA approval, the Project Promoter decided to amend the order of implementation of the three PCIs consisting PCI 3.10 as follows, with PCIs 3.10.2 & 3.10.3 implemented concurrently: PCI 3.10.3 Interconnection between Korakia, Crete and Attica region(EL) PCI 3.10.2 Interconnection between Kofinou (CY) and Korakia, Crete (EL) PCI 3.10.1 Interconnection between Hadera (IL) and Kofinou (CY). The CBCA has been updated on 23.04.2021 and on 21.07.2023 | OffshoreDCTransmissionCable | Kofinou Site | Korakia (Crete)Site | DC | Bipolar | 921 | 500 | 1000 |  | VCS |  | 1939 | 0 | 19.39 | 5% |  |  |  | 1.1 | None
1107 | 2nd interconnecter between Belgium and Germany | 225 | This investment item envisions the possibility of a second 2 GW HVDC interconnection between Belgium and Germany. Subject to further studies. | 12-2037 | 1 | TRUE | Investment on time |  | DCTransmissionLine | Gramme (BE) | Dahlem (DE) | DC | Bipolar | 110 | 525 | 2000 |  | VCS |  | 1585 | 0 | 15.85 | 10%% | ++ | ++ | + (between sync areas)
627 | 400 kV interconnection RS-BA | 227 | Description of broader context - New double circuit 400 kV OHL connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS) and new double circuit 400kV OHL connecting existing substation Visegrad (BA) and substation Bajina Basta (RS). In the first phase one 400 kV circuit would be equiped. In the second phase New SS Bistrica (RS) would be connected to the exisitng double circuit 400 kV OHL between SS Bajina Basta (RS), SS Visegrad (BA) and SS Pljevlja (ME). Part of regional transmission corridor northeast-southwest. | 09-2027 | 3 | TRUE | Delayed | Updated information regarding the scope of works and investments that will be necessary in order to complete this project. | ACTransmissionLine | SS Bajina Basta | SS Visegrad | AC | None | 45.2 | 400 | 0 | 1330 |  |  | 19.3 | 0 | 0.19 | 5% | ++ | ++ | 0 | 17 | OtherNatureProtectionAreasUnderNationalLaw |  | 1 | MarinStrategyFrameworkDirective
628 | 2x400 kV OHL B.Basta-Obrenovac | 227 | Double circuit 400 kV OHL between upgraded substation Bajina Basta and substation Obrenovac. Part of larger regional transmission corridor northeast-southwest. | 09-2026 | 3 | FALSE | Delayed | Updated information regarding the scope of works and investments that will be necessary in order to complete this project. | ACTransmissionLine | SS Bajina Basta | SS Obrenovac | AC | None | 109 | 400 | 0 | 2660 |  |  | 71.1 | 0 | 0.45 | 5% | ++ | ++ | 0
630 | 400 kV interconnection RS-ME | 227 | Description of broader context - New double circuit 400kV OHL connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS) and new double circuit 400kV OHL connecting existing substation Visegrad (BA) and substation Bajina Basta (RS). In the first phase one 400 kV circuit would be equiped. In the second phase New SS Bistrica (RS) would be connected to the exisitng double circuit 400 kV OHL between SS Bajina Basta (RS), SS Visegrad (BA) and SS Pljevlja (ME). Part of regional transmission corridor northeast-southwest. | 09-2027 | 3 | TRUE | Delayed | Updated information regarding the scope of works and investments that will be necessary in order to complete this project. | ACTransmissionLine | SS Bajina Basta | SS Pljevlja | AC | None | 98.4 | 400 | 0 | 1330 |  |  | 41.9 | 0 | 0.42 | 5% | ++ | ++ | 0 | 17 | OtherNatureProtectionAreasUnderNationalLaw |  | 1 | MarinStrategyFrameworkDirective
631 | Upgrading SS Bajina Basta to 400 kV voltage level | 227 | Upgrade of existing 220/110 kV substation in Bajina Basta to 400/220/110 kV substation as part of overall western Serbia system upgrade to 400 kV voltage level. Part of larger regional transmission corridor northeast-southwest. | 09-2026 | 3 | FALSE | Delayed | Updated information regarding the scope of works and investments that will be necessary in order to complete this project. | OnshoreSubstation | Bajina Basta (RS) | Bajina Basta (RS) | AC | None | 0 | 400 | 0 |  |  |  | 18.6 | 0 | 0.14 | 5%
1526 | 400 kV OHL Lastva - Pljevlja | 227 | 400 kV OHL Lastva - Pljevlja | 09-2024 | 4 | FALSE | Delayed | Adjusted to match the remainder of the project. Also, the project faced some issues regarding the land ownership. Those will not harm the construction. | ACTransmissionLine | SS Lastva | SS Pljevlja | AC | None | 151 | 400 | 0 | 1385 |  |  | 70.2 | 0 | 0.7 | 5% | ++ | ++ | 0
1888 | Equipping the 2nd circuit from SS Visegrad to SS Pljevlja | 227 | Equipping the 2nd circuit from SS Visegrad to SS Pljevlja | 09-2030 | 3 | FALSE | New Investment |  | ACTransmissionLine | SS Visegrad | SS Pljevlja | AC | None | 91 | 400 | 0 | 1330 |  |  | 9 | 0 | 0.09 | 5% |  |  |  | 17 | OtherNatureProtectionAreasUnderNationalLaw |  | 1 | MarinStrategyFrameworkDirective
1231 | Muhlbach Eichstetten | 228 | Reinforcement of the existing 400kV OHL and deployment of a second 400kV circuit at existing double circuit OHL Muhlbach - Eichstetten, instead of the currently operated circuit Eichstetten - Vo-gelgrun (currently operated with 225kV). The project includes also a transformer in Sierentz substation to balance flows between 225kV and 400kV grid in the area. | 12-2027 | 3 | TRUE | Rescheduled | Adjustment of commissioning date to 2027 during the project planning process. | ACTransmissionLine | Muhlbach | Eichstetten | AC | None | 32 | 400 | 0 |  |  |  | 147.5 | 0 | 1.47 | 10%% | ++ | ++ | 0
1282 | 380 kV Grid Reinforcement Beznau - Tiengen | 231 | This projects helps to increase the cross border capacity between Switzerland and Germany by upgrading an existing line from 220 kV to 380 kV including internal reinforcements. | 12-2035 | 2 | TRUE | Investment on time |  | ACTransmissionLine | Beznau (CH) | Tiengen (DE) | AC | None | 11 | 380 | 0 | 2369 |  |  | 59.6 | 0 | 0.47001 | 10%% | - | - | 0 | 0 | Other |  | 0 | Other
664 | HVDC LINE C - SUEDLINK | 235 | New DC-lines to integrate new wind generation from Northern Germany towards Southern Germany and Southern Europe for consumption and storage. | 12-2028 | 3 | TRUE | Rescheduled |  | DCTransmissionLine | Brunsbüttel, Wilster | Großgartach, Bergrheinfeld West | DC | Bipolar | 1250 | 525 | 4000 |  | VCS |  | 10600 | 0 | 85 | +-20%% | ++ | ++ | + (between sync areas) | 121 | OtherNatureProtectionAreasUnderNationalLaw |  | 157 | OtherNatureProtectionAreasUnderNationalLaw
1241 | Fenno-Skan 3 | 239 | Replacement of the existing 400 kV HVDC cable interconnection between Finland and Sweden. Fennoskan 1 will be decommissioned and a new interconnector with the capacity of 800 MW will be built between FI and SE3, resulting in a total capacity of 1600 MW between FI and SE3. | 06-2038 | 1 | TRUE | Rescheduled | According to new studies, Fenno-Skan 1 lifetime can be continued until 2040 and this project will be commissioned after that. | OffshoreDCTransmissionCable | SE3 | FI | DC | None | 250 | 500 | 800 |  | VCS |  | 700 | 0 | 5.25 | +/- 20 %% | ++ | ++ | + (between sync areas)
1269 | New 400 kV overhead line Sombor (RS) - Ernestinovo (HR) | 243 | The project necessity stems for the need to increase the transfer capacity between RS and HR in order to accommodate connection of RES and improve market integration, according to the results based on TYNDP CBA. | 09-2038 | 1 | TRUE | Delayed | There is a slight delay due to the new circumstances and observations regarding the project. | ACTransmissionLine | SS Ernestinovo | SS Sombor 3 | AC | None | 70 | 400 | 0 | 1330 |  |  | 44 | 0 | 0.4 | 15% | ++ | ++ | 0
1245 | Vigy - Uchtelfangen (or beyond) | 244 | Upgrade of existing transmission OHL between Vigy and Uchtelfangen (or beyond) to increase the thermal cross-border capacity. To reach a higher capacity the options are High Temperature Low Sag (HTLS) conductors or a reconstruction of the tie-line in the existing route . | 12-2029 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Vigy (FR) | Uchtelfangen (DE) | AC | None | 65 | 400 | 0 |  |  |  | 78 | 0 | 0.624 | 10%% | - | - | 0
1514 | Power flow control between Vigy and Ensdorf | 244 | Installation of Phase Shift Transformers (PSTs) in Ensdorf substation to allow an optimal use of the capacity increase. | 12-2029 | 3 | FALSE | Investment on time |  | PhaseShiftingTransformer | Vigy (FR) | Ensdorf (DE) | AC | None | 0 | 400 | 0 |  |  |  | 66 | 0 | 0.528 | 10%%
1381 | AQUIND Interconnector | 247 | AQUIND Interconnector is a proposed High Voltage Direct Current (HVDC) subsea and underground electric power transmission link between Great Britain (Lovedean substation, Hampshire) and France (Barnabos substation, Seine-Maritime) with a net transmission capacity of 2,000 MW. The Interconnector is designed as two parallel monopole 1000 MW circuits employing Voltage Source Converter technology. | 09-2028 | 3 | TRUE | Delayed | Since TYNDP 2022, ongoing delay in implementation of energy chapter of the Trade and Cooperation Agreement together with the delay of the third Cap&Floor window by Ofgem resulted in a delay with permitting and regulatory procedures in GB and France. Respectively commissioning of the project moved to 2028. | OffshoreDCTransmissionCable | Lovedean (GB) | Barnabos (FR) | DC | Monopolar | 240 | 320 | 2075 |  | VCS |  | 1560 | 60 | 18 | +/-10% | ++ | ++ | + (between sync areas)
1384 | Merchant line "Castasegna (CH) - Mese (IT)" | 250 | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Rationalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200 MW.The main Project elements are (merchant line): 220 kV Connection to the Swiss HVG in Castasegna; 220 kV Cable line of around 14 km between Castasegna and Mese; 220/380 kV Substation with PST 250 MVA in Mese. The Grid Rationalisation in the Region of Mese foresees the following actions: Displacement of 2 km of the 380 kV Line "Soazza - Bulciago"; "Realisation of a new 380/132 kV Substation in Mese (Transformation 2 x 250 MVA); Displacement of 0.8 km of 132 kV Lines; Realisation of 2.6 km of 132 kV Cable connections; Demolition of 2.45 km of 380 kV line and 2.3 km of 132 kV lines." | 03-2025 | 3 | TRUE | Delayed | The permitting phase in Italy is ongoing since April 2014 but we are still facing some challenges regarding Environmental impact of the 380/132kV Substation Terna in Mese. Commissioning expected in 2025. | ACTransmissionLine | Castasegna | Mese | AC | None | 14 | 220 | 0 | 250 |  |  | 90 | 0 | 0.1 | +/-15% | [9 empty] | Environmental positive impact due to the connected grid rationalisation 380/132kV in the region of Mese. Improvement N-1 security for hydro power plant production transmission in Castasegna (CH).
660 | HVDC Line A South - Ultranet | 254 | New HVDC-lines from Osterath to Philippsburg to integrate new wind generation especially from North Sea towards Central-South Germany for consumption and storage. | 12-2026 | 3 | TRUE | Investment on time |  | DCTransmissionLine | Osterath (DE) | Philippsburg (DE) | DC | Bipolar | 342 | 400 | 2000 |  | VCS |  | 2180.6 | 0 | 17.45 | 10%% |  |  |  | 12.6 16.7 209 | HabitatsDirective BirdsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 4.5 15.4 183.3 49.5 | HabitatsDirective RAMSARSite IUCNKeyBiodiversityAreas MarinStrategyFrameworkDirective
1205 | New 400 kV OHL Debrecen Dél (HU) - Oradea Sud (RO) | 259 | New 90 km single circuit 400 kV OHL between Hungary and Romania (60 km on Hungarian and 30 km on Romanian side). Internal investments in Romania associated to the project are also included. | 12-2030 | 2 | TRUE | Investment on time |  | ACTransmissionLine | Debrecen Dél | Oradea Sud | AC | None | 90 | 400 | 0 | 1384 |  |  | 145.43 | 0.71 | 0.72715 | -5%, +5%% | ++ | ++ | 0
1832 | New 400/220 kV transformer in substation Rosiori (RO) | 259 | New 400/220 kV transformer in substation Rosiori | 12-2027 | 2 | FALSE | Investment on time |  | Transformer | Rosiori (RO) | Rosiori (RO) | AC | None | 0 | 0 | 0 | 400 |  |  | 5.22 | 0 | 0.052002 | ± 5%%
1833 | Reconductoring of 220 kV OHL Urechesti (RO) -Targu Jiu Nord (RO) | 259 | Reconductoring 220 kV OH line Urechesti-Tg. Jiu Nord | 12-2028 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Urechesti (RO) | Targu Jiu Nord (RO) | AC | None | 22 | 220 | 0 | 450 |  |  | 2.205 | 0.13 | 0.021999 | ±5%%
1834 | Reconductoring of 220 kV OHL Targu Jiu Nord (RO)- Paroseni (RO) | 259 | Reconductoring 220 kV OH line Tg. Jiu Nord - Paroseni | 12-2028 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Targu Jiu Nord (RO) | Paroseni (RO) | AC | None | 38 | 220 | 0 | 450 |  |  | 3.81 | 0.23 | 0.038001 | ± 5%%
1835 | Reconductoring of 220 kV OHL Paroseni (RO)- Baru Mare (RO) | 259 | Reconductoring 220 kV OH line Paroseni- Baru Mare | 12-2028 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Paroseni (RO) | Baru Mare (RO) | AC | None | 20.2 | 220 | 0 | 450 |  |  | 2.02 | 0.12 | 0.02 | ± 5%%
1836 | Reconductoring of 220 kV OHL Baru Mare (RO) -Hasdat (RO) | 259 | Reconductoring 220 kV OH line Baru Mare-Hasdat | 12-2028 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Baru Mare (RO) | Hasdat (RO) | AC | None | 43.9 | 400 | 0 | 450 |  |  | 4.4 | 0.262 | 0.022 | ±5%%
1865 | 2nd circuit of 400kV OHL Nadab (RO) - Bekescsaba (HU) | 259 | 2nd circuit of 400kV OHL Nadab (Romania) - Bekescsaba (Hungary) | 12-2027 | 2 | FALSE | New Investment |  | ACTransmissionLine | Nadab | Bekescsaba | AC | None | 59.62 | 400 | 0 | 1741 |  |  | 22.34 | 0.36 | 0.040011 | 5%
1255 | Interconnector GB-NL | 260 | Multi-purpose interconnector between GB and NL also connecting GB and NL windfarms. | 12-2030 | 1 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | TBD | TBD | DC | None | 0 | 525 | 1800 |  | VCS |  | 1200 | 0 | 35.004 | ±10%% | ++ | ++ | + (between sync areas)
1262 | Hansa PowerBridge II | 267 | Possible second HVDC cable interconnector between southern Sweden (Bidding area SE4) and Germany (50Hertz). This project candidate is driven by market based target capacities found in the Common Planning Studies by Regional Group Baltic Sea. | 12-2040 | 1 | TRUE | Delayed | Postponement of commissioning, currently the full focus is on HBPI. | OffshoreDCTransmissionCable | Hurva (SE4) | Gnewitz (DE) | DC | None | 300 | 300 | 700 |  | VCS |  | 600 | 0 | 6 | +-15%% | ++ | ++ | + (between sync areas)
1211 | HVDC Aragon region -Marsillon | 270 | New axis Aragon region -Marsillon | 12-2041 | 1 | TRUE | Investment on time |  | DCTransmissionLine | Aragon region | Marsillon | DC | None | 120 | 320 | 2000 |  | VCS |  | 2300 | 0 | 3.2591 | 5%% | ++ | ++ | + (between sync areas) | 61 | Other |  | 12 | HabitatsDirective
1212 | New axis Ejea-Aragon region 400 kV | 270 | New AC line (double circuit 400kV) between Ejea and Aragon region where the converter station is located | 09-2030 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Ejea de los Caballeros | Aragon region | AC | None | 110 | 400 | 0 |  |  |  | 62 | 0 | 0.89999 | 10%% | ++ | ++ | 0
1214 | Ejea de los Caballeros subestation | 270 | New 400kV Ejea de los Caballeros subestation and connection to the lines La Serna-Magallon and Magallon Peñalba | 09-2030 | 2 | FALSE | Investment on time |  | OnshoreSubstation | Ejea de los Caballeros | Ejea de los Caballeros | AC | None | 0 | 400 | 0 |  |  |  | 0 | 0 | 0 | 10%%
1215 | Aragon region subestation | 270 | New 400 kV Aragon region subestation and connection to existing network and future cross border project | 09-2030 | 2 | FALSE | Investment on time |  | OnshoreSubstation | Aragon region | Aragon region | AC | None | 0 | 400 | 0 |  | VCS |  | 10 | 0 | 0.03 | 10%%
2024 | Upgrade Cantegrit-Marsillon | 270 | Upgrade of existing 2*225kV line Cantegrit-Marsillon to 1* 400kV | 00-0000 | 1 | FALSE | Rescheduled |  | ACTransmissionLine | Cantegrit | Marsillon | AC | None | 80 | 400 | 0 |  |  |  | 150 | 0 | 1.9999 | 10%
1206 | HVDC Pamplona area - Cantegrit | 276 | HVDC Pamplona area(Spain) -Cantegrit (France) | 12-2037 | 1 | TRUE | Investment on time |  | DCTransmissionLine | Pamplona area | Cantegrit | DC | None | 225 | 320 | 2000 |  | VCS |  | 2300 | 0 | 5.3291 | 5%% | ++ | ++ | + (between sync areas) | 20 | Other |  | 2 | HabitatsDirective
1207 | Upgrade Cantegrit-Saucats | 276 | Upgrade of 2* 400 kV lines Cantegrit-Saucats | 00-0000 | 1 | FALSE | Rescheduled |  | ACTransmissionLine | Cantegrit | Saucats | AC | None | 70 | 400 | 0 |  |  |  | 150 | 0 | 1.9999 | 10%% | - | - | 0
1210 | New substation Pamplona area | 276 | New substation Pamplona area 400 kV and connection to the 400 kV line Ichaso-Castejón/Muruarte? | 12-2030 | 2 | FALSE | Investment on time |  | OnshoreSubstation | Pamplona area | Pamplona area | AC | None | 0 | 400 | 0 |  |  |  | 9 | 0 | 0.17 | 10%%
1008 | Lonny-Achene-Gramme | 280 | Installation of PST and line capacity upgrade of Lonny-Achene-Gramme | 12-2030 | 2 | TRUE | Investment on time |  | ACTransmissionLine | Lonny (FR) | Gramme (BE) | AC | None | 100 | 400 | 0 | 2700 |  |  | 148 | 0 | 0.518 | 10%% | - | - | 0
1378 | TuNur DC | 283 | The HVDC transmission architecture is based on two independent bipolar +/-525 kV systems of 1GW. The HVDC converter is based on VSC (Voltage Source Converter) technology, providing high reliability and efficiency of the transmission system. TuNur DC will consist of two independent bipolar +/-525 kV systems of 1GW. Each bipolar system will consist of a DC overhead line in Tunisia spanning from the power plant to the shoring point, submarine cable from the Tunisian Northern coast to Montalto di Castro, and VSC HVDC converter stations at both terminal points. | 02-2034 | 1 | TRUE | Delayed | The project timeline has been delayed due to the evolution of the regulatory frameworks and supply chain constraints (specifically HVDC cable supply). | OffshoreDCTransmissionCable | Rejim Maatoug (TUN) VSC HVDC - +/- 500 kV DC – 2x 1GW | Montalto di Castro (ITA) VSC HVDC - +/- 500 kV DC - 400 kV AC – 2x 1GW | DC | Bipolar | 1308 | 525 | 2000 |  | VCS |  | 4807 | 817.2 | 40.5999 | 8% | ++ | ++ | + (between sync areas) | 1 | RAMSARSite |  |  |  |  | TuNur DC: Job Creation - Creation of numerous qualified jobs in Tunisia for the construction and O&M of the land lines and HVDC converters
1430 | TuNur AC | 283 | 400 kV AC underground cables from the HVDC converter in Montalto to Terna’s 400 kV station in Montalto. CAPEX includes 2 circuit breaker bays within Terna’s station. | 02-2034 | 1 | FALSE | Delayed | The project timeline has been delayed due to the evolution of the regulatory frameworks and supply chain constraints (specifically HVDC cable supply). | OnshoreACTransmissionCable | Montalto di Castro (ITA) VSC HVDC - +/- 500 kV DC - 400 kV AC – 2x 1GW | Montalto di Castro (IT) Terna station 400 kV AC | AC | None | 2 | 400 | 0 | 2100 |  |  | 20 | 3.4 | 0.1 | 8% of the overall project cost as exact length is not yet confirmed, it being understood that the impact of the short AC cable on the overall project will be negligible.% | ++ | ++ | 0 | [6 empty] | TuNur DC: Job Creation - Creation of numerous qualified jobs in Tunisia for the construction and O&M of the land lines and HVDC converters
1383 | GridLink | 285 | UK-France, 1.4GW HVDC Interconnector | 12-2025 | 3 | TRUE | Delayed | Brexit - investment request submitted but declared void on 24 December 2020 as there were no provisions in the FTA which would allow the French & UK regulators to continue to have competence to decide the investment request. A new investment request was submitted solely to CRE in March 2021. | OffshoreDCTransmissionCable | Kingsnorth (UK) | Warande (Gravelines, France) | DC | Monopolar | 158 | 525 | 1400 |  | VCS |  | 1510 | 1570 | 23.38 | 10% |  |  |  |  | None
604 | BRABO III: Liefkenshoek - Mercator | 297 | The existing 150kV overhead will be upgraded to a single 380kV overhead line between the site Liefkenshoek and the substation Mercator. To facilitate this upgrade, the adjacent 150kV grid will be adapted. | 12-2026 | 4 | TRUE | Delayed | Permitting process took longer than expected | ACTransmissionLine | Liefkenshoek (BE) | Mercator (BE) | AC | None | 19 | 380 | 0 | 1900 |  |  | 120 | 0 | 0.2 | 20%% | ++ | ++ | 0 | 4 | BirdsDirective |  | 14.7 | HabitatsDirective
1458 | SACOI 3 | 299 | New HVDC triterminal link between Italy mainland, Corsica and Sardinia replacing existing link SACOI 2 | 12-2027 | 4 | TRUE | Investment on time |  | DCTransmissionLine | Codrongianos - Lucciana | Suvereto | DC | Bipolar | 410 | 200 | 400 |  | VCS |  | 1820 | 0 | 13.1 | 10% | ++ | ++ | + (between sync areas) | 0 | Other | - | 3 | Other | - | -
1628 | NeuConnect Interconnector | 309 | 1.4GW HVDC Interconnector between UK and Germany | 06-2026 | 4 | TRUE | Delayed | The project connection date is delayed due events outwith of NeuConnect's direct control | OffshoreDCTransmissionCable | Grain West 400kV Substation | Fedderwarden 380kV Substation | DC | Bipolar | 720 | 500 | 1400 |  | VCS |  | 2075.82 | 49 | 32.3 | 10%%
1472 | St. Peter (AT) - Tauern (AT) | 312 | new 380-kV-Line | 12-2025 | 4 | TRUE | Delayed | Duration of permitting process. | ACTransmissionLine | St. Peter | Tauern | AC | None | 128 | 380 | 0 | 4818 |  |  | 1109 | 0 | 0.8 | 10%% | [6 empty] | 43 | None
1473 | Isar/Altheim/Ottenhofen - St. Peter | 313 | New 380kV double circuit OHL Isar/Altheim/Ottenhofen - St. Peter including new 380kV switchgears Altheim, Pirach, Simbach and St. Peter. | 12-2027 | 3 | TRUE | Delayed | Delay due to complex and long permitting process | ACTransmissionLine | Isar/Altheim/Ottenhofen (DE) | St. Peter (AT) | AC | None | 90 | 380 | 0 | 4988 |  |  | 619 | 0 | 5 | 10% |  |  |  | 4 | OtherNatureProtectionAreasUnderNationalLaw
1478 | Dekani (SI) - Zaule (IT) interconnection | 323 | The Zaule (IT) - Dekani (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3 d.o.o. and HSE d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Zaule (IT) substation to Dekani substation, including a 110/135 kV Phase Shifter Transformer. | 08-2026 | 3 | TRUE | Delayed | The promoter asked the respective NRA for the NTC recalculation not subject to conditions (eg third party network reinforcements), which will be guaranteed for the exemption period and from the entry into the new commercial operation date (COD) of the interconnector. The process was concluded in July 2023. | ACTransmissionLine | DEKANI | ZAULE | AC | None | 11 | 110 | 0 | 125 |  |  | 26 | 0.4 | 0.26 | 7%% | ++ | ++ | 0 |  | None |  |  | None
1482 | Redipuglia (IT) - Vrtojba (SI) Interconnection | 324 | "The Redipuglia (IT) - Vrtojba (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3 d.o.o. and HSE d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Redipuglia (IT) substation to Vrtojba (SI) substation, including a 110/135 kV Phase Shifter Transformer." | 08-2026 | 3 | TRUE | Delayed | The promoter asked the respective NRA for the NTC recalculation not subject to conditions (eg third party network reinforcements), which will be guaranteed for the exemption period and from the entry into the new commercial operation date (COD) of the interconnector. The process was concluded in July 2023. | ACTransmissionLine | REDIPUGLIA | VRTOJBA | AC | None | 22.5 | 110 | 0 | 125 |  |  | 46 | 0.59 | 0.46 | 7%% | ++ | ++ | 0
1483 | Upgrade Obersielach (AT) - Podlog (SI) | 325 | upgrade from 220 kV to 380 kV | 06-2035 | 1 | TRUE | Investment on time |  | ACTransmissionLine | Obersielach (AT) | Podlog (SI) | AC | None | 70 | 380 | 0 | 1330 |  |  | 249 | 0 | 0.19995 | 10% | ++ | ++ | 0 | 4 | OtherNatureProtectionAreasUnderNationalLaw |  | 81 | OtherNatureProtectionAreasUnderNationalLaw
1620 | Substation Aach | 328 | New 400/220-kV-substation | 12-2026 | 2 | FALSE | Investment on time |  | OnshoreSubstation | N/A | N/A | AC | None | 0 | 400 | 0 |  |  |  | 40 | 0 | 0.128 | 10%% | [9 empty] | The project replaces an existing overhead line.
1629 | Substation Bofferdange | 328 | New 400/220/110 kV substation including transformer 400/220 kV to be commissioned in Bofferdange (LU) | 12-2028 | 3 | FALSE | Investment on time |  | OnshoreSubstation | N/A | N/A | AC | None | 0 | 400 | 0 |  |  |  | 88 | 0 | 0.34 | 10%% | [9 empty] | The project replaces an existing overhead line.
1630 | AC Overhead Line Aach-Bofferdange | 328 | New AC Overhead Line between Germany and Luxembourg | 12-2028 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Aach (DE) | Bofferdange (LU) | AC | None | 40 | 400 | 0 |  |  |  | 118 | 0 | 0.67 | 10%% | ++ | ++ | 0 | [6 empty] | The project replaces an existing overhead line.
1518 | Stevin-Izegem/Avelgem: new corridor | 329 | Realisation of a new AC corridor up to 6 GW capacity | 12-2028 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Stevin | Avelgem | AC | None | 82 | 380 | 0 | 3000 |  |  | 700 | 0 | 0.6 | 25%% | ++ | ++ | 0
1498 | New CZ-SK 400 kV interconnector | 330 | This investment consists of single circuit 400 kV OHL Otrokovice (CZ) - Ladce (SK). | 12-2035 | 1 | TRUE | New Investment |  | ACTransmissionLine | Otrokovice (CZ) | Ladce (SK) | AC | None | 78 | 400 | 0 | 1694 |  |  | 112.949 | 0 | 0.37273 | ±10%%
1499 | Extension of 400 kV substation Ladce | 330 | This investment consists of the extension of 400 kV substation Ladce, which will replace existing 220 kV substation Považská Bystrica and will therefore increase security of supply in this particular region. After commissioning this new 400 kV substation it will be possible to build new 400 kV cross-border OHL from Ladce (SK) to Otrokovice (CZ). | 12-2035 | 2 | FALSE | New Investment |  | OnshoreSubstation | Ladce (SK) | Ladce (SK) | AC | None | 0 | 400 | 0 |  |  |  | 3.8 | 0 | 0.19 | ±10%%
1504 | Danish Hub | 335 | Hub installation suitable to connect 2GW of HVDC systems to Danish shore and up to 4GW of nearby offshore wind. Danish hub is connected to German and Dutch hub with 2 GW HVDC systems each. | 01-2032 | 1 | TRUE | Investment on time |  | OffshoreSubstation | 0 | 0 | AC | None | 0 | 0 | 0 |  |  |  | 1994 | 0 | 6.6001 | The Capex uncertainty range for this asset is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1505 | Interconnection DKw to Danish hub | 335 | HVDC connector including substations interfacing the Danish hub and the Western Danish power system. | 01-2032 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | REVSING | Danish hub | DC | None | 256 | 525 | 2000 |  | VCS |  | 1160 | 0 | 5.8 | The Capex uncertainty range for this 525kV link covers -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1506 | Interconnection NL Maasvlakte to Dutch hub (#1) | 335 | One of two HVDC connectors including substations interfacing the Dutch hub and the Dutch power system. | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Maasvlakte 380 kV | Dutch hub | DC | None | 356 | 525 | 2000 |  | VCS |  | 1710 | 0 | 8.5996 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1507 | Interconnection NL Maasvlakte to Dutch hub (#2) | 335 | One of two HVDC connectors including substations interfacing the Dutch hub and the Dutch power system. | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Maasvlakte 380 kV | Dutch hub | DC | None | 356 | 525 | 2000 |  | VCS |  | 1710 | 0 | 8.5996 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1508 | Interconnection DE (Heide(West)) to German hub | 335 | One of three HVDC connectors including substations interfacing the German hub and the German power system. | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Heide(West) | German hub | DC | None | 348 | 525 | 2000 |  | VCS |  | 1681 | 0 | 8.4 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1509 | Interconnection DE (area north of Bremen) to German hub | 335 | One of three HVDC connectors including substations interfacing the German hub and the German power system. | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | German substation located in the area north of Bremen | German hub | DC | None | 423 | 525 | 2000 |  | VCS |  | 1960 | 0 | 9.8 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1511 | Interconnection DE (area of Rastede) to German hub | 335 | One of three HVDC connectors including substations interfacing the German hub and the German power system. | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | German substation located in the area of Rastede | German hub | DC | None | 369 | 525 | 2000 |  | VCS |  | 1759 | 0 | 8.8003 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1815 | Dutch Hub | 335 | Hub installation suitable to connect 4GW of HVDC systems to Dutch shore and up to 4W of nearby offshore wind. Dutch hub is connected to the Danish and German hub with 2 GW HVDC systems each. | 01-2035 | 1 | TRUE | Investment on time |  | OffshoreSubstation | 0 | 0 | AC | None | 0 | 0 | 0 |  |  |  | 1994 | 0 | 6.6001 | The Capex uncertainty range for this asset is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1816 | German Hub | 335 | Hub installation suitable to connect 6 GW of HVDC systems to German shore and up to 6 GW of nearby offshore wind. German hub is connected to the Danish and Dutch hub with 2 GW HVDC systems each. | 01-2035 | 1 | TRUE | Investment on time |  | OffshoreSubstation | 0 | 0 | AC | None | 0 | 0 | 0 |  |  |  | 2991 | 0 | 9.9989 | The Capex uncertainty range for this asset is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1817 | Interconnection Danish hub to Dutch hub | 335 | One of three HVDC connectors including substations interfacing 2 of the 3 hubs | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Danish hub | Dutch hub | DC | None | 351 | 525 | 2000 |  | VCS |  | 1306 | 0 | 6.5 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1818 | Interconnection Danish hub to German hub | 335 | One of three HVDC connectors including substations interfacing 2 of the 3 hubs | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Danish hub | German hub | DC | None | 226 | 525 | 2000 |  | VCS |  | 841 | 0 | 4.2 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1819 | Interconnection Dutch hub to German hub | 335 | One of three HVDC connectors including substations interfacing 2 of the 3 hubs | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Dutch hub | German hub | DC | None | 125 | 525 | 2000 |  | VCS |  | 465 | 0 | 2.2999 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1521 | New HVDC line between Villanova and Fano existing 400 kV substations | 338 | HVDC lines | 12-2028 | 3 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Villanova | Fano | DC | None | 560 | 500 | 1000 |  | VCS |  | 1506 | 0 | 3.53 | 10% | ++ | ++ | + (between sync areas)
1557 | Tyrrhenian HVDC link - West | 339 | Italian HVDC tri-terminal link | 12-2027 | 4 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Caracoli | Selargius | DC | None | 900 | 500 | 1000 |  | VCS |  | 1900 | 0 | 3.6 | 0% | ++ | ++ | + (between sync areas) | 43 | Other | - | 36 | Other | -
1795 | Tyrrhenian HVDC link - East | 339 | Tyrrhenian HVDC link - East | 12-2028 | 4 | FALSE | New Investment | - | OffshoreDCTransmissionCable | Montecorvino | Caracoli | DC | None | 424 | 500 | 1000 |  | VCS |  | 1800 | 0 | 3.4 | 0%
1519 | Avelgem-Courcelles | 340 | Realisation of a 6 GW new corridor | 12-2030 | 3 | TRUE | Delayed | Permitting procedure | ACTransmissionLine | Avelgem | Courcelles | AC | None | 90 | 380 | 0 | 3000 |  |  | 510 | 0 | 0.6 | 25%% | ++ | ++ | 0
1536 | Portile de Fier (RO) - Djerdap (RS) 2nd | 341 | Portile de Fier (RO) - Djerdap (RS) 2nd . Doubling the existing OHL 400 kV (1.5 km on Serbian (thermal limit 1800 A) and 0.5 km on Romanian( thermal limit 2192 A) Side) | 09-2029 | 2 | TRUE | Investment on time |  | ACTransmissionLine | Portile de Fier | Djerdap | AC | None | 2 | 400 | 0 | 1247 |  |  | 8.32 | 0 | 0.079997 | 5% | ++ | ++ | 0
1537 | New SS 400/110 kV Belgrade 50 | 341 | New SS 400/110 kV Belgrade 50 (former name Belgrade West) | 09-2028 | 3 | FALSE | Investment on time |  | Transformer | Belgrade 50 | Belgrade 50 | AC | None | 0 | 400 | 0 | 600 |  |  | 48.3 | 0 | 0.48 | 5%
1538 | New OHL 400 kV WPP Cibuk - SS Belgrade 50 | 341 | New OHL 400 kV WPP Cibuk - SS Belgrade 50 | 09-2028 | 3 | FALSE | Investment on time |  | ACTransmissionLine | WPP Cibuk | SS Belgrade 50 | AC | None | 83 | 400 | 0 | 2660 |  |  | 31.7 | 0 | 0.32 | 5% | ++ | ++ | 0 | 33.75 4.7 | Other Other | Important bird area (IBA), but out of EU territory International Ecological Corridors
1864 | Reconductoring of 220kV double circuit OHL Portile de Fier - Resita | 341 | Reconductoring of 220kV double circuit OHL Portile de Fier (Romania) - Resita (Romania) | 12-2028 | 2 | FALSE | New Investment |  | ACTransmissionLine | Portile de Fier 220kV | Resita 220kV | AC | None | 116.55 | 220 | 0 | 450 |  |  | 13.6 | 0.9 | 0.068503 | 5%
1520 | SS Bobov Dol (BG) - SS Leskovac 2 (RS) | 342 | Second interconnection line on the border between Bulgaria and Serbia | 09-2034 | 2 | TRUE | Investment on time |  | ACTransmissionLine | SS Bobov Dol | SS Leskovac 2 | AC | None | 123 | 400 | 0 | 1330 |  |  | 75 | 0 | 0.75 | 5% | ++ | ++ | 0
1522 | Upgrade of existing OHL 220 kV to 400 kV SS Nis 2 - SS Krusevac 1 | 342 | Upgrade of existing OHL 220 kV to 400 kV SS Nis 2 - SS Krusevac 1 | 09-2034 | 2 | FALSE | Investment on time |  | ACTransmissionLine | SS Nis 2 | SS Krusevac 1 | AC | None | 72 | 400 | 0 | 1330 |  |  | 28 | 0 | 0.28 | 5%
1523 | Upgrading SS 220/110 kV Krusevac 1 to 400 kV | 342 | Upgrading SS 220/110 kV Krusevac 1 to 400 kV | 09-2034 | 2 | FALSE | Investment on time |  | OnshoreSubstation | SS Krusevac 1 | SS Krusevac 1 | AC | None | 0 | 400 | 0 |  |  |  | 9.3 | 0 | 0.089996 | 5%
1524 | Upgrade of existing OHL 220 kV to 400 kV SS Krusevac 1 - SS Kraljevo 3 | 342 | Upgrade of existing OHL 220 kV to 400 kV SS Krusevac 1 - SS Kraljevo 3 | 09-2034 | 2 | FALSE | Investment on time |  | ACTransmissionLine | SS Krusevac 1 | SS Kraljevo 3 | AC | None | 48 | 400 | 0 | 1330 |  |  | 18.7 | 0 | 0.18001 | 5%
1525 | Upgrade of existing OHL 220 kV to 400 kV SS Kraljevo 3 - SY Pozega | 342 | Upgrade of existing OHL 220 kV to 400 kV SS Kraljevo 3 - SY Pozega | 09-2034 | 2 | FALSE | Investment on time |  | ACTransmissionLine | SS Kraljevo 3 | SY Pozega | AC | None | 70 | 400 | 0 | 1330 |  |  | 26.1 | 0 | 0.26001 | 5%
1698 | New 400 kV SY Pozega | 342 | New 400 kV SY Pozega | 09-2034 | 2 | FALSE | Investment on time |  | OnshoreSubstation | SS Pozega | SS Pozega | AC | None | 0 | 400 | 0 |  |  |  | 6.4 | 0 | 0.06 | 5%
1699 | New OHL SS Jagodina 4 - SS Pozarevac 3 | 342 | New OHL SS Jagodina 4 - SS Pozarevac 3 | 09-2030 | 2 | FALSE | Delayed | Updated consideration of the necessary investments and the scope of work. | ACTransmissionLine | SS Jagodina 4 | SS Pozarevac 3 | AC | None | 77 | 400 | 0 | 2660 |  |  | 42 | 0 | 0.40001 | 5% | ++ | ++ | 0
1700 | 2x400 kV OHL SY Pozega - Vardiste | 342 | Upgrading 220 kV OHL SY Pozega - Vardiste to 2x400 kV | 09-2034 | 2 | FALSE | Investment on time |  | ACTransmissionLine | SY Pozega | Vardiste | AC | None | 50 | 400 | 0 | 1330 |  |  | 24 | 0 | 0.24 | 5% | ++ | ++ | 0
1839 | New 400 kV SS Pozarevac 3 | 342 | New 400 kV SS Pozarevac 3 | 09-2030 | 2 | FALSE | New Investment | The need for this investment came after the detailed consideration of the need for connecting SS Jagodina 4 with the Kostolac and Banat regions. | OnshoreSubstation | SS Pozarevac 3 | SS Pozarevac 3 | AC | None | 0 | 400 | 0 |  |  |  | 13 | 0 | 0.50001 | 5%
1532 | New OHL 400 kV Banja Luka - Lika | 343 | New OHL 400 kV Banja Luka - Lika | 12-2035 | 2 | FALSE | Rescheduled | This investment item is postponed due to mutual agreement | ACTransmissionLine | Banja Luka (BA) | Lika (HR) | AC | None | 180 | 400 | 0 |  |  |  | 108 | 0 | 0.108 | 15%%
1533 | New OHL 2x400 kV Lika – Melina | 343 | New OHL 2x400 kV Lika – Melina | 12-2035 | 3 | FALSE | Rescheduled |  | ACTransmissionLine | Lika (HR) | Melina (HR) | AC | None | 68 | 400 | 0 |  |  |  | 61.2 | 0 | 0.0612 | 15%%
1534 | New OHL 2x400 kV Lika – Konjsko | 343 | New OHL 2x400 kV Lika – Konjsko | 12-2034 | 3 | TRUE | Rescheduled |  | ACTransmissionLine | Lika (HR) | Konjsko (HR) | AC | None | 203 | 400 | 0 |  |  |  | 182.7 | 0 | 0.1827 | 15%%
1535 | New Substation 400/110 kV Lika | 343 | New Substation 400/110 kV Lika | 12-2034 | 3 | FALSE | Rescheduled |  | OnshoreSubstation | Lika (HR) | Lika (HR) | AC | None | 0 | 400 | 0 |  |  |  | 31.8 | 0 | 0.477 | 15%%
1846 | New OHL 2x400 kV Lika - Tumbri | 343 | New OHL 2x400 kV Lika - Tumbri | 12-2034 | 3 | FALSE | New Investment |  | ACTransmissionLine | SS Lika | SS Tumbri | AC | None | 111 | 400 | 0 |  |  |  | 102.2 | 0 | 0.1022 | 15%%
1544 | ZuidWest380 Oost | 346 | New 380 kV substation Tilburg; New 380 kV double circuit line 2645MVA between Rilland and Tilburg | 06-2029 | 3 | TRUE | Delayed | Complicated permitting procedures | ACTransmissionLine | Rilland | Tilburg | AC | None | 80 | 380 | 0 | 2630 |  |  | 1090 | 0 | 5.5 | 10%% | ++ | ++ | 0
1638 | Mares Cable : Irish Sea Interconnector Cable | 349 | HVDC 750MW 320kV symmetrical mono-pole interconnector between UKNG and EIRGRID | 12-2029 | 3 | TRUE | Rescheduled |  | DCTransmissionLine | Bodelwyddan | Maynooth | DC | Monopolar | 245 | 320 | 750 |  | VCS |  | 473.6 | 0 | 0.5 | 7.5%
1642 | MaresConnect Converter Station Ireland | 349 | 750MW 320kV VSC HVDC Convertor Station to connect to EIRGRID AC | 12-2029 | 3 | FALSE | New Investment |  | OnshoreSubstation | Maynooth | Maynooth | DC | Monopolar | 0 | 320 | 750 |  | VCS |  | 157.3 | 1.5 | 3 | 7.5%
1646 | Mares Converter Station UK | 349 | 750MW 320kV VSC HVDC Convertor Station to connect to UKNG | 12-2029 | 3 | FALSE | New Investment |  | OnshoreSubstation | Bodelwyddan | Bodelwyddan | DC | Monopolar | 0 | 320 | 750 |  | VCS |  | 157.3 | 1.5 | 3 | 7.5%
1652 | Enabling Works 1: 1 x 400kV Connection bay UKNG and associated works | 349 | AC Connection to UKNG system Bodelwyddan 400kV bays and associated works | 12-2029 | 3 | FALSE | New Investment |  | OnshoreSubstation | Bodelwyddan | Bodelwyddan | AC | None | 1 | 400 | 0 | 750 |  |  | 18.7 | 0 | 0.05 | 7.5%
1653 | Enabling Works 2: EIRGRID 1 x 245kV Connection bay at Maynooth and associated works | 349 | EIRGRID 1 x 245kV Connection bays at Maynooth and associated works | 12-2029 | 3 | FALSE | New Investment |  | OnshoreSubstation | Maynooth | Maynooth | AC | None | 1 | 245 | 0 | 750 |  |  | 18.7 | 0 | 0 | 7.5%
1622 | 400kV OHL SS Bitola - SS Elbasan | 350 | New 150km cross-border single circuit 400kV OHL between existing substation Bitola(Macedoonia) and Elbasan(Albania). | 12-2024 | 4 | TRUE | New Investment |  | ACTransmissionLine | Bitola | Elbasan | AC | None | 151 | 400 | 0 |  |  |  | 63.733 | 0 | 2.867 | ±10%
1623 | 400 kV SS Ohrid | 350 | New 400/110 kV substation in Ohrid area connected in/out to the new 400 kV line Bitola-Elbasan. This SS will contribute to the security of supply in the internal southern network of the country. | 12-2023 | 4 | FALSE | New Investment |  | OnshoreSubstation | SS Ohrid | missing value | AC | None | 0 | 400 | 0 |  |  |  | 17.68 | 0 | 1.414 | ±10%
1555 | Lienz (AT) - Veneto region (IT) | 375 | Reconstruction of the existing 220kV-interconnection line between Lienz and Veneto Region (IT) | 12-2035 | 2 | TRUE | New Investment |  | ACTransmissionLine | Lienz (AT) | Veneto region (IT) | AC | None | 140 | 220 | 0 | 900 |  |  | 300 | 0 | 0.48 | 10% | ++ | ++ | 0 | 31 | Other | - | 3 | Other | -
1559 | Refurbishment of the 400kV Meliti (GR)-Bitola (MK) interconnector | 376 | Reconductoring of the existing 400kV interconnection line Meliti (GR)-Bitola (MK) | 12-2035 | 1 | TRUE | Investment on time |  | ACTransmissionLine | Meliti (GR) | Bitola (MK) | AC | None | 35.512 | 400 | 0 | 2000 |  |  | 5.625 | 0 | 0.21488 | ±20%%
1561 | BE-NL interconnector: upgrade VanEyck-Maasbracht | 377 | Upgrade of existing interconnection between Van Eyck (BE) and Maasbracht (NL), by adding PST(s) and/or replacing existing conductors by HTLS. The study is to confirm the appropriate implementation option and phasing of this implementation also with respect to evolution of DE-NL interconnectors. | 12-2032 | 1 | TRUE | Investment on time |  | ACTransmissionLine | VanEyck | Maasbracht | AC | None | 12 | 380 | 0 | 2600 |  |  | 84 | 0 | 0.09996 | 25%% | - | - | 0
1584 | Transformer Gatica | 378 | Only 400 to 220 kV transformer. Not the whole substation | 12-2027 | 2 | TRUE | Rescheduled |  | OnshoreSubstation | GATICA 400 | GATICA 220 | AC | None | 0 | 220 | 0 | 600 |  |  | 8.16 | 0 | 0.2 | 10%%
1593 | Uprate Gatica-Guenes | 379 | Uprate 400 kV Gatica-Guenes substation | 12-2026 | 2 | TRUE | Investment on time |  | ACTransmissionLine | Gatica | Guenes | AC | None | 38.8 | 400 | 0 |  |  |  | 0.22 | 0 | 0 | 10%%
1595 | Uprate Gatica-Amorebieta-Ichaso | 379 | Uprate the 400 kV axis Gatica-Amorebieta-Ichaso | 12-2026 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Gatica | Ichaso | AC | None | 69.12 | 400 | 0 |  |  |  | 1.65 | 0 | 0 | 10%%
1597 | Uprate Gatica-Azpeitia | 379 | Uprate the 400 kV Gatica-Azpeitia line | 12-2026 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Gatica | Azpeitia | AC | None | 57 | 400 | 0 |  |  |  | 0.31 | 0 | 0.0020001 | 10%%
1692 | HVDC from Wilhelmshaven to Region Hamm | 1034 | HVDC line from Wilhelmshaven to Uentrop to integrate onshore and offshore wind energy in Northern Germany and transport it to the load centers in Western Germany | 12-2032 | 2 | TRUE | Rescheduled | expansion of the project scope because of legislative change (empty tube/ cable tube) | DCTransmissionLine | Wilhelmshaven | Region Hamm | DC | Bipolar | 270 | 525 | 2000 |  | VCS |  | 3981 | 0 | 31.848 | 10%
1693 | HVDC from Heide/West to Polsum | 1034 | HVDC line from Heide/West to Polsum to integrate onshore and offshore wind energy in Northern Germany and transport it to the load centers in Western Germany | 12-2032 | 2 | FALSE | Rescheduled | expansion of the project scope because of legislative change (empty tube/ cable tube) | DCTransmissionLine | Heide/West | Polsum | DC | Bipolar | 440 | 525 | 2000 |  | VCS |  | 5732 | 0 | 45.856 | 10%
1675 | SE North-south Long-term reinforcements | 1039 | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. The need for capacity is driven by RES integration in northern Sweden and nuclear decommission in southern Sweden. | 01-2040 | 1 | TRUE | Investment on time |  | ACTransmissionLine | SE2 | SE3 | AC | None | 475 | 400 | 0 |  |  |  | 1250 | 0 | 6.25 | +-10%% | ++ | ++ | 0
1764 | SE North-south Long-term reinforcements | 1039 | The second investment has also the same description as the first one. | 01-2040 | 1 | TRUE | Investment on time |  | ACTransmissionLine | SE2 | SE3 | AC | None | 475 | 400 | 0 |  |  |  | 1250 | 0 | 6.25 | +-10%%
1677 | LirIC | 1040 | New HVDC VSC Monopole sub sea cable between Kilroot 275kV substation in Northern Ireland (TBC) and Hunterston 400kV sub station in Scotland (TBC) | 09-2030 | 1 | TRUE | New Investment | N/A | OffshoreDCTransmissionCable | NI Kilroot 275kV (TBC) | GB Hunterston 400kV (TBC) | DC | Monopolar | 142 | 320 | 700 |  | VCS |  | 710 | 0 | 15.0002 | 20% | ++ | ++ | + (between sync areas)
1682 | Wadi El Natroon - Mesogeia / St Stefanos HVDC | 1041 | The HVDC transmission link of 3,000 MW thermal capacity, to be constructed, will consist of two (2) bi-pole systems each of 1,500 MW. Each system having converters at both ends, constitutes submarine HVDC cables from Sidi Barrani shore (Egypt) to Keratea / Kakia Thalassa (Attica, Greece) and from Sidi Barrani shore (Egypt) to Nea Makri (Attica, Greece). Supporting/complementary interconnection infrastructure at the two landing points in Egypt and Greece are also part of the GREGY project. Chapters 3 and 4 of the prefeasibility study provide the selection of technical equipment in more detail. | 06-2029 | 1 | TRUE | Rescheduled | The implementation timeline of GREGY Green Energy Interconnector has been updated by considering the ongoing execution of the final feasibility study. The final feasibility study will have been completed by May 2024. The project will be commissioned by December 2028 at the latest. This is a conservative plan, as the project promoter aims to exploit the possibility of reaching an agreement with the potential suppliers of cables and Electromechanical equipment (e.g., converters, etc.) to reduce the delivery time and hence reduce the overall time required to implement GREGY. | DCTransmissionLine | Wadi El Natroon | Mesogeia / St Stefanos | DC | Bipolar | 954 | 525 | 3000 |  | VCS |  | 3569 | 0 | 42.528 | 10% | ++ | ++ | + (between sync areas) | 83 | HabitatsDirective |  | 18.5 | HabitatsDirective |  | Following the inclusion of GREGY in PCI/PMI list (Project No 2.13), the dedicated project website (www.gregy-interconnector.gr) has been established and is being regularly updated.
1688 | Nuojuankangas-Huutokoski (Järvilinja 2) | 1046 | New single circuit 400 kV OHLs will be built from central part of Finland to the northern area to increase the capacity between North and South Finland. Enables integration of renewables to the northern part of the country. | 06-2026 | 4 | TRUE | New Investment |  | ACTransmissionLine | Nuojuankangas | Huutokoski | AC | None | 290 | 400 | 0 | 2200 |  |  | 140 | 0 | 0.15 | +- 20% | ++ | ++ | 0
1689 | Petäjäskoski-Herva-Nuojuankangas | 1046 | New single circuit 400 kV OHL will be built to the northern part of Finland. Enables the integration of renewables to the northern part of the country and the increasing power transfer from North to South . | 06-2027 | 3 | FALSE | New Investment |  | ACTransmissionLine | Petäjäskoski | Nuojuankangas | AC | None | 215 | 400 | 0 | 2200 |  |  | 80 | 0 | 0.15 | +-20% | ++ | ++ | 0
1697 | Petäjävesi/Toivila-Hikiä (2 x OHL) | 1046 | New 2 x 400 kV OHL will be built to the central part of Finland (+other required investments). Enables the integration of renewables and the utilization of full transfer capacity from North to South . | 06-2028 | 3 | FALSE | New Investment |  | ACTransmissionLine | Petäjävesi/Toivila | Hikiä | AC | None | 175 | 400 | 0 | 2200 |  |  | 90 | 0 | 0.15 | +-20% | ++ | ++ | 0
1780 | Jylkkä-Alajärvi (2 x OHL) –Toivila (1 x OHL) | 1046 | New 2 x 400 kV OHL built from Jylkkä substation (western Finland) to Alajärvi substation (central Finland) (+other required investments). The line continues as a single 400 kV OHL from Alajärvi to Toivila substation (Central Finland). Enables the integration of renewables and the utilization of full transfer capacity from North to South . | 06-2028 | 3 | FALSE | New Investment |  | ACTransmissionLine | Jylkkä | Toivila | AC | None | 300 | 400 | 0 | 2200 |  |  | 140 | 0 | 0.15 | +-20%
1781 | Nuojuankangas-Vihtavuori (Metsälinja 2) | 1046 | New single circuit 400 kV OHL will be built to the central part of Finland. Enables the integration of renewables and the utilization of full transfer capacity from North to South . | 06-2030 | 3 | FALSE | New Investment |  | ACTransmissionLine | Nuojuankangas | Petäjävesi | AC | None | 290 | 400 | 0 | 2200 |  |  | 120 | 0 | 0.15 | +-20%
1709 | Greece Africa Power Interconnector | 1048 | 2 HVDC Subsea cables interconnecting the Northern coast of Egypt with the island of Crete at Atherinolakkos. At both connection points bipolar HVDC conversion stations will be constructed. | 08-2030 | 1 | TRUE | Rescheduled |  | OffshoreDCTransmissionCable | Atherinolakkos (Crete) | Mersa Matruh (Egypt) | DC | Bipolar | 450 | 600 | 600 |  | VCS |  | 650 | 3 | 4.9998 | 5%% | ++ | ++ | + (between sync areas) |  |  |  |  | None
1706 | Converter Stations & Subsea Cabling | 1049 | 1.4 GW HVDC electricity interconnector between UK and Belgium Voltage Source Converter (VSC)/Bipolar Grid connection point (substations name): Kemsley (UK) and in Belgium the exact substation location will be determined by the main grid study to be completed by Elia. Total cable length (substation to substation) 202km. Two cables (XLPE) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load. The annual Availability is 98.1% availability, with 1.8% planned outages, and 0.1% forced outages. The maximum single failure according to the design is 1.4GW. The project will enable the reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. There are no material anticipated environmental impacts during construction and operation. | 12-2031 | 1 | TRUE | New Investment | N/A | OffshoreDCTransmissionCable | Kemsley, Kent | Most appropriate connection site under study | DC | Bipolar | 202 | 525 | 1400 |  | VCS |  | 937 | 65 | 34.9998 | 10%% | ++ | ++ | + (between sync areas) | 1 1 | RAMSARSite HabitatsDirective |  |  |  |  | No other residual impact
1707 | Converter stations and Subsea Cabling | 1050 | 1.4 GW HVDC electricity interconnector between UK and Germany Voltage Source Converter (VSC)/Bipolar Grid connection point (substations name): East Anglia Connection Node (UK) and Niederlangen (Germany), exact substation location subject to grid study in Germany. Total cable length (substation to substation) 610km. Two cables (XLPE) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load. The annual Availability is 98.1% availability, with 1.8% planned outages, and 0.1% forced outages. The maximum single failure according to the design is 1.4GW. The project will enable the reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. There are no material anticipated environmental impacts during construction and operation | 10-2030 | 1 | TRUE | New Investment | N/A | OffshoreDCTransmissionCable | East Anglia, connection node 400kV Substation | Niederlangen, Germany | DC | Bipolar | 610 | 525 | 1400 |  | VCS |  | 1675 | 65 | 37.0007 | 10%% |  |  |  | 9 12 | HabitatsDirective MarinStrategyFrameworkDirective |  |  |  |  | No other residual impact
1713 | Lienz (AT) - Malta (AT) - Obersielach (AT) | 1052 | 380 kV New | 06-2033 | 2 | TRUE | Rescheduled | Revision of the grid expansion concept. Cascade effects due to project delays in projects ranked ahead. | ACTransmissionLine | Lienz (AT) | Obersielach (AT) | AC | None | 202 | 380 | 0 | 5543 |  |  | 3152 | 0 | 1.1915 | 10% |  |  |  | 4 | None |  | 81 | None
1715 | 220-kV Westtirol (AT) - Zell/Ziller (AT) | 1054 | Upgrade of the existing 220kV-line Westtirol - Zell-Ziller and erection of an additional 220/380kV-Transformer. Line length 104km. | 12-2030 | 2 | TRUE | Rescheduled | Revision of the expansion concept. Cascade effects due to project delays in projects ranked ahead. | ACTransmissionLine | Westtirol (AT) | Zell-Ziller (AT) | AC | None | 104 | 220 | 0 | 2564 |  |  | 74 | 0 | 0.26004 | 10% |  |  |  | 11 | None |  | 74 | None
1716 | Interconnection between Crete and Peloponnese (Phase I) | 1055 | New 150 kV AC double circuit submarine and underground cables between Crete and Peloponnese | 05-2021 | 5 | FALSE | Investment on time |  | ACTransmissionLine | Chania I | Molai (through Sklavouna Terminal) | AC | None | 179 | 150 | 0 | 2 x 200 |  |  | 376 | 0 | 1.2 | 9% | ++ | ++ | 0 | 25 11 2 | HabitatsDirective BirdsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 9.63 | HabitatsDirective
1717 | Interconnection between Crete and Attica (Phase II) | 1055 | New symmetric bipolar submarine HVDC-VSC link between Crete and Attica | 09-2024 | 4 | TRUE | Investment on time |  | DCTransmissionLine | Damasta | Koumoundouros | DC | Bipolar | 373 | 500 | 1000 |  | VCS |  | 1162 | 0 | 1.5 | 9% | ++ | ++ | + (between sync areas) | 5.2 4.48 | HabitatsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 14.9 | HabitatsDirective
1726 | HVDC Line DE-CH | 1058 | The concept of extending German HVDC-Lines towards Switzerland and Italy offers a further potential to realize a new North-South HVDC corridor. Large developments of variable wind and photovoltaic power, coal and nuclear phaseout, mainly gas-based thermal generation, and the pump storage potentials in the Alps are the main drivers of power system evolution that will challenge the future transmission system in central southern Europe. | 12-2037 | 1 | TRUE | Investment on time |  | DCTransmissionLine | Oberjettingen (DE) | Mettlen (CH) | DC | Bipolar | 214 | 525 | 1000 |  | VCS |  | 1096 | 0 | 8.7998 | ±20%% |  |  |  | 0 | Other |  | 0 | Other
645 | OHL between the Laino and Altomonte in Calabria | 1059 | New 400kV OHL between the existing substations of Laino and Altomonte in Calabria. | 12-2029 | 3 | FALSE | Rescheduled |  | ACTransmissionLine | Laino (IT) | Altomonte (IT) | AC | None | 50 | 400 | 0 | 2076 |  |  | 203 | 0 | 0.9 | 0% | ++ | ++ | 0 | 9 | Other |  | 1 | Other
1727 | Montecorvino-Avellino and Nord-Ben. in Campania | 1059 | New 400 kV between Montecorvino-Avellino and Nord-Ben. in Campania | 12-2029 | 3 | TRUE | New Investment |  | ACTransmissionLine | Montecorvino (IT) | Benevento (IT) | AC | None | 0 | 400 | 0 | 1870 |  |  | 319 | 0 | 0.3 | 0% | ++ | ++ | 0 | 24 | Other |  | 5 | Other
1736 | 400kV OHL, Maritsa East 2 (BG) – Vize Havza (TR) | 1066 | New interconnection line BG-TR by a 150km single circuit 400kV OHL. | 11-2035 | 1 | TRUE | New Investment |  | ACTransmissionLine | Maritsa East 2 (BG) | Vize Havza (TR) | AC | None | 150 | 400 | 0 |  |  |  | 74.4 | 0 | 1.9865 | +-10%%
1738 | New AC 400 kV interconnection line Greece - Turkey | 1067 | New AC 400 kV Overhead line Greece - Turkey | 06-2031 | 2 | TRUE | Ahead of time |  | ACTransmissionLine | Nea Santa (GR) | Babaeski (TR) | AC | None | 130 | 400 | 0 | 2000 |  |  | 53 | 0 | 1.3 | ± 20%% | ++ | ++ | 0
1787 | New 400 kV OHL Nea Santa - Filippi | 1067 | New AC 400 kV double circuit OHL Nea Santa - Filippi | 06-2028 | 2 | FALSE | Rescheduled |  | ACTransmissionLine | Nea Santa | Fillipi | AC | None | 140 | 400 | 0 | 2 x 1400 |  |  | 49 | 0 | 0.4998 | ± 20%% | ++ | ++ | 0
1740 | LaSGo Link - Gotland to Latvia | 1068 | New monopolar HVDC VSC monopole sub-sea cable running from a new substation in Gotland (TBC) to Grobina in Latvia (or Ventspils or a possible a new substation inbetween Grobina and Ventspils) (TBC). This investment consists of two VSC HVDC converter stations connected via two 320kV HVDC XLPE cables. | 07-2037 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | New substation on Gotland (TBC) | Grobina (TBC) | DC | Monopolar | 195 | 320 | 500 |  | VCS |  | 511.5 | 0 | 7.9999 | +/-15%% | ++ | ++ | + (between sync areas)
1741 | LaSGo Link - Sweden to Gotland | 1068 | New monopolar HVDC VSC monopole sub-sea cable running from the vicinity of Oskarshamn in mainland Sweden (TBC) to a new substation in Gotland (TBC). This investment consists of one HVDC VSC converter station connected via two 320kV HVDC XLPE cables to a Converter Station being built as part of the LaSGo Link Gotland to Latvia investment. | 07-2037 | 1 | FALSE | New Investment |  | OffshoreDCTransmissionCable | Oskarshamn (TBC) | New substation on Gotland (TBC) | DC | Monopolar | 125 | 320 | 700 |  | VCS |  | 287.5 | 0 | 4 | +/-15%% | ++ | ++ | + (between sync areas)
1742 | 400 kV OHL SS Subotica 3 – SS Sándorfalva | 1074 | New 400 kV interconnection OHL between SS Subotica (RS) and SS Sándorfalva (HU). This is the main investment of the project and a part of the new North-South corridor for energy transmission. | 09-2028 | 2 | TRUE | Ahead of time | No delay on this investment yet. | ACTransmissionLine | SS Subotica 3 | SS Sándorfalva | AC | None | 50.6 | 400 | 0 | 1330 |  |  | 24.1 | 0 | 0.24001 | 10% | ++ | ++ | 0
1743 | 400 kV OHL SS Novi Sad 3 – SS Sombor 3 | 1074 | New 400 kV OHL from existing substation Novi Sad 3 to existing substation Sombor 3 (both in Serbia). | 09-2030 | 2 | FALSE | Ahead of time | No delay on this investment yet. | ACTransmissionLine | SS Sombor 3 | SS Novi Sad 3 | AC | None | 80 | 400 | 0 | 1330 |  |  | 35.5 | 0 | 0.40001 | 5% | ++ | ++ | 0
1744 | 2x400 kV OHL SS Belgrade 50 – SS Sremska Mitrovica 2 | 1074 | New 400 kV OHL from future substation Srbobran to existing substation Sremska Mitrovica 2 (both in Serbia). | 09-2030 | 2 | FALSE | Ahead of time | No delay on this investment yet. | ACTransmissionLine | SS Belgrade 50 | SS Sremska Mitrovica 2 | AC | None | 60 | 400 | 0 | 1330 |  |  | 27.5 | 0 | 0.28001 | 5% | ++ | ++ | 0
1840 | Reconstruction of SS Subotica 3 | 1074 | Reconstruction of SS Subotica 3 in the Serbian system. | 09-2030 | 2 | FALSE | New Investment | No delay yet. | OnshoreSubstation | SS Subotica 3 | SS Subotica 3 | AC | None | 0 | 400 | 0 |  |  |  | 33 | 0 | 0.3 | 5%
1751 | Malta-Italy Cable link No. 2 | 1085 | 200MWe HVAC 2nd electrical cable link between Malta and Sicily | 12-2026 | 3 | TRUE | Delayed | The permitting process is taking longer than anticipated. | OffshoreACTransmissionCable | In Malta (MT): Maghtab Terminal Station (Maghtab TS) | In Italy (IT): Ragusa Terminal Station (Ragusa TS) | AC | None | 122 | 220 | 0 | 250 |  |  | 285.5 | 0.75 | 6.4 | 20% | ++ | ++ | 0
1752 | L356 Mustvee-Paide 330 kV OHL reconstrucion (EE) | 1086 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. To reduce the environmental impact partially the parallel 110 kV lines will be place on the common towers with 330 kV reconstructed line. The thermal transmission capacity of the line is planned 1770 MW. | 06-2026 | 4 | TRUE | New Investment |  | ACTransmissionLine | Mustvee | Paide | AC | None | 87 | 330 | 0 | 1770 |  |  | 38 | 38 | 0.19 | 10% | ++ | ++ | 0 | 0.8 | HabitatsDirective |  | 1.03 | HabitatsDirective
1753 | L357 Kiisa-Paide 330 kV OHL reconstruction (EE) | 1086 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. To reduce the environmental impact partially the parallel 110 kV lines will be place on the common towers with 330 kV reconstructed line. The thermal transmission capacity of the line is planned 1770 MW. | 06-2026 | 4 | FALSE | New Investment |  | ACTransmissionLine | Kiisa | Paide | AC | None | 70 | 330 | 0 | 1770 |  |  | 25 | 25 | 0.13 | 10% | ++ | ++ | 0 | 3.3 | OtherNatureProtectionAreasUnderNationalLaw |  | 1.95 | HabitatsDirective
1754 | Lihula 330 KV substation (EE) and reinforcement of internal grid in western part of Estonia | 1086 | New Lihula 330 kV substation will be connected to existing Harku-Sindi 330 kV OHL in Lihula. It consists of 2 330 kV duplex bays for 330 kV lines, and 3 simplex 330 kV bays of which 2 will be used for power transformers (200 MVA each) and one for reactive power compensator (125 Mvar). The investment also includes the reinforcement of internal 110 kV grid where are the potential RES connection points. | 06-2026 | 4 | FALSE | New Investment |  | OnshoreSubstation | Lihula | Lihula | AC | None | 0 | 330 | 0 |  |  |  | 57 | 57 | 0.29 | 10%
1755 | The interconnector between Latvia and Estonia with Off-shore wind connection hub in between | 1088 | The planned subsea interconnection between Estonia and Latvia with off-shore connection hub in between. The connection of off-shore wind up to 1000 MW. | 12-2035 | 1 | TRUE | Investment on time |  | OffshoreACTransmissionCable | Pavilosta (LV) | Saaremaa-Hub (EE) | AC | Bipolar | 150 | 220 | 1000 | 1200 | VCS |  | 500 | 0 | 0.2 | 20% | ++ | ++ | + (between sync areas)
1758 | Internal network reinforcement Pavilosta (LV) - Broceni (LV) | 1088 | New 330 kV OHL for internal network strengthening in Latvia | 12-2035 | 1 | FALSE | New Investment |  | ACTransmissionLine | Pavilosta (LV) | Broceni (LV) | AC | None | 95 | 330 | 0 | 1156 |  |  | 45 | 0 | 0.45 | +5%; -5%% | ++ | ++ | 0
1761 | Off-shore substation for off-shore wind park connection - Latvia | 1088 | The planned off-shore substation in Baltic Sea near Western part of Latvia for offshore wind connection. The exact location of the substation will be determined by ongoing studies. | 12-2035 | 1 | FALSE | Investment on time |  | OffshoreSubstation | ELWIND off-shore substation | ELWIND off-shore substation | AC | Bipolar | 0 | 220 | 1000 | 0 | VCS |  | 155 | 0 | 1.4999 | 20% | ++ | ++ | + (between sync areas)
1886 | Internal new 330 kV connection between Lihula substation (EE) and Saaremaa hub (EE) | 1088 | 330 kV OHLs and cable lines, new 330 kV substations | 12-2035 | 1 | FALSE | New Investment |  | ACTransmissionLine | Lihula | western Saaremaa off-shore hub | AC | None | 160 | 330 | 0 | 1400 |  |  | 370 | 0 | 0.49987 | 30%
1887 | Internal new 330 kV OHL between Lihula (EE) and Paide (EE) | 1088 | New overhead power line between Lihula and Paide 330 kV substations. | 12-2035 | 1 | FALSE | New Investment |  | ACTransmissionLine | Lihula | Paide | AC | None | 90 | 330 | 0 | 1770 |  |  | 45 | 0 | 0.23 | 20%
1966 | Offshore platform with reactive power compensation equipment | 1088 | The 4th Latvia and Estonia interconnection is a long subsea cable which request additional reactive power compensation equipment in between. It is planned to install additional offshore platform with shunt reactors for reactive power compensation. | 12-2035 | 1 | FALSE | New Investment |  | ReactiveCompensationDevice | Platform with equipment for reactive power compensation | Platform with equipment for reactive power compensation | AC | None | 0 | 220 | 0 | 0 |  | 1215 | 70 | 0 | 0.7 | 10%
1976 | Construction of new substation in Pavilosta (LV) | 1088 | The construction of new 330 kV substation in Pavilosta to connect Estonia and Latvia 4th interconnector | 12-2035 | 1 | FALSE | New Investment |  | OnshoreSubstation | Pavilosta (LV) | Pavilosta (LV) | AC | None | 0 | 330 | 0 | 0 |  |  | 20 | 0 | 0.2 | 5%
1978 | Reconstruction of OHL Pavilosta (LV) - Grobina (LV) | 1088 | The reconstruction of existing OHL to increase the capacity for cross-border exchange and offshore wind production between Estonia and Latvia | 12-2035 | 1 | FALSE | New Investment |  | ACTransmissionLine | Pavilosta (LV) | Grobina (LV) | AC | None | 40 | 330 | 0 | 1156 |  |  | 20 | 0 | 0.2 | 3%
1759 | Connection between Belgium and the Danish Energy Island | 1092 | Hybrid HVDC interconnector | 12-2032 | 2 | TRUE | Rescheduled | Revision of Danish Energy Island concept | OffshoreDCTransmissionCable | Baekeland | Substation on Danish Energy Island | DC | Bipolar | 773 | 1050 | 2000 |  | VCS |  | 6286 | 0 | 62.86 | 27% | ++ | ++ | + (between sync areas)
1777 | Connection between Denmark and the Danish Energy Island | 1092 | Hybrid HVDC interconnector | 12-2032 | 2 | FALSE | Rescheduled | Revision of Danish Energy Island concept | OffshoreDCTransmissionCable | Danish Energy Island | Revsing | DC | Bipolar | 215 | 1050 | 2000 |  | VCS |  | 3806 | 0 | 38.06 | 27% | ++ | ++ | + (between sync areas)
1760 | Estlink 3 | 1094 | HVDC subsea connection between FI and EE, including converter stations | 06-2035 | 2 | TRUE | New Investment |  | OffshoreDCTransmissionCable | FI | EE | DC | None | 120 | 450 | 700 |  | VCS |  | 800 | 0 | 0.7504 | 20% | ++ | ++ | + (between sync areas)
1769 | Estonian grid reinforcements: L346 Paide-Sopi 330 kV OHL reconstruction | 1094 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. The thermal transmission capacity of the line is planned 1772 MW. | 12-2028 | 2 | FALSE | New Investment |  | ACTransmissionLine | Paide | Sopi | AC | None | 66.3 | 330 | 0 | 1770 |  |  | 36 | 0 | 0.13 | 10% | ++ | ++ | 0
1770 | Estonian grid reinforcements: L347 Sopi-Sindi 330 kV OHL reconstruction | 1094 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. The thermal transmission capacity of the line is planned 1772 MW. | 12-2028 | 2 | FALSE | New Investment |  | ACTransmissionLine | Sopi | Sindi | AC | None | 28.7 | 330 | 0 | 1770 |  |  | 9 | 0 | 0.039996 | 10% | ++ | ++ | 0
1771 | Estonian grid reinforcements: L506 Rakvere-Kiisa 330 kV OHL reconstruction | 1094 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. The thermal transmission capacity of the line is planned 1772 MW. | 12-2029 | 2 | FALSE | New Investment |  | ACTransmissionLine | Rakvere | Kiisa | AC | None | 107.8 | 330 | 0 | 1770 |  |  | 49 | 0 | 0.24 | 10% | ++ | ++ | 0
1774 | Estonian grid reinforcements: L360 Püssi-Rakvere 330 kV OHL reconstruction | 1094 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. The thermal transmission capacity of the line is planned 1772 MW. | 12-2030 | 2 | FALSE | New Investment |  | ACTransmissionLine | Püssi | Rakvere | AC | None | 57.7 | 330 | 0 | 1770 |  |  | 39 | 0 | 0.12999 | 10% | ++ | ++ | 0
1775 | Estonian grid reinforcements: Kiisa-Aruküla 330 kV new OHL | 1094 | New 330 kV overhead powerline and new 330 kV substation between Kiisa and Aruküla 330 kV substations, | 06-2035 | 2 | FALSE | New Investment |  | ACTransmissionLine | Aruküla | Kiisa | AC | None | 41 | 330 | 0 | 1770 |  |  | 53 | 0 | 0.26998 | 10% | ++ | ++ | 0
1785 | Inkoo-Hikiä | 1094 | Inkoo-Hikiä 400 kV single circuit OHL | 06-2031 | 2 | FALSE | New Investment |  | ACTransmissionLine | Inkoo (FI) | Hikiä (FI) | AC | None | 100 | 400 | 0 | 2200 |  |  | 40 | 0 | 0.2 | +-20% | ++ | ++ | 0
1979 | Estonian grid reinforcements: New 330 kV substation for converter station connection | 1094 | New 330 kV substation and two 330kV overhead powerlines to connect Estlink 3 to Estonian transmission grid. | 06-2035 | 2 | FALSE | New Investment |  | OnshoreSubstation | Aulepa | Aulepa | AC | None | 0 | 330 | 0 | 0 |  |  | 40 | 0 | 0.2 | 10%
1762 | 4th AC Finland-Sweden north | 1095 | Fourth AC 400 kV overhead line interconnector between Finland north and Sweden SE1. | 06-2032 | 2 | TRUE | New Investment |  | ACTransmissionLine | FI | SE1 | AC | None | 250 | 400 | 0 | 2200 |  |  | 270 | 0 | 0.81 | +-20%% | ++ | ++ | 0
1763 | Beznau - Mettlen | 1096 | line | 12-2031 | 3 | TRUE | Delayed | permitting procedure | ACTransmissionLine | Beznau | Mettlen | AC | None | 1 | 380 | 0 | 1580 |  |  | 102.25 | 0 | 0.51 | 10% | ++ | ++ | 0 | 0 | Other |  | 47 | Other
1847 | Transformers Mettlen | 1096 | Transformers | 12-2026 | 4 | FALSE | New Investment |  | Transformer | Mettlen 380 kV | Mettlen 220 kV | AC | None | 1 | 380 | 0 | 1600 |  |  | 83.24 | 0 | 0.42 | 10% |  |  |  | 0 | Other |  | 0 | Other
1942 | Transformer Lachmatt | 1096 | Transformer | 12-2026 | 4 | FALSE | New Investment |  | Transformer | Lachmatt 380 kV | Lachmatt 220 kV | AC | None | 1 | 380 | 0 | 400 |  |  | 41.45 | 0 | 0.21 | 10% |  |  |  | 0 | Other None |  | 0 | Other
1765 | Upgrade to Konti-Skan | 1097 | This project will increase the capacity on the existing HVDC connections Konti-Skan 1 and 2 connecting SE3 and DK1 by 700 MW, resulting in a total of 1400 MW capacity between SE3 and DK1. | 01-2032 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | SE4 (Substation is not decided yet) | DK1 (Substation is not decided yet) | DC | None | 160 | 525 | 700 |  | VCS |  | 850 | 0 | 8.5 | +-20%% | ++ | ++ | + (between sync areas)
1778 | Extension of Darbenai substation | 1098 | Extension of Darbenai substation to connect offshore wind farm. | 12-2030 | 2 | TRUE | New Investment |  | OnshoreSubstation | Darbenai | - | AC | None | 0 | 330 | 0 |  |  |  | 20 | 0 | 0.2 | +10%, -10%% | ++ | ++ | 0
1766 | Modernization of existing interconnector Hradec - Röhrsdorf | 1100 | The project consists in the modernization of an existing 400 kV line between the Hradec and Röhrsdorf substations. | 08-2028 | 3 | TRUE | New Investment |  | ACTransmissionLine | Hradec | Röhrsdorf | AC | None | 81.5 | 400 | 0 | 1694 |  |  | 49.841 | 0 | 0.01 | -10%, +15%% | ++ | ++ | 0 | 13 7.5 | BirdsDirective HabitatsDirective |  | 3 | IUCNKeyBiodiversityAreas
1767 | Mettlen - Ulrichen | 1102 | AC Line | 12-2034 | 3 | TRUE | Ahead of time |  | ACTransmissionLine | Mettlen | Ulrichen | AC | None | 1 | 220 | 0 | 1120 |  |  | 471.96 | 0 | 2.36 | 10% | ++ | ++ | 0 | 0 | Other |  | 34 | Other
1768 | Bickigen - Chippis | 1103 | line | 12-2027 | 3 | TRUE | Ahead of time |  | ACTransmissionLine | Bickigen | Chippis | AC | None | 1 | 380 | 0 | 1580 |  |  | 57.01 | 0 | 0.29 | 10% | ++ | ++ | 0 | 0 | Other |  | 0 | Other
1772 | Roost - Flebour - Border Luxemburg | 1104 | Upgrade of existing transmission OHL between Roost and Border Luxembourg to increase the thermal cross-border capacity. | 12-2022 | 5 | TRUE | New Investment |  | ACTransmissionLine | Bauler (DE) | Roost (LU) | AC | None | 27.8 | 220 | 0 |  |  |  | 14.79 | 0 | 0.118 | 10%% | ++ | ++ | 0
1773 | Bauler - German Border | 1104 | Upgrade of existing transmission OHL between Station Bauler and Border to Luxembourg to increase the thermal capacity by using High Temperature Low Sag (HTLS) conductors | 12-2025 | 2 | FALSE | New Investment |  | ACTransmissionLine | German Border | Bauler (DE) | AC | None | 20.3 | 220 | 0 |  |  |  | 4 | 0 | 0.016 | 10% | ++ | ++ | 0
1782 | Black Sea HVDC submarine interconnection project | 1105 | Submarine cable Anaklia-Constanta Sud which will be placed under Black Sea DC 2-circuit ±500 kV cable, route distance – 1155KM | 12-2031 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | SS Anaklia | SS Constanta Sud | DC | Bipolar | 1155 | 500 | 1000 |  | VCS |  | 3571.5 | 0 | 27.1434 | 5% | ++ | ++ | + (between sync areas)
1793 | Bornholm Energy Island: BEI-DKE | 1106 | DC connection from mainland Zealand (Solhøjgård, DKE) to Bornholm including converters on Zealand and on Bornholm, as well as AC and MTDC components on the island of Bornholm | 12-2029 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Solhøjgård (DKE) | Bornholm Energy Island (BEI) | DC | None | 229 | 525 | 1200 |  | VCS |  | 988 | 0 | 5.434 | +-20% | ++ | ++ | + (between sync areas)
1794 | Bornholm Energy Island: BEI-DE | 1106 | DC connection from mainland Germany (area of Brünzow/Kemnitz) to Bornholm including converters in Stilow and on Bornholm, as well as AC and MTDC components on the island of Bornholm | 12-2030 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Stilow (DE) | Bornholm Energy Island (BEI) | DC | None | 193 | 525 | 2000 |  | VCS |  | 1091 | 0 | 8.728 | +-20% | ++ | ++ | + (between sync areas)
1796 | New 400 kV overhead line between Aliano and Montecorvino | 1109 | New 400 kV overhead line between Aliano and Montecorvino | 12-2032 | 2 | TRUE | New Investment |  | ACTransmissionLine | Aliano | Montecorvino | AC | None | 116 | 400 | 0 | 1870 |  |  | 274 | 0 | 0.4932 | 0% | ++ | ++ | 0 | 61 | Other |  | 1 | Other
1797 | New 400 kV overhead line in the northern area of Benevento | 1109 | New 400 kV overhead line in the northern area of Benevento | 12-2035 | 2 | FALSE | New Investment |  | ACTransmissionLine | Benevento | New Substation | AC | None | 42 | 400 | 0 | 1870 |  |  | 60 | 0 | 0.198 | 0% | ++ | ++ | 0 | 25 | Other |  | 1 | Other
1798 | New 400 kV submarine cable Bolano-Annunziata | 1110 | New 400 kV submarine cable Bolano-Annunziata | 12-2026 | 3 | TRUE | New Investment |  | ACTransmissionLine | Bolano | Annunziata | AC | None | 9 | 400 | 0 | 1040 |  |  | 226 | 0 | 0.4 | 0% | ++ | ++ | 0 | 2 | Other |  | 2 | Other
1799 | GRITA 2 | 1112 | New HVDC link between Italy (Galatina) and Greece (Thesprotia) with an NTC increase of 1000 MW | 12-2031 | 2 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Galatina (IT) | Thesprotia (GR) | DC | Bipolar | 275 | 400 | 1000 |  | VCS |  | 1250 | 0 | 3 | 10% | ++ | ++ | + (between sync areas) | 2 | Other | - | 2 | Other | -
1805 | 220-kV Hessenberg (AT) - Weißenbach (AT) | 1121 | Reinforcement/Upgrade 220-kV Overheadline | 12-2030 | 2 | TRUE | New Investment |  | ACTransmissionLine | Hessenberg (AT) | Weißenbach (AT) | AC | None | 71 | 220 | 0 | 1872 |  |  | 158 | 0 | 0.17996 | 10% | ++ | ++ | 0
1810 | CM1 Offshore wind farm HVDC grid connection | 1122 | HVDC offshore platform with converter station + onshore converter station + HVDC onshore & offshore cables+ onshore AC transmission cable | 03-2032 | 2 | TRUE | Investment on time |  | DCTransmissionLine | Centre Manche 1 | Menuel | DC | Monopolar | 100 | 320 | 1250 |  | VCS |  | 2700 | 0 | 18.9999 | 40% | ++ | ++ | + (between sync areas) | 6 6 6 | OtherNatureProtectionAreasUnderNationalLaw BirdsDirective OtherNatureProtectionAreasUnderNationalLaw
1811 | Offshore Wind Connection Centre Manche 2 | 1123 | HVDC offshore platform with converter station + onshore converter station + HVDC onshore & offshore cables+ offshore AC transmission cable | 09-2032 | 2 | TRUE | Investment on time |  | OffshoreSubstation | Centre Manche 2 | Tourbe | DC | Monopolar | 100 | 320 | 1250 |  | VCS |  | 2450 | 0 | 17.0006 | 40% | ++ | ++ | + (between sync areas)
1812 | Offshore Wind Connection South Britanny | 1124 | HVAC offshore platform + onshore and offshore cables + onshore substation | 09-2030 | 2 | TRUE | Investment on time |  | OffshoreACTransmissionCable | Bretagne Sud | Pluvigner | AC | None | 80 | 225 | 0 | TBD |  |  | 1520 | 0 | 11.0002 | 40% | ++ | ++ | 0
1808 | AO6 Occitanie | 1125 | HVAC 225 kV offshore platform + onshore and offshore cables + onshore substation | 03-2031 | 2 | TRUE | Investment on time |  | OffshoreACTransmissionCable | OSS TRAMONTANE | Liviere | AC | None | 60 | 225 | 0 |  |  |  | 1290 | 0 | 9.0003 | 50%
1809 | AO6 Occitanie | 1126 | HVAC 225 kV offshore platform + onshore and offshore cables + onshore substation | 12-2031 | 2 | TRUE | Investment on time |  | OffshoreACTransmissionCable | OSS MISTRAL | Lavera | AC | None | 60 | 225 | 0 |  |  |  | 1300 | 0 | 8.9999 | 50% | ++ | ++ | 0
1813 | HVDC converter stations and cables (substations) | 1127 | HVDC offshore platform, onshore converter station, hvdc cables | 03-2032 | 2 | TRUE | Investment on time |  | OffshoreSubstation | Oléron 1 substation | Grandzay | DC | None | 140 | 320 | 0 |  | VCS |  | 2700 | 0 | 18.9999 | 40% | ++ | ++ | + (between sync areas)
1838 | GiLA 1st circuit | 1134 | 2 x 1200 MW HVDC 320 kV links including onshore and offshore cables +¨onshore converter stations | 12-2033 | 1 | TRUE | New Investment |  | DCTransmissionLine | Bordeaux area | Nantes area | DC | Monopolar | 400 | 320 | 1200 |  | VCS |  | 875 | 0 | 6.1434 | 50%
2023 | GiLA 2nd circuit | 1134 | One 1200 MW HVDC 320 kV link including onshore and offshore cables +¨onshore converter stations | 12-2034 | 1 | FALSE | New Investment |  | DCTransmissionLine | Bordeaux area | Nantes area | DC | None | 1 | 320 | 1200 |  | VCS |  | 875 | 1 | 6.076 | 1%
1860 | 400kV OHL Suceava-Balti | 1138 | New 400kV interconnection OHL aims to enhance the transmission capacity along the East-West corridor in the South-Eastern and Central Europe, remove bottlenecks and integrate RES to the network. | 12-2030 | 3 | TRUE | New Investment |  | ACTransmissionLine | Suceava | Balti | AC | None | 148 | 400 | 0 | 1741 |  |  | 97.8 | 0.89 | 4.89 | 5%
1861 | 400/330 kV substation Balti | 1138 | new transformer 400/330kV in Balti (Republic of Moldova) substation | 12-2030 | 2 | FALSE | New Investment |  | OnshoreSubstation | Balti (RM) 400kV | Balti (RM) 330kV | AC | None | 0 | 0 | 0 |  |  |  | 20 | 0 | 0.2 | 5%
1983 | 400kV OHL Suceava (RO) - Gadalin (RO) | 1138 | A new 400kV OHL that helps the transit of electricity in the east-west direction in Romania up to the border of the Republic of Moldova | 12-2030 | 2 | FALSE | New Investment |  | ACTransmissionLine | 400kV Suceava (RO) | 400kV Gadalin (RO) | AC | None | 258.8 | 400 | 0 | 1741 |  |  | 178.37 | 1.55 | 0.89185 | 5%
1854 | 380-kV Westtirol (AT) – Zell/Ziller (AT) | 1139 | 380-kV OHL | 12-2037 | 1 | TRUE | New Investment |  | ACTransmissionLine | Westtirol (AT) | Zell/Ziller (AT) | AC | None | 125 | 380 | 0 | 5543 |  |  | 3826 | 0 | 0.71929 | 10%
1855 | 380-kV St. Peter (AT) - Dürnrohr (AT) | 1140 | 380-kV OHL | 12-2037 | 1 | TRUE | New Investment |  | ACTransmissionLine | St. Peter (AT) | Dürnrohr (AT) | AC | None | 276 | 380 | 0 | 5543 |  |  | 2531 | 0 | 1.2402 | 10%
1844 | 380-kV Obersielach (AT) - Hessenberg (AT) | 1145 | Integration of large amounts of RES in the federted states of Styria and Carinthia. | 12-2035 | 1 | TRUE | New Investment |  | ACTransmissionLine | Obersielach (AT) | Hessenberg (AT) | AC | None | 119 | 380 | 0 | 5543 |  |  | 1175 | 0 | 0.56988 | 10%
1856 | PST romands - Riddes (220 kV/220 kV) | 1153 | PST on line Cornier - Riddes in the Riddes substation | 12-2030 | 1 | FALSE | New Investment |  | PhaseShiftingTransformer | Riddes 220 kV | Riddes 220 kV | AC | None | 1 | 220 | 0 | 450 |  |  | 18.75 | 0 | 0.09375 | 10% |  |  |  | 0 | Other None |  | 0 | Other
1857 | PST romands - Châtelard (380 kV/220 kV) | 1153 | substituted PST transformer in the Châtelard substation | 12-2030 | 1 | FALSE | New Investment |  | PhaseShiftingTransformer | Châtelard 380 kV | Châtelard 220 kV | AC | None | 1 | 380 | 0 | 450 |  |  | 42.92 | 0 | 0.2146 | 10% |  |  |  | 0 | Other None |  | 0 | Other
1858 | PST romands - St Triphon (220 kV/220 kV) | 1153 | PST on line Cornier - St. Triphon in the St Triphon substation | 12-2030 | 1 | FALSE | New Investment |  | PhaseShiftingTransformer | St Triphon 220 kV | St Triphon 220 kV | AC | None | 1 | 220 | 0 | 450 |  |  | 28.75 | 0 | 0.14375 | 10% |  |  |  | 0 | Other |  | 0 | Other
1859 | PST romands - Verbois (380 kV/220 kV) | 1153 | new PST transformer in the Verbois substation | 12-2030 | 1 | TRUE | New Investment |  | PhaseShiftingTransformer | Verbois 380 kV | Verbois 220 kV | AC | None | 1 | 380 | 0 | 800 |  |  | 50.88 | 0 | 0.2544 | 10% |  |  |  | 0 | Other |  | 0 | Other
1955 | PST romands - Verbois (220 kV/220 kV #1) | 1153 | PST on line Génissiat - Verbois #1 in the Verbois substation | 12-2030 | 1 | FALSE | New Investment |  | PhaseShiftingTransformer | Verbois 220 kV | Verbois 220 kV | AC | None | 1 | 220 | 0 | 600 |  |  | 37.79 | 0 | 0.18895 | 10% |  |  |  | 0 | Other |  | 0 | Other
1956 | PST romands - Verbois (220 kV/220 kV #2) | 1153 | PST on line Génissiat - Verbois #2 in the Verbois substation | 12-2030 | 1 | FALSE | New Investment |  | PhaseShiftingTransformer | Verbois 220 kV | Verbois 220 kV | AC | None | 1 | 220 | 0 | 600 |  |  | 37.79 | 0 | 0.18895 | 10% |  |  |  | 0 | Other |  | 0 | Other
1862 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT) | 1155 | Integration of large amounts of industry and RES in the federal states of Lower Austria and Vienna. | 12-2032 | 2 | TRUE | New Investment |  | ACTransmissionLine | Burgenland North (AT) | Greater Vienna (AT) | AC | None | 62 | 380 | 0 | 5543 |  |  | 777 | 0 | 0.35975 | 10%
1863 | 380-kV Greater Vienna (AT) - Hessenberg (AT) | 1156 | Integration of large amounts of industry and RES in the federal states of Styria, Lower Austria and Vienna. | 12-2033 | 2 | TRUE | New Investment |  | ACTransmissionLine | Hessenberg (AT) | Greater Vienna (AT | AC | None | 176 | 380 | 0 | 5543 |  |  | 1629 | 0 | 1.3993 | 10%
1889 | HVDC Milano-Montalto | 1157 | HVDC Milano-Montalto | 12-2030 | 2 | TRUE | New Investment |  | DCTransmissionLine | Montalto | Avenza | DC | Bipolar | 440 | 500 | 2000 |  | VCS |  | 2675 | 0 | 12.305 | 0%
1869 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT) | 1158 | RES Integration; 1.000 MW Wind + 1.000 MW PV | 12-2037 | 1 | TRUE | New Investment |  | ACTransmissionLine | Bisamberg (AT) | Zaya (AT) | AC | None | 48 | 380 | 0 | 5543 |  |  | 578 | 0 | 0.39015 | 10%
1868 | 220-kV Bisamberg (AT) – Wien Südost (AT) | 1159 | RES Integration + 500 MW PV | 12-2033 | 2 | TRUE | New Investment |  | ACTransmissionLine | Bisamberg (AT) | Wien Südost (AT) | AC | None | 38 | 220 | 0 | 1954 |  |  | 107 | 0 | 0.10004 | 10%
1878 | HVDC converter stations Oléron2 | 1161 | Connection of a 1.2 GW offshore wind farm to an offshore link | 12-2035 | 1 | TRUE | New Investment |  | OffshoreSubstation | Oléron 2 | Gironde Loire-Atlantique Link | DC | None | 20 | 320 | 1200 |  | VCS |  | 1790 | 0 | 13.0008 | 50%
1879 | Offshore Wind Connection Fécamp-Grand Large 1 HVDC OSS + Onshore Converter Station + Cables | 1162 | 525 kV Le Havre 1 HVDC terrestrial converter stations and OSS | 12-2034 | 1 | TRUE | New Investment |  | OffshoreSubstation | Le Havre 1 | Le Havre Port Jérôme area | DC | None | 0 | 525 | 2000 |  | VCS |  | 3700 | 0 | 25.9999 | 50%
1881 | Offshore Wind Connection Fécamp-Grand Large 2 HVDC OSS + Onshore Converter Station + Cables | 1163 | 525 kV Le Havre 2 HVDC terrestrial converter stations and OSS | 12-2035 | 1 | TRUE | New Investment |  | OffshoreSubstation | Le Havre 2 | Le Havre Port Jérôme area | DC | Monopolar | 0 | 525 | 2000 |  | VCS |  | 3700 | 0 | 25.9999 | 50%
1883 | Offshore Wind Connection Golfe de Lion Centre HVDC OSS + Onshore Converter Station + Cables | 1164 | 525 kV Fos HVDC terrestrial converter stations and OSS | 12-2035 | 1 | TRUE | New Investment |  | OffshoreSubstation | Fos | Fos sur Mer - Realtor area | DC | None | 0 | 525 | 2000 |  | VCS |  | 4450 | 0 | 30.9987 | 50%
1885 | HVDC converter station Golfe de Gascogne Sud | 1165 | Connection of a 1.2 GW offshore wind farm to an offshore link | 12-2034 | 1 | TRUE | New Investment |  | OffshoreSubstation | Charente-Maritime | Gironde Loire-Atlantique Link | DC | None | 20 | 320 | 1200 |  | VCS |  | 1990 | 0 | 13.9997 | 50%
1913 | HG Adriatic Corridor | 1166 | HG Adriatic Corridor | 12-2036 | 2 | TRUE | New Investment |  | DCTransmissionLine | Foggia (IT) | Forlì (IT) | DC | Bipolar | 500 | 500 | 2000 |  | VCS |  | 2355 | 0 | 10.362 | 0%
1917 | HG Central link | 1167 | HG Central link | 12-2030 | 2 | TRUE | New Investment |  | DCTransmissionLine | Villavalle (IT) | S. Barbara (IT) | AC | Bipolar | 150 | 220 | 0 |  |  |  | 280 | 0 | 1.12 | 0%
1918 | HG Ionian-Tyrrhenian Corridor:Ionian Link | 1168 | HG Ionian-Tyrrhenian Corridor:Ionian Link | 12-2035 | 2 | FALSE | New Investment |  | DCTransmissionLine | Priolo (IT) | Rossano (IT) | DC | Bipolar | 425 | 500 | 1000 |  | VCS |  | 1410 | 0 | 6.486 | 0%
1919 | HG Ionian-Tyrrhenian Corridor:Rossano-Montecorvino-Latina | 1168 | HG Ionian-Tyrrhenian Corridor:Rossano-Montecorvino-Latina | 12-2035 | 2 | TRUE | New Investment |  | DCTransmissionLine | Rossano (IT) | Latina (IT) | DC | Bipolar | 345 | 500 | 2000 |  | VCS |  | 2724 | 0 | 13.0752 | 0%
1921 | SAPEI 2 | 1169 | SAPEI 2 | 12-2040 | 2 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Selargius | Montalto di castro | DC | Bipolar | 500 | 500 | 1000 |  | VCS |  | 1422 | 0 | 5.9724 | 0%
1962 | 400kV Interconnection IT-CH | 1171 | 380 kV interconnection projects between Italian and Swiss transmission system | 01-2038 | 2 | TRUE | New Investment |  | ACTransmissionLine | Regoledo | Swiss node | AC | None | 80 | 400 | 0 | 1000 |  |  | 1250 | 0 | 3.75 | 5%
1996 | New EHV SS Thesprotia | 1182 | New SS 400/150 kV Thesprotia | 10-2030 | 2 | TRUE | New Investment |  | OnshoreSubstation | Aracthos | Thesprotia | AC | None | 0 | 400 | 0 |  |  |  | 42 | 0 | 0.2 | 20%
1997 | New double circuit OHL 400 kV Aracthos - Thesprotia | 1182 | New double circuit OHL 400 kV Aracthos - Thesprotia | 10-2030 | 2 | FALSE | New Investment |  | ACTransmissionLine | Aracthos | Thesprotia | AC | None | 65 | 400 | 0 | 2 x 2000 |  |  | 31.2 | 0 | 0.50001 | 20%
1988 | New single circuit OHL 400 kV Thesprotia - Fier | 1183 | New single circuit OHL 400 kV Thesprotia - Fier | 10-2030 | 2 | TRUE | New Investment |  | ACTransmissionLine | Fier | Thesprotia | AC | None | 170 | 400 | 0 | 2000 |  |  | 67.7 | 0 | 0.9 | 15%%
1935 | South Coast Offshore Transmission Project | 1185 | While the project is at an early stage of development, to facilitate up to 900MW of new renewable generation, it is envisaged that the following infrastructure will be required: two new 220kV offshore platforms, two new 220kV onshore reactive compensation compounds / substations, two 220kV HVAC export transmission cables (consisting of both onshore and offshore elements comprising approximately 124km in total). | 10-2030 | 1 | TRUE | New Investment | N/A | OffshoreSubstation | Two new offshore substation platforms located within the DMAP area (as identified in accompanying map). | Great Island substation and a new substation in Cork looping into the Aghada – Knockraha 220 kV 1 & 2 circuits (these are the leading onshore connection nodes at this time). | AC | None | 124 | 220 | 0 | 580 |  |  | 1349 | 320 | 13.8502 | 40%
1943 | Germany-UK Hybrid Interconnector - Phase1 | 1192 | 2GW hybrid interconnector | 10-2033 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Fiddes | TBC | DC | Bipolar | 810 | 525 | 2000 |  | VCS |  | 5263 | 108 | 83.6817 | 20% | [9 empty] | not applicable.
1963 | Germany-UK Hybrid Interconnector - Phase2 | 1193 | 2GW hybrid interconnector | 10-2035 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Fiddes | TBC | DC | Bipolar | 100 | 525 | 2000 |  | VCS |  | 2089 | 73 | 35.3041 | 20% | [9 empty] | not applicable
1934 | NU-Link | 1197 | Subsea HVDC Interconnector between GB and NL | 12-2031 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Mablethorpe | Moerdijk | DC | MonopolarBipolar | 330 | 525 | 1200 |  | VCS |  | 1327.4 | 0 | 43.3024 | 15%
1936 | Hybrid interconnector Norway-Sørvest F Windfarm (first leg) | 1200 | One or more hybrid interconnectors connecting the Sørvest F windfarm area to Norway as well as to other countries around the North Sea. In the first phase we are planning for a 1400 MW hybrid interconnector, but a 2000 MW interconnector might as well be considered. At this stage the Danish, German and Belgian alternative are considered equal alternatives. Step 1 (1500 MW) of Sørvest F windfarm is planned awarded in Q4/2023 and radial connected. Step 2 is planned awarded in 2025 and will potential be hybrid connected. Further steps might be expected, as the potential of Sørvest F windfarms is in the range 6-12 GW. | 12-2035 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Kristiansand | Sørvest F windfarm | DC | Bipolar | 250 | 525 | 1400 |  | VCS |  | 1300 | 0 | 13 | 30%
1937 | Hybrid interconnector Sørvest F Windfarm-Denmark (second leg, alt.1) | 1200 | One or more hybrid interconnectors connecting the Sørvest F windfarm area to Norway as well as to other countries around the North Sea. In the first phase we are planning for a 1400 MW hybrid interconnector, but a 2000 MW interconnector might as well be considered. In the CBA, only one of the Continental countries might be CBA-assessed (for ENTSO-E to decide). At this stage the Danish, German and Belgian alternative are considered equal alternatives. Step 1 (1500 MW) of Sørvest F windfarm is planned awarded in Q4/2023 and radial connected. Step 2 is planned awarded in 2025 and will potential be hybrid connected. Further steps might be expected, as the potential of Sørvest F windfarms is in the range 6-12 GW. | 12-2035 | 1 | FALSE | New Investment |  | OffshoreDCTransmissionCable | Sørvest F windfarm | Danish offshore island (to be decided) | DC | Bipolar | 200 | 525 | 1400 |  | VCS |  | 1000 | 0 | 10 | 30%
1938 | Hybrid interconnector Sørvest F Windfarm-Germany (second leg, alt.2) | 1200 | Statnett is by the Norwegian Ministry given the task to plan for one or more hybrid interconnectors connecting the Sørvest F windfarm area to Norway as well as to other countries around the North Sea. MoUs are about to be signed between Statnett and TSOs of Denmark, Germany and Belgium aiming to develop one or more hybrid interconnectors. In the first phase we are planning for a 1400 MW hybrid interconnector, but a 2000 MW interconnector will also be evaluated. This is the alternative to Germany. Statnett, Amprion GmbH and TenneT TSO GmbH are currently investigating several options for the design of a possible hybrid interconnector between Norway and Germany. It is currently still open whether this is an offshore - offshore or offshore - onshore connection. Also several connection points are under consideration. | 12-2035 | 1 | FALSE | New Investment |  | OffshoreDCTransmissionCable | Sørvest F windfarm | Germany (connection point to be decided) | DC | Bipolar | 350 | 525 | 1400 |  | VCS |  | 1500 | 0 | 15 | 30%
1939 | Hybrid interconnector Sørvest F Windfarm-Belgium (second leg, alt.3) | 1200 | One or more hybrid interconnectors connecting the Sørvest F windfarm area to Norway as well as to other countries around the North Sea. In the first phase we are planning for a 1400 MW hybrid interconnector, but a 2000 MW interconnector might as well be considered. In the CBA, only one of the Continental countries might be CBA-assessed (for ENTSO-E to decide). At this stage the Danish, German and Belgian alternative are considered equal alternatives. Step 1 (1500 MW) of Sørvest F windfarm is planned awarded in Q4/2023 and radial connected. Step 2 is planned awarded in 2025 and will potential be hybrid connected. Further steps might be expected, as the potential of Sørvest F windfarms is in the range 6-12 GW. | 12-2035 | 1 | FALSE | New Investment |  | OffshoreDCTransmissionCable | Sørvest F windfarm | Belgium (connection point to be decided, Mercator as reference) | DC | Bipolar | 780 | 525 | 1400 |  | VCS |  | 3120 | 0 | 31.2 | 30%
1940 | Interconnector Norway-Denmark | 1201 | The existing interconnectors Skagerrak 1 and 2 (500 MW in total) were commissioned in 1976 and 1977 and are at the end of their technical life. The cables are expected to be in operation until 2026 with normal maintenance. The risk of failures is increasing and major repairs are not considered to be rational. The Norwegian TSO (Statnett) and the Danish TSO (Energinet) are considering to build a new 700 MW interconnector as a replacement of the ones that soon are expected to be decommissioned. MoU has been signed between the Statnett and Energinet. | 12-2035 | 2 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Kristiansand | Tjele | DC | Monopolar | 249 | 525 | 700 |  | VCS |  | 1250 | 0 | 12.5 | 75 % to 125 %%
1941 | Back-to-Back converter Seidafjellet | 1202 | Back-to-Back converter in the new Seidafjellet station (planned to replace the current Varangerbotn station) on the 220 kV line between Norway and Finland, the power flow will be better controlled and by this the cross-border capacity on existing 220 kV line Varangerbotn-Ivalo will be better utilised. | 12-2030 | 2 | TRUE | New Investment |  | BackToBackSubstation | Seidafjellet | Seidafjellet | DC | None | 0 | 420 | 150 |  | VCS |  | 110 | 0 | 1.1
1981 | Offshore Wind Connection Bretagne Nord-Ouest HVDC OSS + Onshore Converter Station + Cables | 1203 | 320 kV North Atlantic HVDC terrestrial converter stations and OSS | 12-2036 | 1 | TRUE | New Investment |  | OnshoreSubstation | North Atlantic OSS | Cordemais | DC | None | 0 | 320 | 1200 |  | VCS |  | 3200 | 0 | 22 | 50%
1944 | 380kV overhead Line Niederstedem-Bertrange | 1207 | This projects helps to increase the cross border capacity between Germany and Luxemburg by upgrading an existing line from 220 kV to 380 kV. The additional capacity is needed to ensure security of supply in Luxemburg. | 12-2037 | 2 | TRUE | Investment on time |  | ACTransmissionLine | Niederstedem | Bertrange | AC | None | 72.4 | 380 | 0 | 2369 |  |  | 187 | 0 | 2.805 | 10%
1945 | Medlink (Algeria - Italy) - DC Link 1 | 1208 | Medlink is a 4000 MW system composed of two links of 2000MW each, connecting Italy to North Africa. The link hereby described refers to the La Specia s/s (Italy) – Annaba (Algeria) and will be built in HVDC-VSC technology with an operating voltage of 525 kVdc. The link consists of a double bipole of 1 GW each equipped with sea electrodes, so to be able to operate at half power (500 MW) in case of fault of one pole. This is also favorable for the receiving system (Italy) where the application of the N-1 security criterion entails the loss of only 500 MW, which is fully compatible with the current reserve of the system. Design of the system can be subject to modification and revision during the detailed engineering phase. | 06-2030 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Annaba (Algeria) - new | La Spezia (Italy) - existing | DC | Bipolar | 940 | 525 | 2000 |  | VCS |  | 3689 | 40 | 36.1522 | 10%
1946 | Medlink (Tunisia - Italy) - DC Link 2 | 1208 | Medlink is a 4000 MW system composed of two links of 2000MW each, connecting Italy to North Africa. The link hereby described refers to the Suvereto s/s (Italy) – Marsa Dhib (Tunisia) and will be built in HVDC-VSC technology with an operating voltage of 525 kVdc. The link consists of a double bipole of 1 GW each equipped with sea electrodes, so to be able to operate at half power (500 MW) in case of fault of one pole. This is also favorable for the receiving system (Italy) where the application of the N-1 security criterion entails the loss of only 500 MW, which is fully compatible with the current reserve of the system. Design of the system can be subject to modification and revision during the detailed engineering phase | 06-2030 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Marsa Dhib (Tunisia) - New | Suvereto (Italy) - Existing | DC | Bipolar | 590 | 525 | 2000 |  | VCS |  | 3000 | 40 | 30 | 10%
1947 | Medlink (Algeria - AC) | 1208 | The RES generation site currently located in Touggourt region (Algeria) will be connected to the 2 GW HVDC link converter station in Annaba through 2 x 400kV double three-phase circuit AC lines and relate sub-stations. Data provided below refer to each single circuit. | 06-2030 | 1 | FALSE | New Investment |  | ACTransmissionLine | Annaba | Tougourt | AC | None | 600 | 400 | 0 | 1190 |  |  | 580 | 0 | 5.8 | 10%
1948 | Medlink (Tunisia - AC) | 1208 | The RES generation site currently located in De Jebil area (Tunisia) will be connected to the 2 GW HVDC link converter station in Marsa Dhib through 2 x 400kV double three-phase circuit AC lines and relate sub-stations | 06-2030 | 1 | FALSE | New Investment |  | ACTransmissionLine | De Jebil (Tunisia) | Marsa Dhib (Tunisia) | AC | None | 500 | 400 | 0 | 1190 |  |  | 488 | 0 | 4.88 | 10%
1953 | Broceni - Varduva new cross-border line between Latvia and Lithuania | 1209 | The new cross-border network interconnection between Broceni (LV) - Varduva (LT) | 12-2035 | 1 | TRUE | New Investment |  | ACTransmissionLine | Broceni (LV) | Varduva (LT) | AC | None | 50 | 330 | 0 | 1156 |  |  | 50 | 0 | 0.5 | 3%
1954 | Cross-border network reinforcement Grobina (LV) - Derbenai (LT) | 1209 | The reconstruction of the existing 330 kV OHL from substation Grobina in Latvia to substation Derbenai in Lithuania. The capacity increase on cross-border Latvia - Lithuania up to 300 MW. | 12-2035 | 1 | FALSE | New Investment |  | ACTransmissionLine | Grobina (LV) | Derbenai (LT) | AC | None | 65 | 330 | 0 | 1156 |  |  | 50 | 0 | 0.5 | 3%
1967 | New 330 kV OHL Darbenai-Varduva-Musa | 1209 | New 330 kV OHL Darbenai-Varduva-Musa | 12-2034 | 1 | FALSE | New Investment |  | ACTransmissionLine | Derbenai | Musa | AC | None | 170 | 330 | 0 | 1017 |  |  | 158 | 0 | 1.58 | 1%
1968 | New 330 kV OHL Panevezys-Musa | 1209 | New 330 kV OHL Panevezys-Musa | 12-2033 | 1 | FALSE | New Investment |  | ACTransmissionLine | Panevezys | Musa | AC | None | 72 | 330 | 0 | 1017 |  |  | 60 | 0 | 0.6 | 1%
1969 | New 330 kV Varduva substation | 1209 | New 330 kV Varduva substation | 12-2032 | 1 | FALSE | New Investment |  | OnshoreSubstation | Varduva | Varduva | AC | None | 0 | 330 | 0 | 0 |  |  | 37.2 | 0 | 0.36999 | 1%
1970 | New reactive compensation device in Darbenai substation | 1209 | New reactive compensation device in Darbenai substation, for compensation of reactive power generated by new 330 kV lines. | 12-2028 | 1 | FALSE | New Investment |  | ReactiveCompensationDevice | Darbenai | Darbenai | AC | None | 0 | 330 | 0 |  |  |  | 8.1 | 0 | 0.080004 | 1%
1971 | New reactive compensation device in Musa substation | 1209 | New reactive compensation device in Musa substation, for compensation of reactive power generated by new 330 kV lines. | 12-2028 | 1 | FALSE | New Investment |  | ReactiveCompensationDevice | Musa | Musa | AC | None | 0 | 330 | 0 |  |  |  | 8.1 | 0 | 0.080004 | 1%
1977 | Reconstruction of Broceni substation (LV) | 1209 | The reconstruction of Broceni substation in Latvia | 12-2035 | 1 | FALSE | New Investment |  | OnshoreSubstation | Broceni (LV) | Broceni (LV) | AC | None | 0 | 330 | 0 | 0 |  |  | 20 | 0 | 0.2 | 1%
1957 | APOLLO-LINK | 1210 | The project is a 2GW HVDC Interconnection with two converters operating a VSC technology at 525 kV. It consists of approx. 660 km of subsea and 40km of onshore transmission cable. The investment is a new green field project with 2,091MW thermal capacity. | 01-2032 | 1 | TRUE | New Investment |  | DCTransmissionLine | La Spezia (Italy) | Ramis (Spain) | DC | Bipolar | 700 | 525 | 2091 |  | VCS |  | 3081.6 | 0 | 19.9996 | 30%
1958 | Baltic WindConnector (BWC) | 1211 | HVDC interconnector including converters and sea cables | 12-2037 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Saaremaa-Hub (EE) | Area of Brünzow/Kemnitz (DE) | DC | Bipolar | 800 | 525 | 2000 |  | VCS |  | 6600 | 0 | 33 | 20%
1960 | HVDC line | 1213 | Hybrid offshore Interconnector between Germany and the Netherlands | 12-2035 | 1 | TRUE | New Investment |  | DCTransmissionLine | Search area 6/7 | NOR-14-x | DC | Bipolar | 30 | 525 | 2000 |  | VCS |  | 886 | 0 | 7.1004 | 10%
1964 | Hybrid Interconnector Denmark-Germany | 1214 | The project aims to integrate 2 GW of additional Danish offshore wind capacity to onshore markets as part of the Danish Energy Island. To integrate the additional capacity an increase of transfer capacity across the DE-DK EEZ corridor is envisioned towards 2036. | 12-2036 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Danish Energy Island | German offshore grid connection |  | None | 1000 | 525 | 0 |  |  |  | 6000 | 0 | 60 | 45%
1991 | Xlinks DC | 1215 | The HVDC transmission architecture is based on two 1,800 MW (receiving end) bipolar 525 kV DC lines. Each cable system will be connected to a HVDC converter at the landing site based on VSC (Voltage Source Converter) technology, providing high reliability and efficiency of the transmission system. Each bipolar system will be an XLPE rigid bipole, using an aluminum conductor with a cross section of 3,500mm2. The cable systems will have two layers of steel armoring and will be buried 1m below the seabed. The entire cable system will be operated in an average water depth of 120-150m, with very limited sections of the cable crossing the seabed at water depths of 600-700m. | 10-2032 | 1 | TRUE | New Investment | N/A | OffshoreDCTransmissionCable | [Tan Tan] (MOR) VSC HVDC - 525 kV DC – 2x 1.8GW | (GER) VSC HVDC - 525 kV DC - 2x 1.8GW | DC | Bipolar | 4800 | 525 | 3600 |  | VCS |  | 14480 | 45 | 33.999 | 30%
1986 | HVDC Arad-Albertirsa | 1216 | HVDC cable 2500MW 238km between Romania and Hungary | 12-2030 | 1 | TRUE | New Investment |  | DCTransmissionLine | Arad | Albertirsa | DC | Bipolar | 238 | 525 | 2500 |  | VCS |  | 1401 | 0 | 2.802 | 30%
1987 | HVDC Arad-Constanta South | 1216 | HVDC cable 2500MW between Arad (RO) and Constanta South (RO) | 12-2030 | 1 | FALSE | New Investment |  | DCTransmissionLine | Arad | Constanta South | DC | Bipolar | 830 | 525 | 2500 |  | VCS |  | 2822 | 0 | 5.644 | 30%
2003 | HVDC Arad-Bucharest | 1216 | HVDC cable between Arad and Bucharest South | 12-2030 | 1 | FALSE | New Investment |  | DCTransmissionLine | Arad | Bucharest South | DC | None | 586 | 525 | 2500 |  | VCS |  | 1821 | 0 | 3.642 | 30%
2008 | HVDC Bucharest - Constanta South | 1216 | HVDC cable between Bucharest and Constanta South | 12-2030 | 1 | FALSE | New Investment |  | DCTransmissionLine | Bucharest South | Constanta South | DC | Bipolar | 344 | 525 | 2500 |  | VCS |  | 1240 | 0 | 2.48 | 30%
1972 | MOG 3 | 1217 | 2000MW radial connection | 12-2040 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | MOG 3 | Van Eyck | DC | Bipolar | 310 | 1050 | 2000 |  | VCS |  | 3400 | 0 | 34 | 40%
1973 | Hybrid IC BE-NL | 1218 | Link between Belgium and a already radially connected offshore wind farms in the Netherlands. | 12-2040 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Offshore wind farm | Doel | DC | Bipolar | 503 | 1050 | 2000 |  | VCS |  | 3505 | 0 | 35.05 | 40%
1974 | 380kV Overhead line Bofferdange – Bertrange | 1219 | The projected 380kV overhead line in subsection Bofferdange – Bertrange; length: 20km; Pylons: 2 x 380 kV AC circuits (1 circuit per side) | 12-2030 | 2 | TRUE | New Investment |  | ACTransmissionLine | Bofferdange | Bertrange | AC | None | 20 | 380 | 0 |  |  |  | 90 | 48 | 0.9 | 10%
1975 | 380/220/110-65kV substation Bertrange | 1219 | Upgrade of existing 220/65/20kV substation Bertrange to connect the 380kV transmission grid to the 220kV grid infrastructure, connection e.a. of 2 circuits of the 380kV overhead line Bofferdange – Bertrange | 12-2035 | 2 | FALSE | New Investment |  | OnshoreSubstation | Bertrange | Bertrange | AC | None | 0 | 380 | 0 | 0 |  |  | 88 | 54.2 | 0.88 | 10%
1980 | Offshore Wind Connection Viana do Castelo | 1220 | Offshore Wind Connection (to be confirmed technical details\type of element) | 12-2030 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | tbc | tbc | AC | None | 0 | 0 | 0 | 0 |  |  | 2000 | 0 | 0 | 100%
1989 | Offshore Wind Connection Leixões | 1221 | Offshore Wind Connection (to be confirmed technical details\type of element) | 12-2030 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | tbc | tbc | AC | None | 0 | 0 | 0 | 0 |  |  | 1500 | 0 | 0 | 100%
1998 | Offshore Wind Connection Figueira da Foz (North) | 1222 | Offshore Wind Connection (to be confirmed technical details\type of element) | 12-2030 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | tbc | tbc | AC | None | 0 | 0 | 0 | 0 |  |  | 2000 | 0 | 0 | 100%
1999 | Offshore Wind Connection Figueira da Foz | 1223 | Offshore Wind Connection (to be confirmed technical details\type of element) | 12-2030 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | tbc | tbc | AC | None | 0 | 0 | 0 | 0 |  |  | 2000 | 0 | 0 | 100%
2000 | Offshore Wind Connection Ericeira | 1224 | Offshore Wind Connection (to be confirmed technical details\type of element) | 12-2030 | 1 | TRUE | New Investment |  | OffshoreACTransmissionCable | tbc | tbc | AC | None | 0 | 0 | 0 | 0 |  |  | 1000 | 0 | 0 | 100%
2006 | Offshore Wind Connection Sines | 1225 | Offshore Wind Connection (to be confirmed technical details\type of element) | 12-2030 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | tbc | tbc | AC | None | 0 | 0 | 0 | 0 |  |  | 1500 | 0 | 0 | 100%
2011 | 400kV OHL, Maritsa East (BG) - Nea Santa (GR) | 1226 | Third interconnection line on the border between Bulgaria and Greece. It is in parallel to the existing one. | 07-2036 | 1 | TRUE | New Investment |  | ACTransmissionLine | SS Maritsa East (BG) | SS Nea Santa (GR) | AC | None | 153 | 400 | 0 |  |  |  | 90 | 0 | 0.18 | +15%, -15%%
2013 | 400kV OHL, Blagoevgrad (BG) - Lagadas (GR) | 1226 | Fourth interconnection line on the border between Bulgaria and Greece | 07-2036 | 1 | FALSE | New Investment |  | ACTransmissionLine | SS Blagoevgrad (BG) | SS Lagadas (GR) | AC | None | 161 | 400 | 0 |  |  |  | 94.7 | 0 | 0.1894 | +15%, -15%%
2014 | 400kV OHL, Tsarevets (BG) - Draganesti Olt (RO) | 1226 | Fifth interconnection line on the border between Bulgaria and Romania | 07-2036 | 1 | FALSE | New Investment |  | ACTransmissionLine | SS Tsarevets (BG) | SS Draganesti Olt (RO) | AC | None | 153 | 400 | 0 |  |  |  | 90 | 0 | 0.18 | +15%, -15%%
2015 | 400kV OHL, Svoboda (BG) - Bucuresti Sud (RO) | 1226 | Sixth interconnection line on the border between Bulgaria and Romania | 07-2036 | 1 | FALSE | New Investment |  | ACTransmissionLine | SS Svoboda (BG) | SS Bucuresti Sud (RO) | AC | None | 147 | 400 | 0 |  |  |  | 86.47 | 0 | 0.17294 | +15%, -15%%
2016 | 400kV OHL, Tsarevets (BG) - Zlatitsa (BG) | 1226 | New internal km single circuit 400kV OHL | 07-2036 | 1 | FALSE | New Investment |  | ACTransmissionLine | SS Tsarevets (BG) | SS Zlatitsa (BG) | AC | None | 0 | 400 | 0 |  |  |  | 97.05 | 0 | 0.1941 | +15%, -15%%
1984 | HVDC from Ovelgönne/Rastede/Wiefelstede/Westerstede to Bürstadt | 1229 | New HVDC-line from Ovelgönne/Rastede/Wiefelstede/Westerstede to Bürstadt to integrate new wind generation especially from North Sea towards Central Germany for consumption and storage. | 03-2033 | 2 | TRUE | New Investment |  | DCTransmissionLine | Ovelgönne/Rastede/Wiefelstede/Westerstede (DE) | Bürstadt (DE) | DC | Bipolar | 523 | 525 | 2000 |  | VCS |  | 5435 | 0 | 43.5017 | 10%
1985 | HVDC from Ovelgönne/Rastede/Wiefelstede/Westerstede to Marxheim | 1229 | New HVDC-line from Ovelgönne/Rastede/Wiefelstede/Westerstede to Marxheim to integrate new wind generation especially from North Sea towards Central Germany for consumption and storage. | 03-2035 | 2 | FALSE | New Investment |  | DCTransmissionLine | Ovelgönne/Rastede/Wiefelstede/Westerstede (DE) | Marxheim (DE) | DC | Bipolar | 461 | 525 | 2000 |  | VCS |  | 4117 | 0 | 32.8989 | 10%
1992 | TuNur DC | 1230 | The HVDC transmission architecture is based on a single symmetrical monopole +/-320 kV system of 500MW. The HVDC converter is based on VSC (Voltage Source Converter) technology, providing high reliability and efficiency of the transmission system. TuNur DC will consist of a single symmetrical monopole +/-320 kV HVDC system with 500MW, including the overhead transmission line in Tunisia spanning from the power plant to the first converter station located in the gulf of Gabès in Tunisia, the submarine cable from the Tunisian coast to the landing point in Malta, and the HVDC converter station on the Maltese side. | 02-2032 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Rejim Maatoug (TUN) VSC HVDC - +/- 320 kV DC, 500MW | Converter station in Malta (MLT) VSC HVDC - +/- 320 kV DC – 220kV AC, 500MW | DC | Monopolar | 654 | 320 | 500 |  | VCS |  | 1437 | 244 | 11.8998 | 8% | [9 empty] | TuNur DC: Job Creation - Creation of numerous qualified jobs in Tunisia for the construction and O&M of the land lines and HVDC converters.
1993 | TuNur AC | 1230 | 220 kV AC underground cables from the HVDC converter station in Malta to the point of injection in the Maltese network (identification of the final point of injection is ongoing and will be finalized through a network impact study in coordination with Enemalta). CAPEX includes also bays extension in the existing substation in the Maltese network. | 02-2032 | 1 | FALSE | New Investment |  | OnshoreACTransmissionCable | Converter station in Malta (MLT) VSC HVDC - +/- 320 kV DC – 220kV AC, 500MW | Malta (MLT) Enemalta substation 220 kV AC | AC | None | 4 | 220 | 0 | 522 |  |  | 52 | 9 | 0.39998 | 8% of the overall project cost as exact length is not yet confirmed, it being understood that the impact of the short AC cable on the overall project will be negligible.% | [9 empty] | TuNur DC: Job Creation - Creation of numerous qualified jobs in Tunisia for the construction and O&M of the land lines and HVDC converters.
1994 | New HVDC link between Germany and Greece | 1231 | New HVDC link between Germany and Greece with an NTC increase of 3000 MW. | 12-2035 | 1 | TRUE | New Investment |  | DCTransmissionLine | Thesprotia | Ottenhofen | DC | Bipolar | 1400 | 525 | 3000 |  | VCS |  | 8100 | 0 | 81 | ±30%
2001 | Beznau - Laufenburg | 1233 | line | 12-2035 | 1 | FALSE | New Investment |  | ACTransmissionLine | Beznau 380 kV | Laufenburg 380 kV | AC | None | 16 | 380 | 0 | 1745 |  |  | 40 | 0 | 0.2 | 10% |  |  |  | 0 | Other None |  | 0 | Other
2002 | Beznau - Breite | 1233 | line | 12-2035 | 1 | TRUE | New Investment |  | ACTransmissionLine | Beznau 380 kV | Breite 380 kV | AC | None | 42 | 380 | 0 | 1745 |  |  | 100 | 0 | 0.5 | 10% |  |  |  | 0 | Other |  | 0 | Other
2004 | 220-kV Reitdorf (AT) - Weißenbach (AT) | 1234 | Reinforcement/Upgrade 220-kV Overheadline | 12-2028 | 3 | TRUE | New Investment |  | ACTransmissionLine | Reitdorf (AT) | Weißenbach (AT) | AC | None | 73 | 220 | 0 | 1872 |  |  | 156 | 0 | 0.18 | 10%
2007 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | 1235 | nstallation of the second circuit on existing 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | 12-2027 | 1 | TRUE | New Investment |  | ACTransmissionLine | Sajóivánka (HU) | Rimavska Sobotá (SK) | AC | None | 51.057 | 400 | 0 | 1551.9 |  |  | 16.09 | 0 | 0.04827 | 10%
2010 | Power-to-Gas for Austria (P2G4A) | 1236 | P2G Pilot | 12-2029 | 1 | TRUE | New Investment |  | Transformer | Prottes (AT) | Prottes (AT) | AC | None | 0 | 380 | 0 | 50 |  |  | 149 | 0 | 0.009983 | 10%
2017 | 400 kV cross-border interconnection between Mukacheve (UA) - Velké Kapušany (SK) | 1239 | Upgrade of the line 400 kV Mukacheve (UA) - Velké Kapušany (SK) | 12-2026 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Mukacheve (UA) | Velké Kapušany (SK) | AC | None | 52 | 400 | 0 | 1730 |  |  | 21.3 | 0 | 0.106 | 5%
2018 | Reconstruction of substation Velké Kapušany (SK) | 1239 | Reconstruction of substation Velké Kapušany (SK) | 12-2030 | 2 | FALSE | New Investment |  | OnshoreSubstation | Substation | Substation | AC | None | 0 | 400 | 0 |  |  |  | 66 | 0 | 0.264 | 5%
2019 | Extension of substation Lemešany (SK) | 1239 | Extension of 400 kV substation Lemešany (SK) by one bay + W2 busbar | 12-2031 | 2 | FALSE | New Investment |  | OnshoreSubstation | Substation | Substation | AC | None | 1 | 400 | 0 |  |  |  | 7.96 | 0 | 0.03184 | 5%
2020 | Upgrade of 400 kV line Lemešany (SK) - Vola (SK) | 1239 | New double-circuit 400kV OHL Lemešany (SK) - Vola (SK) and Lemešany (SK) - Velké Kapušany (SK). | 08-2032 | 2 | FALSE | New Investment |  | ACTransmissionLine | Lemešany (SK) | Vola (SK) | AC | None | 47 | 400 | 0 | 1663 |  |  | 69.77 | 0 | 0.27908 | 5%
2021 | Upgrade of 400 kV line Vola (SK) - Velké Kapušany (SK) | 1239 | New double-circuit 400kV OHL Lemešany (SK) - Velké Kapušany (SK) and Vola (SK) - Mukacheve (UA) | 08-2032 | 2 | FALSE | New Investment |  | ACTransmissionLine | Vola (SK) | Velké Kapušany (SK) | AC | None | 23 | 400 | 0 | 1663 |  |  | 36.904 | 0 | 0.14762 | 5%
2022 | 400 kV cross-border interconnection between Artsyz (UA) - Isaccea (RO) | 1240 | New double-circuit 400kV OHL Artsyz (UA) - Isaccea (RO). | 12-2028 | 2 | TRUE | New Investment |  | ACTransmissionLine | Artsyz (UA) | Isaccea (RO) | AC | None | 130 | 400 | 0 | 1730 |  |  | 221.4 | 0 | 2.4354 | 30%

## Stor.Projects
TYNDP 2024 - General description of storage projects | [17 empty] | Needs addressed by the project |  |  |  | Projects costs |  |  |  | Technical characteristics of the project |  |  |  |  | Residual impact of the project |  |  | CBA
Project ID | Project Name | Promoters | Country | National development plan(s) | Storage technology | Project description | Commissioning year estimated by the promoter(s) | Status ID 1 : Under Consideration 2 : In Planning but not permitting 3 : In permitting 4 : Under Construction | Progress of the project since TYNDP2022 | Explanation in case of delay | Type of project - Is it an upgrade of existing infrastructure? | Is the project on the 5th PCI list? | PCI number | Inclusion in previous TYNDPs | Is the project in the reference grid 2030? | Is the project in the reference grid 2035? | Where can one find more information on the project? (ex: project website url) | Needs addressed by the project | Explanation by the promoter on how the project addresses the system needs | Relevant system needs study results in 2030 | Relevant system needs study results in 2040 | Estimated CAPEX (MEUR) | Sustaining CAPEX (Meuro) | Estimated OPEX (MEUR/year) | Cost Uncertainty Range | Total turbining capacity (MW) | Storage Capacity (GWh) | Total Pumping Capacity of Pump Storage (MW) | Roundtrip efficiency (%) | Operational lifetime (Years) | Residual Environmental Impact | Residual Social Impact | Other Residual Impact | Comments on CBA results by the project promoter

## 2030NT
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 56 | 60 | 51 | 62 | 61 | 62 | 60 | 131 | 137 | 125 | -537 | -532 | -543 | 53 | 7 | 67 | 108 | 1 | 7 | 11 | 2027 | 2140 | 1914 | 1154 | -83 | -27 | -4 | -1 | -1 | -10 | 157 | 12 | 1962 | 1962 | 1962 | 14 | 14 | 14
4 | Interconnection Portugal-Spain | TOOT | 26 | 31 | 17 |  | 13 | 17 | 10 | 18 | 22 | 11 | -113 | -87 | -151 | 23 | 1 | 14 | 23 | 0 | 3 | 5 | 281 | 340 | 165 |  | -14 | -9 | -17 | 0 | -1 | -3 | 41 | 5 | 245 | 245 | 245 | 3 | 3 | 3
16 | Biscay Gulf | TOOT | 372 | 382 | 358 |  | 189 | 201 | 180 | 217 | 251 | 192 | -1662 | -1585 | -1773 | 356 | 21 | 207 | 335 | 4 | 44 | 72 | 3337 | 3904 | 2928 |  | -620 | -186 | -58 | -6 | -7 | -65 | 2593 | 123 | 2211 | 2211 | 2211 | 75 | 75 | 75
28 | Italy-Montenegro | TOOT | 34 | 50 | 18 |  | 23 | 27 | 19 | 19 | 25 | 14 | -204 | -168 | -236 | 29 | 3 | 25 | 41 | 0 | 4 | 6 | 286 | 378 | 222 |  | -75 | -23 | -7 | -1 | -1 | -8 | 107 | 8 | 20 | 20 | 20 | 0 | 0 | 0
29 | Italy-Tunisia | TOOT | 124 | 137 | 109 |  | 69 | 76 | 61 | 22 | 27 | 16 | -606 | -534 | -669 | -7 | 8 | 75 | 122 | 0 | -1 | -2 | 337 | 405 | 245 |  | -218 | -74 | -10 | -1 | -1 | -26 | -36 | -2 | 514 | 514 | 514 | 4 | 4 | 4
33 | Central Northern Italy | TOOT | 5 | 11 | 1 |  | 0 | 2 | -1 | 5 | 9 | 2 | -4 | 11 | -20 | -13 | 0 | 1 | 1 | 0 | -2 | -3 | 73 | 134 | 32 |  | -16 | -3 | -3 | 0 | 0 | -1 | 58 | -3 | 18 | 18 | 18 | 0 | 0 | 0
35 | CZ Southwest-east corridor | TOOT | 89 | 102 | 78 |  | 54 | 62 | 47 | 28 | 30 | 27 | -479 | -412 | -545 | 32 | 6 | 60 | 97 | 0 | 4 | 6 | 431 | 452 | 417 |  | -191 | -62 | -2 | -1 | -1 | -22 | 290 | 14 | 179 | 179 | 179 | 3 | 3 | 3
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 26 | 30 | 24 |  | 10 | 14 | 7 | 20 | 26 | 15 | -89 | -64 | -126 |  | 1 | 11 | 18 |  |  |  | 308 | 410 | 223 |  | -48 | -8 | -26 | -1 | -2 | -3 |  |  | 11 | 11 | 11 | 0 | 0 | 0
47 | Westtirol (AT) - Vöhringen (DE) | TOOT | 39 | 40 | 38 |  | 18 | 20 | 17 | 30 | 33 | 26 | -159 | -147 | -178 | 27 | 2 | 20 | 32 | 0 | 3 | 5 | 455 | 505 | 406 |  | -61 | -19 | -1 | 0 | -1 | -7 | 147 | 9 | 194 | 194 | 194 | 3 | 3 | 3
81 | North South Interconnector | TOOT | 65 | 76 | 52 |  | 27 | 30 | 19 | 27 | 39 | 19 | -234 | -170 | -266 | -1 | 3 | 29 | 47 | 0 | 0 | 0 | 420 | 596 | 289 |  | -74 | -27 | -16 | 0 | 0 | -10 | -40 | 0 | 153 | 153 | 153 | 3 | 3 | 3
85 | Integration of RES in Alentejo | TOOT | 0 | 2 | 0 | 12 | -1 | 4 | -7 | 17 | 19 | 14 | 5 | 58 | -31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 293 | 220 | 442 | -16 | -1 | -15 | -1 | -1 | -1 | 18 | 1 | 0 | 0 | 0 | 0 | 0 | 0
94 | GerPol Improvements | TOOT | 133 | 140 | 127 |  | 74 | 79 | 67 | 36 | 38 | 35 | -651 | -592 | -697 | 78 | 8 | 81 | 131 | 1 | 10 | 16 | 559 | 595 | 528 |  | -385 | -53 | -252 | -10 | -17 | -19 | 478 | 27 | 468 | 468 | 468 | 8 | 8 | 8
107 | Celtic Interconnector | TOOT | 193 | 199 | 187 |  | 62 | 64 | 59 | 201 | 203 | 199 | -545 | -522 | -566 | 88 | 7 | 68 | 110 | 1 | 11 | 18 | 3092 | 3101 | 3080 |  | -119 | -47 | -56 | 0 | -1 | -16 | 862 | 31 | 825 | 825 | 825 | 27 | 27 | 27
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 48 | 60 | 40 |  | 8 | 18 | 2 | 43 | 45 | 41 | -75 | -19 | -158 | 6 | 1 | 9 | 15 | 0 | 1 | 1 | 658 | 683 | 631 |  | -114 | -1 | -87 | -3 | -5 | -1 | 4 | 2 | 610 | 610 | 610 | 8 | 8 | 8
120 | Princess Elisabeth Island (MOG 2) | TOOT | 289 | 289 | 289 | 559 | 224 | 224 | 224 | 885 | 885 | 884 | -1976 | -1974 | -1978 | 136 | 25 | 246 | 398 | 2 | 17 | 28 | 13621 | 13780 | 13463 | 3600 | -732 | -206 | -109 | -8 | -11 | -72 | 644 | 42 | 1122 | 1122 | 1122 | 16 | 16 | 16
121 | Nautilus: multi-purpose interconnector Belgium - UK | TOOT | 122 | 126 | 116 |  | 33 | 34 | 31 | 58 | 61 | 55 | -288 | -275 | -300 | 38 | 4 | 36 | 58 | 0 | 5 | 8 | 895 | 927 | 850 |  | -171 | -45 | -31 | -2 | -3 | -16 | 166 | 11 | 627 | 627 | 627 | 9 | 9 | 9
124 | Ekhyddan-Nybro-Hemsjö | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 36 | 41 | 34 |  | 30 | 34 | 24 | 2 | 4 | 0 | -264 | -213 | -303 | 22 | 3 | 33 | 53 | 0 | 3 | 4 | 34 | 71 | 7 |  | -232 | -26 | -113 | -5 | -7 | -10 | 177 | 11 | 104 | 104 | 104 | 0 | 0 | 0
127 | Central Southern Italy | TOOT | 25 | 32 | 20 |  | 12 | 15 | 10 | 11 | 15 | 6 | -108 | -88 | -131 | 28 | 1 | 13 | 22 | 0 | 4 | 6 | 166 | 231 | 97 |  | -30 | -15 | -18 | 0 | -1 | -5 | 132 | 8 | 354 | 354 | 354 | 0 | 0 | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 233 | 299 | 176 |  | 90 | 151 | 41 | 96 | 124 | 71 | -793 | -365 | -1330 | 27 | 10 | 99 | 160 | 0 | 3 | 5 | 1 | 1 | 1 |  | -379 | -98 | -55 | -4 | -5 | -35 | 0 | -9
132 | HVDC Line A-North | TOOT | 812 | 932 | 721 |  | 121 | 196 | 27 | 413 | 476 | 363 | -1071 | -239 | -1461 | 52 | 13 | 133 | 216 | 1 | 6 | 10 | 4 | 5 | 4 |  | -466 | -135 | -38 | -5 | -5 | -48 | 0 | -18
138 | Black Sea Corridor | TOOT | 13 | 22 | 8 |  | 4 | 12 | -1 | -4 | 0 | -10 | -37 | 11 | -102 | 26 | 0 | 5 | 7 | 0 | 3 | 5 | -64 | 7 | -157 |  | -13 | -6 | -9 | 0 | 0 | -2 | 95 | 7 | 297 | 297 | 297 | 0 | 0 | 0
144 | Mid Continental East corridor | TOOT | 8 | 9 | 7 |  | 5 | 11 | 2 | -3 | 1 | -9 | -47 | -18 | -100 | 23 | 1 | 6 | 9 | 0 | 3 | 5 | -46 | 18 | -135 |  | -3 | -3 | -9 | 0 | -1 | -1 | 85 | 6 | 461 | 461 | 461 | 7 | 7 | 7
150 | Italy-Slovenia | TOOT | 17 | 23 | 9 |  | 9 | 19 | 1 | 0 | 9 | -8 | -79 | -11 | -166 | 31 | 1 | 10 | 16 | 0 | 4 | 6 | -3 | 130 | -128 |  | -20 | -9 | -8 | 0 | 0 | -3 | 99 | 8 | 86 | 86 | 86 | 1 | 1 | 1
153 | France-Alderney-Britain | TOOT | 233 | 239 | 228 |  | 72 | 83 | 62 | 228 | 235 | 218 | -638 | -548 | -734 | 130 | 8 | 79 | 129 | 2 | 16 | 26 | 3588 | 3601 | 3576 |  | -208 | -66 | -6 | -2 | -2 | -23 | 829 | 44 | 1428 | 1428 | 1428 | 15 | 15 | 15
170 | Baltic States Synchronization with Continental Europe | TOOT | 269 | 269 | 268 |  | 188 | 191 | 184 | 127 | 131 | 120 | -1658 | -1622 | -1680 | -198 | 21 | 207 | 334 | -3 | -25 | -40 | 1953 | 2020 | 1840 |  | -65 | -112 | -112 | -3 | -15 | -31 | -1083 | -64 | 595 | 595 | 595 | 10 | 10 | 10
174 | Greenconnector | TOOT | 127 | 152 | 110 |  | 71 | 78 | 63 | 0 | 6 | -5 | -628 | -558 | -684 | 98 | 8 | 78 | 127 | 1 | 12 | 20 | -2 | 97 | -71 |  | -338 | -102 | -32 | -3 | -3 | -36 | 569 | 34 | 72 | 72 | 72 | 1 | 1 | 1
176 | Hansa PowerBridge I | TOOT | 129 | 135 | 126 |  | 76 | 80 | 68 | 24 | 29 | 19 | -667 | -596 | -707 | 57 | 8 | 83 | 134 | 1 | 7 | 11 | 361 | 439 | 284 |  | -156 | -75 | -33 | 0 | 0 | -25 | 246 | 18 | 267 | 267 | 267 | 4 | 4 | 4
187 | St. Peter (AT) - Pleinting (DE) | TOOT | 214 | 224 | 202 |  | 113 | 114 | 113 | 134 | 142 | 128 | -1001 | -993 | -1009 | 18 | 13 | 125 | 202 | 0 | 2 | 4 | 2058 | 2157 | 1964 |  | -363 | -98 | -79 | -5 | -6 | -35 | 73 | 4 | 1667 | 1667 | 1667 | 26 | 26 | 26
200 | CZ Northwest-South corridor | TOOT | 89 | 102 | 78 |  | 54 | 62 | 47 | 28 | 30 | 27 | -479 | -412 | -545 | 6 | 6 | 60 | 97 | 0 | 1 | 1 | 431 | 452 | 417 |  | -191 | -62 | -2 | -1 | -1 | -22 | 199 | 7 | 183 | 183 | 183 | 3 | 3 | 3
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 20 | 27 | 13 |  | 7 | 12 | 5 | 0 | 2 | -3 | -65 | -41 | -104 | 3 | 1 | 8 | 13 | 0 | 0 | 1 | -8 | 29 | -49 |  | -40 | -12 | 0 | 0 | 0 | -4 | 35 | 2 | 27 | 27 | 27 | 0 | 0 | 0
219 | Great Sea Interconnector | TOOT | 145 | 150 | 139 |  | 62 | 65 | 58 | 0 | 4 | -5 | -547 | -510 | -576 | 270 | 7 | 68 | 110 | 3 | 34 | 54 | -8 | 61 | -80 |  | -262 | -60 | -39 | -3 | -3 | -22 | 651 | 66 | 985 | 985 | 985 | 10 | 10 | 10
225 | 2nd interconnector Belgium - Germany | light PINT | 70 | 82 | 61 |  | 27 | 31 | 24 | 51 | 64 | 40 | -241 | -213 | -273 | 128 | 3 | 30 | 49 | 2 | 16 | 26 | 788 | 978 | 603 |  | -83 | -23 | -19 | -1 | -1 | -8 | 630 | 38 | 39 | 39 | 39 | 1 | 1 | 1
227 | Transbalkan Corridor | TOOT | 5 | 11 | 0 |  | 0 | 4 | -5 | -3 | -1 | -8 | 4 | 48 | -37 | -25 | 0 | 0 | 0 | 0 | -3 | -5 | -52 | -17 | -117 |  | -18 | -1 | -15 | -1 | -1 | -1 | -91 | -7 | 116 | 116 | 116 | 2 | 2 | 2
228 | Muhlbach - Eichstetten | TOOT | 23 | 26 | 19 |  | 3 | 7 | 0 | 17 | 21 | 12 | -24 | -4 | -59 | 26 | 0 | 3 | 5 | 0 | 3 | 5 | 260 | 325 | 190 |  | -21 | -7 | -2 | 0 | 0 | -2 | 175 | 9 | 259 | 259 | 259 | 9 | 9 | 9
231 | Beznau - Tiengen | TOOT | 47 | 56 | 39 |  | 22 | 29 | 18 | 39 | 47 | 33 | -195 | -160 | -260 | 60 | 2 | 24 | 39 | 1 | 7 | 12 | 606 | 719 | 498 |  | -77 | -24 | -6 | -1 | -1 | -8 | 122 | 16 | 23 | 23 | 23 | 0 | 0 | 0
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 845 | 1049 | 715 |  | 163 | 206 | 135 | 385 | 488 | 316 | -1441 | -1192 | -1278 | 80 | 18 | 180 | 291 | 1 | 10 | 16 | 4 | 5 | 3 |  | -657 | -180 | -74 | -7 | -8 | -64 | -1 | -32
239 | Fenno-Skan 3 | Light PINT | 33 | 39 | 25 |  | 14 | 19 | 9 | 22 | 28 | 18 | -120 | -82 | -164 |  | 2 | 15 | 24 |  |  |  | 337 | 429 | 280 |  | -89 | -10 | -47 | -2 | -3 | -4 |  |  | 104 | 104 | 104 | 1 | 1 | 1
243 | New 400 kV interconnection line between Serbia and Croatia | Light PINT | 6 | 8 | 2 |  | 5 | 7 | 1 | 4 | 6 | 2 | -44 | -7 | -65 |  | 1 | 5 | 9 |  |  |  | 67 | 85 | 34 |  | -26 | -2 | -22 | -1 | -1 | -1 |  |  | 4 | 4 | 4 | 0 | 0 | 0
244 | Vigy - Uchtelfangen area | TOOT | 142 | 152 | 132 |  | 34 | 38 | 31 | 88 | 99 | 74 | -297 | -276 | -339 | 172 | 4 | 37 | 60 | 2 | 21 | 35 | 1351 | 1535 | 1134 |  | -221 | -44 | -98 | -4 | -6 | -16 | 1045 | 55 | 1429 | 1429 | 1429 | 50 | 50 | 50
247 | AQUIND Interconnector | TOOT | 362 | 370 | 351 |  | 108 | 115 | 100 | 352 | 353 | 352 | -951 | -881 | -1011 | 130 | 12 | 118 | 192 | 2 | 16 | 26 | 5382 | 5391 | 5373 |  | -300 | -98 | -5 | -2 | -2 | -34 | 685 | 40 | 2231 | 2231 | 2231 | 20 | 20 | 20
250 | Merchant line Castasegna (CH) - Mese (IT) | TOOT | 18 | 26 | 14 |  | 9 | 14 | 6 | -5 | 0 | -11 | -81 | -52 | -125 | 25 | 1 | 10 | 16 | 0 | 3 | 5 | -70 | 0 | -165 |  | -37 | -16 | -13 | 0 | 0 | -5 | 128 | 8 | 6 | 6 | 6 | 0 | 0 | 0
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 168 | 196 | 151 |  | 32 | 35 | 29 | 70 | 81 | 62 | -284 | -254 | -278 | 49 | 4 | 35 | 57 | 1 | 6 | 10 | 1 | 1 | 1 |  | -140 | -35 | -23 | -2 | -2 | -13 | 0 | -18
259 | HU-RO | TOOT | 11 | 17 | 5 |  | 7 | 12 | 4 | 5 | 10 | 2 | -61 | -36 | -109 | 36 | 1 | 8 | 12 | 0 | 5 | 7 | 75 | 150 | 26 |  | -26 | -4 | -14 | -1 | -1 | -2 | 121 | 10 | 39 | 39 | 39 | 1 | 1 | 1
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | TOOT | 161 | 166 | 158 |  | 39 | 40 | 39 | 92 | 97 | 84 | -348 | -342 | -354 | -140 | 4 | 43 | 70 | -2 | -17 | -28 | 1409 | 1511 | 1282 |  | -212 | -54 | -53 | -3 | -4 | -19 | -644 | -48 | 956 | 956 | 956 | 30 | 30 | 30
267 | Hansa PowerBridge II | Light PINT | 120 | 129 | 109 |  | 72 | 83 | 61 | 26 | 33 | 21 | -633 | -542 | -732 |  | 8 | 79 | 128 |  |  |  | 398 | 507 | 327 |  | -51 | -68 | -160 | -5 | -7 | -21 |  |  | 56 | 56 | 56 | 1 | 1 | 1
270 | FR-ES project -Aragón-Atlantic Pyrenees | TOOT | 206 | 208 | 203 |  | 107 | 120 | 89 | 131 | 151 | 109 | -941 | -786 | -1056 | 233 | 12 | 117 | 190 | 3 | 29 | 47 | 2019 | 2347 | 1662 |  | -361 | -105 | -44 | -4 | -5 | -37 | 1547 | 80 | 512 | 512 | 512 | 18 | 18 | 18
276 | FR-ES project -Navarra-Landes | PINT | 206 | 208 | 203 |  | 107 | 120 | 89 | 131 | 151 | 109 | -941 | -786 | -1056 | 230 | 12 | 117 | 190 | 3 | 29 | 46 | 2019 | 2347 | 1662 |  | -361 | -105 | -44 | -4 | -5 | -37 | 1558 | 79 | 509 | 509 | 509 | 18 | 18 | 18
280 | FR-BE: Lonny-Achene-Gramme | TOOT | 52 | 56 | 49 |  | 10 | 10 | 8 | 35 | 41 | 29 | -85 | -73 | -93 | 68 | 1 | 11 | 17 | 1 | 8 | 14 | 544 | 634 | 434 |  | -70 | -17 | -24 | -1 | -2 | -6 | 405 | 22 | 0 | 0 | 0 | 0 | 0 | 0
283 | TuNur Italy | PINT | 21 | 38 | 5 | 862 | 368 | 375 | 361 | 765 | 778 | 752 | -3245 | -3187 | -3303 | 238 | 41 | 404 | 654 | 3 | 30 | 48 | 11798 | 11903 | 11694 | 5000 | -1162 | -362 | -56 | -10 | -11 | -127 | 877 | 63 | 12 | 12 | 12 | 0 | 0 | 0
285 | GridLink | TOOT | 233 | 239 | 228 |  | 72 | 83 | 62 | 228 | 235 | 218 | -638 | -548 | -734 | 108 | 8 | 79 | 129 | 1 | 13 | 22 | 3588 | 3601 | 3576 |  | -208 | -66 | -6 | -2 | -2 | -23 | 658 | 36 | 1425 | 1425 | 1425 | 15 | 15 | 15
297 | BRABO III | TOOT | 33 | 38 | 30 |  | 8 | 10 | 6 | 47 | 51 | 40 | -71 | -50 | -85 | 18 | 1 | 9 | 14 | 0 | 2 | 4 | 723 | 787 | 609 |  | -3 | -7 | -18 | 0 | -1 | -2 | 87 | 5 | 83 | 83 | 83 | 1 | 1 | 1
299 | SACOI 3 | TOOT | 121 | 121 | 121 |  | 52 | 54 | 47 | 4 | 6 | 2 | -455 | -415 | -480 | 23 | 6 | 57 | 92 | 0 | 3 | 5 | 56 | 90 | 33 |  | -1911 | -14 | -1294 | -50 | -69 | -14 | 80 | 6 | 321 | 321 | 321 | 7 | 7 | 7
309 | NeuConnect | TOOT | 297 | 302 | 288 |  | 84 | 88 | 80 | 216 | 218 | 215 | -739 | -705 | -775 | 158 | 9 | 92 | 149 | 2 | 20 | 32 | 3428 | 3626 | 3269 |  | -372 | -93 | -97 | -5 | -8 | -33 | 877 | 50 | 756 | 756 | 756 | 11 | 11 | 11
312 | St. Peter (AT) - Tauern (AT) | TOOT | 159 | 168 | 151 |  | 81 | 82 | 80 | 102 | 105 | 100 | -715 | -704 | -727 | -102 | 9 | 89 | 144 | -1 | -13 | -20 | 1573 | 1592 | 1555 |  | -274 | -72 | -62 | -4 | -5 | -26 | -545 | -32 | 1198 | 1198 | 1198 | 19 | 19 | 19
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 103 | 108 | 96 |  | 49 | 53 | 42 | 67 | 69 | 64 | -430 | -369 | -465 | 24 | 5 | 54 | 87 | 0 | 3 | 5 | 1028 | 1054 | 983 |  | -181 | -48 | -37 | -2 | -3 | -17 | 109 | 31 | 698 | 698 | 698 | 11 | 11 | 11
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 4 | 6 | 0 |  | -2 | 3 | -5 | -4 | -2 | -9 | 18 | 43 | -22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | -66 | -25 | -136 |  | -7 | -2 | -19 | -1 | -1 | -1 | 4 | 1 | 6 | 6 | 6 | 0 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 2 | 4 | 1 |  | -2 | 3 | -6 | -4 | -1 | -10 | 18 | 53 | -25 | 5 | 0 | 0 | 0 | 0 | 1 | 1 | -69 | -19 | -160 |  | -11 | -1 | -10 | 0 | -1 | 0 | 13 | 1 | 9 | 9 | 9 | 0 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | TOOT | 112 | 122 | 103 |  | 63 | 68 | 57 | 21 | 25 | 16 | -555 | -500 | -596 | 64 | 7 | 69 | 112 | 1 | 8 | 13 | 321 | 382 | 247 |  | -254 | -68 | -51 | -3 | -4 | -24 | 352 | 21 | 28 | 28 | 28 | 0 | 0 | 0
328 | Interconnector DE-LUX | TOOT | 1 | 2 | 0 |  | -4 | 0 | -6 | 0 | 3 | -3 | 33 | 50 | -1 | -86 | 0 | 0 | 0 | -1 | -11 | -17 | -2 | 43 | -52 |  | -5 | -3 | -1 | 0 | 0 | -1 | -220 | -23 | 0 | 0 | 0 | 0 | 0 | 0
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 352 | 370 | 325 |  | 126 | 132 | 117 | 274 | 288 | 253 | -2831 | -2978 | -2613 | -20 | 357 | 674 | 892 | 0 | -2 | -4 | 5776 | 5371 | 6046 |  | -3728 | -156 | -5563 | -151 | -414 | -61 | 641 | 13 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | TOOT | 27 | 35 | 17 |  | 9 | 12 | 3 | 10 | 14 | 8 | -76 | -28 | -106 | 32 | 1 | 10 | 15 | 0 | 4 | 6 | 161 | 223 | 127 |  | -30 | -3 | -29 | -1 | -2 | -1 | 121 | 9 | 16 | 16 | 16 | 0 | 0 | 0
335 | North Sea Wind Power Hub | Light PINT | 1407 | 1450 | 1364 | 1656 | 859 | 867 | 851 | 3454 | 3510 | 3398 | -7575 | -7501 | -7650 |  | 95 | 944 | 1527 |  |  |  | 53281 | 53711 | 52851 | 14000 | -2510 | -689 | -448 | -31 | -40 | -242 |  |  | 498 | 498 | 498 | 8 | 8 | 8
338 | Adriatic HVDC link | TOOT | 16 | 26 | 8 |  | 6 | 9 | 2 | 10 | 11 | 8 | -51 | -19 | -80 | 16 | 1 | 6 | 10 | 0 | 2 | 3 | 150 | 176 | 125 |  | -13 | -16 | -67 | -2 | -4 | -5 | 180 | 6 | 467 | 467 | 467 | 0 | 0 | 0
339 | Tyrrhenian link | TOOT | 88 | 94 | 81 |  | 49 | 50 | 48 | 40 | 41 | 40 | -433 | -426 | -438 | 79 | 5 | 54 | 87 | 1 | 10 | 16 | 616 | 637 | 603 |  | -158 | -51 | -3 | -1 | -1 | -18 | 350 | 22 | 1526 | 1526 | 1526 | 0 | 0 | 0
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 112 | 140 | 67 |  | 40 | 50 | 24 | 87 | 109 | 52 | -1213 | -1429 | -745 | -76 | 153 | 289 | 382 | -1 | -9 | -15 | 2030 | 1235 | 2599 |  | -2007 | -17 | -4309 | -45 | -277 | -16 | 310 | -6 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | TOOT | 5 | 10 | 0 |  | -1 | 4 | -4 | -2 | 1 | -6 | 10 | 40 | -34 | 21 | 0 | 0 | 0 | 0 | 3 | 4 | -33 | 16 | -92 |  | -16 | -2 | -10 | 0 | -1 | -1 | -59 | 4 | 277 | 277 | 277 | 4 | 4 | 4
342 | Central Balkan Corridor | TOOT | 11 | 17 | 6 |  | 7 | 10 | 5 | 2 | 4 | 0 | -66 | -43 | -89 | 22 | 1 | 8 | 13 | 0 | 3 | 4 | 36 | 61 | -1 |  | -24 | -6 | -11 | 0 | -1 | -2 | 126 | 8 | 17 | 17 | 17 | 0 | 0 | 0
343 | CSE1 New | TOOT | 6 | 11 | 3 |  | 4 | 7 | 2 | 4 | 6 | 1 | -36 | -15 | -61 | -16 | 0 | 4 | 7 | 0 | -2 | -3 | 61 | 100 | 12 |  | -19 | -2 | -17 | -1 | -1 | -1 | 3 | -2 | 2 | 2 | 2 | 0 | 0 | 0
346 | ZuidWest380 NL Oost | TOOT | 5 | 9 | 3 |  | 4 | 7 | 1 | 4 | 5 | 2 | -33 | -6 | -60 | -16 | 0 | 4 | 7 | 0 | -2 | -3 | 55 | 83 | 34 |  | -15 | -2 | -10 | 0 | -1 | -1 | -90 | -5 | 0 | 0 | 0 | 0 | 0 | 0
349 | MaresConnect | TOOT | 91 | 96 | 83 |  | 32 | 35 | 29 | 95 | 101 | 90 | -285 | -252 | -309 | 6 | 4 | 35 | 57 | 0 | 1 | 1 | 1455 | 1544 | 1367 |  | -45 | -21 | -41 | -1 | -1 | -7 | 61 | 2 | 430 | 430 | 430 | 8 | 8 | 8
350 | South Balkan Corridor | TOOT | 4 | 7 | 1 |  | 0 | 4 | -3 | -2 | -1 | -2 | -2 | 30 | -35 | 25 | 0 | 0 | 0 | 0 | 3 | 5 | -24 | -22 | -26 |  | -16 | -16 | -45 | -1 | -3 | -6 | -51 | 5 | 19 | 19 | 19 | 0 | 0 | 0
375 | Lienz (AT) - Veneto region (IT) 220 kV | TOOT | 71 | 82 | 59 |  | 37 | 41 | 31 | 10 | 13 | 7 | -325 | -272 | -364 | 25 | 4 | 41 | 66 | 0 | 3 | 5 | 156 | 196 | 108 |  | -154 | -44 | -27 | -2 | -2 | -15 | 135 | 8 | 32 | 32 | 32 | 0 | 0 | 0
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | Light PINT | 7 | 11 | 4 |  | 4 | 6 | 0 | 5 | 8 | 2 | -31 | -3 | -56 |  | 0 | 4 | 6 |  |  |  | 76 | 128 | 28 |  | -19 | -1 | -21 | -1 | -1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | TOOT | 28 | 33 | 22 |  | 9 | 12 | 5 | 37 | 42 | 30 | -82 | -46 | -107 | 5 | 1 | 10 | 17 | 0 | 1 | 1 | 564 | 647 | 464 |  | -25 | -6 | -10 | 0 | -1 | -2 | 40 | 1 | 17 | 17 | 17 | 0 | 0 | 0
378 | Transformer Gatica | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 356 | 457 | 290 |  | 44 | 95 | -64 | 179 | 229 | 147 | -655 | -538 | -568 | -8 | 5 | 49 | 79 | 0 | -1 | -2 | 2 | 2 | 1 |  | -291 | -82 | -28 | -3 | -3 | -29 | -128 | -4
1039 | SE North-south long-term reinforcements | PINT | 26 | 28 | 24 |  | 21 | 24 | 17 | 3 | 4 | 3 | -181 | -152 | -212 |  | 2 | 23 | 37 |  |  |  | 49 | 65 | 38 |  | -161 | -18 | -83 | -3 | -5 | -7 |  |  | 95 | 95 | 95 | 0 | 0 | 0
1040 | LirIC | TOOT | 76 | 85 | 69 |  | 28 | 36 | 23 | 85 | 92 | 80 | -248 | -202 | -320 | 12 | 3 | 31 | 50 | 0 | 2 | 3 | 1313 | 1414 | 1244 |  | -52 | -20 | -28 | 0 | 0 | -7 | 163 | 5 | 35 | 35 | 35 | 1 | 1 | 1
1041 | GREGY Green Energy Interconnector | TOOT | 262 | 300 | 208 |  | 96 | 99 | 94 | -2 | 2 | -8 | -851 | -833 | -869 | 475 | 11 | 106 | 171 | 6 | 59 | 96 | -32 | 33 | -120 |  | -371 | -128 | -28 | -2 | -1 | -45 | 1506 | 124 | 2962 | 2962 | 2962 | 29 | 29 | 29
1046 | Finnish North-South reinforcement | PINT | 391 | 391 | 391 |  | 49 | 49 | 49 | 480 | 480 | 480 | 436 | 436 | 436 | -7 | 5 | 54 | 88 | 0 | -1 | -1 | 7505 | 7505 | 7505 |  | -2 | 0 | -2 | 0 | 0 | 0 | -495 | -25 | 0 | 0 | 0 | 0 | 0 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 40 | 49 | 30 |  | 18 | 24 | 13 | 3 | 4 | 1 | -158 | -112 | -209 | 25 | 2 | 20 | 32 | 0 | 3 | 5 | 43 | 62 | 15 |  | -64 | -18 | -10 | -1 | -1 | -6 | 52 | 6 | 3 | 3 | 3 | 0 | 0 | 0
1049 | Cronos Energy Ltd | PINT | 230 | 234 | 224 |  | 58 | 62 | 55 | 181 | 183 | 181 | -516 | -486 | -543 | -8 | 6 | 64 | 104 | 0 | -1 | -2 | 2791 | 2812 | 2775 |  | -250 | -65 | -53 | -3 | -5 | -23 | -914 | -27 | 162 | 162 | 162 | 2 | 2 | 2
1050 | Tarchon Energy Ltd | TOOT | 281 | 290 | 269 |  | 80 | 83 | 77 | 207 | 210 | 204 | -709 | -675 | -734 | 105 | 9 | 88 | 143 | 1 | 13 | 21 | 3177 | 3215 | 3107 |  | -323 | -83 | -76 | -5 | -6 | -29 | 542 | 33 | 229 | 229 | 229 | 2 | 2 | 2
1052 | Lienz (AT) - Malta (AT) - Obersielach (AT) | TOOT | 247 | 276 | 217 | 165 | 201 | 222 | 181 | 235 | 241 | 230 | -1776 | -1597 | -1954 | 56 | 22 | 221 | 358 | 1 | 7 | 11 | 3625 | 3682 | 3569 | 2000 | -759 | -209 | -139 | -9 | -12 | -74 | 330 | 20 | 43 | 43 | 43 | 1 | 1 | 1
1054 | 220-kV Westtirol (AT) - Zell/Ziller (AT) | TOOT | 36 | 38 | 32 |  | 17 | 17 | 16 | 27 | 29 | 26 | -146 | -140 | -153 | 40 | 2 | 18 | 29 | 1 | 5 | 8 | 415 | 448 | 392 |  | -60 | -15 | -12 | -1 | -1 | -5 | 189 | 13 | 198 | 198 | 198 | 3 | 3 | 3
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 121 | 130 | 112 |  | 51 | 55 | 47 | -3 | 1 | -9 | -453 | -417 | -481 | 571 | 6 | 56 | 91 | 7 | 71 | 115 | -40 | 12 | -139 |  | -212 | -51 | -27 | -2 | -2 | -19 | 1692 | 147 | 835 | 835 | 835 | 8 | 8 | 8
1058 | HVDC Interconnector DE-CH | Light PINT | 95 | 108 | 86 |  | 40 | 46 | 33 | 60 | 65 | 53 | -356 | -295 | -405 |  | 4 | 44 | 72 |  |  |  | 926 | 1018 | 803 |  | -126 | -38 | -17 | -1 | -2 | -13 |  |  | 100 | 100 | 100 | 2 | 2 | 2
1059 | Southern Italy | TOOT | 9 | 13 | 5 |  | 3 | 4 | 1 | 8 | 10 | 6 | -24 | -12 | -33 | 5 | 0 | 3 | 5 | 0 | 1 | 1 | 128 | 146 | 97 |  | -3 | -6 | -16 | 0 | -1 | -2 | 97 | 2 | 212 | 212 | 212 | 0 | 0 | 0
1066 | Bulgaria - Turkey | Light PINT | 148 | 155 | 141 |  | 137 | 141 | 133 | 7 | 9 | 5 | -1211 | -1175 | -1247 |  | 15 | 151 | 244 |  |  |  | 114 | 134 | 81 |  | -962 | -13 | -981 | -34 | -66 | -6 |  |  | 59 | 59 | 59 | 0 | 0 | 0
1067 | New AC 400 kV interconnection line Greece - Turkey | Light PINT | 89 | 94 | 84 |  | 89 | 108 | 76 | 5 | 6 | 4 | -787 | -672 | -951 |  | 10 | 98 | 159 |  |  |  | 71 | 88 | 55 |  | -518 | -11 | -517 | -18 | -35 | -4 |  |  | 79 | 79 | 79 | 1 | 1 | 1
1068 | LaSGo Link | PINT | 45 | 48 | 40 |  | 25 | 28 | 20 | 20 | 22 | 17 | -223 | -177 | -251 | 9 | 3 | 28 | 45 | 0 | 1 | 2 | 312 | 347 | 269 |  | -673 | -17 | -416 | -16 | -23 | -12 | 122 | 6 | 11 | 11 | 11 | 0 | 0 | 0
1074 | Pannonian Corridor | TOOT | 12 | 16 | 9 |  | 8 | 11 | 4 | 2 | 3 | 2 | -67 | -35 | -100 | 14 | 1 | 8 | 14 | 0 | 2 | 3 | 36 | 39 | 34 |  | -21 | -3 | -14 | -1 | -1 | -1 | 46 | 4 | 18 | 18 | 18 | 0 | 0 | 0
1085 | Malta-Italy Cable Link No.2 | TOOT | 27 | 35 | 18 |  | 16 | 19 | 13 | 6 | 11 | 1 | -139 | -115 | -167 | 11 | 2 | 17 | 28 | 0 | 1 | 2 | 95 | 169 | 21 |  | -49 | -15 | -7 | -1 | -1 | -5 | 33 | 3 | 27 | 27 | 27 | 0 | 0 | 0
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 8 | 12 | 3 | 84 | 17 | 19 | 16 | 135 | 141 | 129 | -152 | -139 | -169 | 0 | 2 | 19 | 31 | 0 | 0 | 0 | 2081 | 2170 | 1964 | 700 | -385 | -6 | -257 | -10 | -14 | -5 | 76 | 3 | 2 | 2 | 2 | 0 | 0 | 0
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | TOOT | 23 | 29 | 17 | 70 | 16 | 24 | 10 | 134 | 137 | 133 | -143 | -90 | -211 | 2 | 2 | 18 | 29 | 0 | 0 | 0 | 2061 | 2081 | 2040 | 1000 | -189 | -6 | -115 | -5 | -6 | -4 | 41 | 3 | 68 | 68 | 68 | 1 | 1 | 1
1092 | TritonLink: offshore hybrid HVDC interconnector Belgium – Denmark | TOOT | 527 | 542 | 507 | 412 | 259 | 265 | 255 | 1063 | 1087 | 1044 | -2281 | -2250 | -2336 | 48 | 29 | 284 | 460 | 1 | 6 | 10 | 16333 | 16637 | 15906 | 4000 | -718 | -202 | -114 | -8 | -11 | -71 | 122 | 13 | 368 | 368 | 368 | 6 | 6 | 6
1094 | Estlink 3 | TOOT | 39 | 44 | 34 |  | 34 | 42 | 24 | 6 | 6 | 6 | -295 | -215 | -368 | 17 | 4 | 37 | 60 | 0 | 2 | 3 | 90 | 93 | 88 |  | -1579 | -11 | -1021 | -40 | -55 | -19 | 129 | 6 | 7 | 7 | 7 | 0 | 0 | 0
1095 | Aurora line 2 (4th AC Finland-Sweden north) | TOOT | 35 | 40 | 31 |  | 8 | 11 | 6 | 29 | 32 | 26 | -75 | -57 | -93 | 3 | 1 | 9 | 15 | 0 | 0 | 1 | 442 | 501 | 397 |  | -77 | -5 | -48 | -2 | -3 | -2 | 0 | 1 | 36 | 36 | 36 | 0 | 0 | 0
1096 | Beznau - Mettlen | Light TOOT | 66 | 84 | 50 |  | 34 | 46 | 23 | 43 | 44 | 43 | -296 | -206 | -408 |  | 4 | 37 | 60 |  |  |  | 668 | 684 | 652 |  | -139 | -46 | -6 | -1 | -1 | -16 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1097 | Upgrade to Konti-Skan | PINT | 104 | 112 | 99 |  | 57 | 65 | 47 | 41 | 43 | 37 | -500 | -413 | -575 | 63 | 6 | 62 | 101 | 1 | 8 | 13 | 626 | 660 | 570 |  | -141 | -51 | -10 | -1 | -2 | -17 | 294 | 13 | 77 | 77 | 77 | 1 | 1 | 1
1098 | Offshore Wind LT 2 | TOOT | 9 | 13 | 7 | 45 | 13 | 17 | 10 | 74 | 78 | 70 | -119 | -88 | -146 | 19 | 1 | 15 | 24 | 0 | 2 | 4 | 1139 | 1202 | 1067 | 700 | -224 | -7 | -143 | -6 | -8 | -4 | 132 | 7 | 44 | 44 | 44 | 1 | 1 | 1
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | TOOT | 83 | 83 | 83 |  | 53 | 62 | 49 | 30 | 33 | 24 | -471 | -429 | -548 | 54 | 6 | 59 | 95 | 1 | 7 | 11 | 454 | 503 | 376 |  | -194 | -63 | -2 | -2 | -2 | -22 | 392 | 20 | 29 | 29 | 29 | 0 | 0 | 0
1102 | Mettlen - Ulrichen | Light TOOT | 8 | 17 | 3 |  | 3 | 8 | 0 | 3 | 3 | 2 | -27 | 1 | -67 |  | 0 | 3 | 5 |  |  |  | 43 | 54 | 32 |  | -17 | -3 | -10 | 0 | -1 | -1 |  |  | 42 | 42 | 42 | 1 | 1 | 1
1103 | Bickigen - Chippis | Light TOOT | 34 | 40 | 30 |  | 17 | 20 | 16 | 30 | 31 | 29 | -152 | -138 | -175 |  | 2 | 19 | 31 |  |  |  | 462 | 477 | 444 |  | -51 | -17 | -6 | 0 | 0 | -6 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1104 | Bauler - Roost | TOOT | 0 | 1 | 0 |  | -5 | 0 | -8 | -2 | 0 | -5 | 41 | 72 | 1 | -41 | 0 | 0 | 0 | -1 | -5 | -8 | -31 | 5 | -73 |  | -15 | -4 | -4 | 0 | 0 | -1 | 10 | -9 | 0 | 0 | 0 | 0 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 56 | 67 | 46 |  | 28 | 33 | 22 | 4 | 5 | 2 | -244 | -197 | -292 | -49 | 3 | 30 | 49 | -1 | -6 | -10 | 61 | 84 | 38 |  | -91 | -29 | -3 | -1 | -1 | -10 | 236 | -29 | 240 | 240 | 240 | 1 | 1 | 1
1106 | Bornholm Energy Island (BEI) | TOOT | 127 | 133 | 121 | 466 | 169 | 180 | 154 | 647 | 661 | 636 | -1492 | -1360 | -1586 | -21 | 19 | 186 | 301 | 0 | -3 | -4 | 9948 | 10125 | 9687 | 3000 | -482 | -151 | -25 | -4 | -5 | -53 | -90 | -6 | 233 | 233 | 233 | 3 | 3 | 3
1109 | Basilicata - Campania reinforcements | TOOT | 23 | 29 | 18 |  | 16 | 18 | 12 | 11 | 15 | 4 | -142 | -106 | -163 | 11 | 2 | 18 | 29 | 0 | 1 | 2 | 168 | 225 | 55 |  | -40 | -14 | -2 | 0 | 0 | -5 | -10 | 1 | 42 | 42 | 42 | 0 | 0 | 0
1110 | Sicily - Calabria | TOOT | 7 | 17 | 1 |  | 0 | 2 | -2 | 6 | 10 | 3 | -1 | 17 | -15 | -16 | 0 | 0 | 0 | 0 | -2 | -3 | 98 | 159 | 53 |  | -26 | -3 | -4 | 0 | 0 | -1 | 30 | -3 | 65 | 65 | 65 | 0 | 0 | 0
1112 | GRITA 2 | TOOT | 116 | 118 | 114 |  | 67 | 68 | 65 | 40 | 42 | 38 | -587 | -570 | -603 | 83 | 7 | 73 | 118 | 1 | 10 | 17 | 615 | 661 | 577 |  | -220 | -67 | -16 | -2 | -2 | -23 | 304 | 23 | 46 | 46 | 46 | 0 | 0 | 0
1121 | 220-kV Hessenberg (AT) - Weißenbach (AT) | TOOT | 0 | 0 | 0 | 63 | 17 | 19 | 15 | 58 | 62 | 55 | -150 | -132 | -167 | -11 | 2 | 19 | 30 | 0 | -1 | -2 | 902 | 963 | 841 | 600 | -48 | -16 | -1 | 0 | 0 | -5 | -78 | -4 | 3 | 3 | 3 | 0 | 0 | 0
1122 | Offshore Wind farm connection Centre Manche 1 | TOOT | 1 | 5 | 0 | 237 | 70 | 72 | 69 | 289 | 293 | 285 | -618 | -605 | -636 | 87 | 8 | 77 | 125 | 1 | 11 | 17 | 4447 | 4514 | 4340 | 1050 | -155 | -49 | -6 | -1 | -1 | -17 | 583 | 32 | 138 | 138 | 138 | 4 | 4 | 4
1123 | Offshore Wind farm connection Centre Manche 2 | TOOT | 13 | 19 | 9 | 277 | 86 | 91 | 80 | 356 | 373 | 341 | -758 | -704 | -799 | 76 | 10 | 95 | 153 | 1 | 9 | 15 | 5468 | 5711 | 5193 | 1250 | -197 | -63 | -6 | -2 | -2 | -22 | 498 | 28 | 164 | 164 | 164 | 5 | 5 | 5
1124 | Offshore Wind Connection South Britanny | TOOT | 0 | 0 | 0 | 58 | 14 | 16 | 13 | 68 | 70 | 66 | -127 | -117 | -145 | 13 | 2 | 16 | 26 | 0 | 2 | 3 | 1048 | 1068 | 1012 | 250 | -33 | -12 | -4 | 0 | 0 | -4 | 87 | 5 | 33 | 33 | 33 | 1 | 1 | 1
1125 | Offshore Wind Connection Occitanie | TOOT | 0 | 0 | 0 | 60 | 15 | 16 | 13 | 65 | 69 | 61 | -130 | -119 | -145 | 12 | 2 | 16 | 26 | 0 | 2 | 2 | 1004 | 1068 | 932 | 250 | -45 | -13 | -7 | -1 | -1 | -4 | 9 | 2 | 33 | 33 | 33 | 1 | 1 | 1
1126 | Offshore Wind Connection PACA | TOOT | 0 | 0 | 0 | 59 | 14 | 16 | 13 | 65 | 69 | 61 | -127 | -117 | -145 | 2 | 2 | 16 | 26 | 0 | 0 | 0 | 1002 | 1068 | 925 | 250 | -32 | -12 | -5 | 0 | 0 | -4 | -70 | -2 | 33 | 33 | 33 | 1 | 1 | 1
1127 | Offshore Wind Connection South Atlantic Oléron 1 | TOOT | 14 | 27 | 4 | 261 | 84 | 89 | 80 | 326 | 341 | 313 | -744 | -704 | -786 | 106 | 9 | 93 | 150 | 1 | 13 | 21 | 5015 | 5193 | 4865 | 1250 | -217 | -62 | -31 | -2 | -3 | -22 | 618 | 36 | 164 | 164 | 164 | 5 | 5 | 5
1134 | GiLA | PINT | 79 | 79 | 79 |  | 17 | 17 | 17 | 71 | 71 | 71 | -152 | -152 | -152 | 63 | 2 | 19 | 31 | 1 | 8 | 13 | 1398 | 1398 | 1398 |  | -54 | -17 | -2 | 0 | 0 | -6 | 518 | 25 | 0 | 0 | 0 | 0 | 0 | 0
1138 | 400 kV OHL Suceava (RO) - Balti (MD) | TOOT | 14 | 23 | 7 |  | 7 | 16 | 3 | 4 | 6 | 3 | -66 | -28 | -138 | -52 | 1 | 8 | 13 | -1 | -6 | -10 | 59 | 84 | 45 |  | -13 | -2 | -6 | 0 | -1 | -1 | 85 | -7 | 114 | 114 | 114 | 2 | 2 | 2
1139 | 380-kV Westtirol (AT) – Zell/Ziller (AT) | PINT | 44 | 44 | 44 | 143 | 68 | 75 | 65 | 167 | 168 | 165 | -603 | -572 | -662 | -63 | 8 | 75 | 121 | -1 | -8 | -13 | 2562 | 2600 | 2522 | 1600 | -223 | -58 | -51 | -3 | -4 | -21 | -334 | -21 | 8 | 8 | 8 | 0 | 0 | 0
1140 | 380-kV St. Peter (AT) - Dürnrohr (AT) | PINT | 41 | 47 | 37 | 124 | 60 | 65 | 56 | 164 | 169 | 162 | -530 | -493 | -573 | -39 | 7 | 66 | 107 | 0 | -5 | -8 | 2526 | 2594 | 2460 | 1500 | -179 | -50 | -26 | -2 | -3 | -18 | -242 | -14 | 44 | 44 | 44 | 1 | 1 | 1
1145 | 380-kV Obersielach (AT) - Hessenberg (AT) | TOOT | 7 | 13 | 2 | 200 | 68 | 73 | 64 | 212 | 214 | 210 | -604 | -569 | -646 | 12 | 8 | 75 | 122 | 0 | 1 | 2 | 3260 | 3331 | 3221 | 2000 | -216 | -58 | -44 | -3 | -4 | -20 | -33 | 1 | 9 | 9 | 9 | 0 | 0 | 0
1153 | PST romands | TOOT | 74 | 78 | 66 |  | 40 | 48 | 34 | 7 | 12 | 3 | -351 | -301 | -427 | 93 | 4 | 44 | 71 | 1 | 12 | 19 | 108 | 182 | 42 |  | -197 | -53 | -26 | -2 | -3 | -19 | 585 | 30 | 662 | 662 | 662 | 23 | 23 | 23
1155 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT) | TOOT | 12 | 15 | 5 | 345 | 119 | 122 | 113 | 359 | 362 | 357 | -1049 | -998 | -1079 | 50 | 13 | 131 | 211 | 1 | 6 | 10 | 5524 | 5627 | 5473 | 2000 | -353 | -97 | -63 | -4 | -6 | -34 | 163 | 14 | 9 | 9 | 9 | 0 | 0 | 0
1156 | 380-kV Greater Vienna (AT) - Hessenberg (AT) | TOOT | 8 | 13 | 3 | 273 | 92 | 97 | 89 | 285 | 287 | 283 | -815 | -783 | -855 | 24 | 10 | 102 | 164 | 0 | 3 | 5 | 4384 | 4460 | 4342 | 2500 | -279 | -76 | -52 | -3 | -5 | -27 | 36 | 5 | 9 | 9 | 9 | 0 | 0 | 0
1157 | HG North Tyrrhenian Corridor | TOOT | 49 | 51 | 46 |  | 24 | 31 | 17 | 36 | 38 | 34 | -208 | -153 | -272 | 135 | 3 | 26 | 42 | 2 | 17 | 27 | 549 | 586 | 530 |  | -66 | -19 | -7 | -1 | -1 | -7 | 608 | 38 | 2256 | 2256 | 2256 | 0 | 0 | 0
1158 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT) | PINT | 7 | 13 | 2 | 200 | 68 | 73 | 64 | 212 | 214 | 210 | -604 | -569 | -646 | 36 | 8 | 75 | 122 | 0 | 4 | 7 | 3260 | 3331 | 3221 | 2000 | -216 | -58 | -44 | -3 | -4 | -20 | 129 | 10 | 8 | 8 | 8 | 0 | 0 | 0
1159 | 220-kV Bisamberg (AT) – Wien Südost (AT) | TOOT | 6 | 15 | 0 | 24 | 12 | 17 | 7 | 31 | 33 | 28 | -110 | -59 | -151 | 1 | 1 | 14 | 22 | 0 | 0 | 0 | 478 | 505 | 428 | 500 | -40 | -9 | -16 | -1 | -1 | -3 | -9 | 0 | 4 | 4 | 4 | 0 | 0 | 0
1161 | Offshore Wind Connection South Atlantic Oléron 2 | TOOT | 11 | 12 | 8 | 266 | 83 | 87 | 76 | 336 | 345 | 326 | -728 | -672 | -764 | 123 | 9 | 91 | 147 | 2 | 15 | 25 | 5257 | 5282 | 5231 | 1200 | -199 | -59 | -21 | -2 | -2 | -21 | 704 | 41 | 157 | 157 | 157 | 5 | 5 | 5
1162 | Offshore Wind Connection Fécamp-Grand Large 1 | TOOT | 23 | 26 | 19 | 438 | 135 | 142 | 126 | 563 | 580 | 548 | -1187 | -1112 | -1249 | 96 | 15 | 148 | 239 | 1 | 12 | 19 | 8654 | 8889 | 8341 | 2000 | -335 | -99 | -34 | -3 | -4 | -35 | 476 | 31 | 261 | 261 | 261 | 9 | 9 | 9
1163 | Offshore Wind Connection Fécamp-Grand Large 2 | TOOT | 23 | 26 | 19 | 438 | 135 | 142 | 126 | 563 | 580 | 548 | -1187 | -1112 | -1249 | 90 | 15 | 148 | 239 | 1 | 11 | 18 | 8654 | 8889 | 8341 | 2000 | -335 | -99 | -34 | -3 | -4 | -35 | 476 | 31 | 263 | 263 | 263 | 9 | 9 | 9
1164 | Offshore Wind Connection Golfe de Lion Centre | TOOT | 23 | 26 | 19 | 438 | 135 | 142 | 126 | 563 | 580 | 548 | -1187 | -1112 | -1249 | 59 | 15 | 148 | 239 | 1 | 7 | 12 | 8654 | 8889 | 8341 | 2000 | -335 | -99 | -34 | -3 | -4 | -35 | -132 | 6 | 262 | 262 | 262 | 9 | 9 | 9
1165 | Offshore Wind Connection Golfe de Gascogne Sud | TOOT | 11 | 12 | 8 | 266 | 83 | 87 | 76 | 336 | 345 | 326 | -728 | -672 | -764 | 86 | 9 | 91 | 147 | 1 | 11 | 17 | 5257 | 5282 | 5231 | 1200 | -199 | -59 | -21 | -2 | -2 | -21 | 593 | 32 | 157 | 157 | 157 | 5 | 5 | 5
1166 | HG Adriatic Corridor | PINT | 37 | 44 | 27 |  | 20 | 25 | 17 | 35 | 36 | 34 | -176 | -148 | -224 | 94 | 2 | 22 | 36 | 1 | 12 | 19 | 540 | 556 | 524 |  | -62 | -19 | -6 | -1 | -1 | -7 | 373 | 26 | 88 | 88 | 88 | 0 | 0 | 0
1167 | HG Central link | TOOT | 2 | 4 | 0 |  | -3 | 0 | -6 | -4 | 0 | -8 | 26 | 52 | 2 | 24 | 0 | 0 | 0 | 0 | 3 | 5 | -56 | -2 | -118 |  | -11 | -2 | -7 | 0 | 0 | -1 | 131 | 6 | 191 | 191 | 191 | 0 | 0 | 0
1168 | HG Ionian-Tyrrhenian Corridor | TOOT | 9 | 15 | 3 |  | 4 | 7 | 1 | 7 | 14 | 1 | -39 | -8 | -65 | 37 | 0 | 5 | 8 | 0 | 5 | 7 | 108 | 214 | 8 |  | -18 | -4 | -5 | 0 | 0 | -1 | 132 | 9 | 0 | 0 | 0 | 0 | 0 | 0
1169 | SAPEI 2 | PINT | 23 | 31 | 17 |  | 16 | 20 | 11 | 10 | 16 | 4 | -141 | -98 | -178 | 17 | 2 | 18 | 28 | 0 | 2 | 3 | 154 | 247 | 54 |  | -50 | -15 | -6 | -1 | -1 | -5 | 36 | 3 | 16 | 16 | 16 | 0 | 0 | 0
1171 | Interconnection IT-CH | PINT | 105 | 118 | 88 |  | 61 | 64 | 56 | 4 | 9 | 2 | -538 | -495 | -562 | 81 | 7 | 67 | 108 | 1 | 10 | 16 | 67 | 132 | 33 |  | -265 | -85 | -7 | -2 | -2 | -30 | 437 | 27 | 4 | 4 | 4 | 0 | 0 | 0
1182 | EHV S/S Thesprotias and its connection to the 400 kV System | Light PINT | 7 | 15 | 1 |  | 6 | 11 | 2 | 4 | 13 | 0 | -55 | -14 | -98 | 23 | 1 | 7 | 11 | 0 | 3 | 5 | 68 | 195 | -4 |  | -29 | -5 | -15 | -1 | -1 | -2 | 78 | 6 | 0 | 0 | 0 | 0 | 0 | 0
1183 | New interconnection line 400 kV Greece - Albania | Light PINT | 6 | 10 | 1 |  | 5 | 8 | 1 | 3 | 5 | 1 | -40 | 6 | -69 | -14 | 1 | 6 | 9 | 0 | -2 | -3 | 40 | 78 | 12 |  | -6 | -3 | 0 | 0 | 0 | -1 | -44 | -4 | 0 | 0 | 0 | 0 | 0 | 0
1185 | South Coast Offshore Transmission Project | TOOT | 4 | 8 | 0 | 64 | 24 | 28 | 20 | 82 | 89 | 77 | -216 | -174 | -246 | 0 | 3 | 27 | 44 | 0 | 0 | 0 | 1252 | 1386 | 1177 | 800 | -70 | -14 | -46 | -2 | -2 | -5 | 14 | 0 | 30 | 30 | 30 | 1 | 1 | 1
1192 | HansaLink - Phase 1 | PINT | 393 | 404 | 382 | 271 | 207 | 208 | 205 | 638 | 646 | 629 | -1821 | -1808 | -1834 | -44 | 23 | 227 | 367 | -1 | -5 | -9 | 9838 | 9893 | 9782 | 2000 | -654 | -176 | -126 | -8 | -11 | -62 | -289 | -16 | 383 | 383 | 383 | 5 | 5 | 5
1193 | HansaLink - Phase 2 | PINT | 8 | 10 | 6 | 258 | 88 | 89 | 86 | 323 | 327 | 320 | -775 | -756 | -788 | -11 | 10 | 97 | 156 | 0 | -1 | -2 | 4972 | 5033 | 4878 | 2000 | -194 | -57 | -21 | -2 | -2 | -20 | -92 | -4 | 383 | 383 | 383 | 5 | 5 | 5
1197 | NU-Link Interconnector | PINT | 206 | 213 | 198 |  | 54 | 57 | 49 | 165 | 170 | 160 | -474 | -436 | -502 | 63 | 6 | 59 | 96 | 1 | 8 | 13 | 2531 | 2601 | 2431 |  | -227 | -59 | -50 | -3 | -4 | -21 | 453 | 21 | 140 | 140 | 140 | 4 | 4 | 4
1200 | Hybrid interconnector Norway-Sørvest F Windfarm-Continent (DK, DE or BE) | PINT | 348 | 359 | 338 |  | 196 | 197 | 196 | 82 | 92 | 72 | -1732 | -1725 | -1740 | 68 | 22 | 216 | 349 | 1 | 8 | 14 | 1282 | 1435 | 1129 |  | -568 | -165 | -78 | -6 | -8 | -58 | 622 | 31 | 263 | 263 | 263 | 4 | 4 | 4
1201 | Reinvestment of Skagerrak 1 and 2 | PINT | 135 | 143 | 127 |  | 64 | 64 | 64 | 71 | 79 | 64 | -563 | -562 | -564 | 24 | 7 | 70 | 114 | 0 | 3 | 5 | 1109 | 1224 | 994 |  | -179 | -47 | -43 | -2 | -4 | -16 | 569 | 20 | 98 | 98 | 98 | 1 | 1 | 1
1202 | Increased capacity Norway-Finland, Back-to-Back | PINT | 18 | 20 | 17 |  | 6 | 8 | 4 | 13 | 18 | 10 | -53 | -38 | -68 | 1 | 1 | 7 | 11 | 0 | 0 | 0 | 200 | 273 | 152 |  | -13 | -3 | -5 | 0 | 0 | -1 | 63 | 3 | 25 | 25 | 25 | 0 | 0 | 0
1203 | Offshore Wind Connection Bretagne Nord-Ouest | PINT | 14 | 24 | 4 | 250 | 80 | 86 | 76 | 315 | 326 | 303 | -702 | -672 | -762 | 101 | 9 | 88 | 142 | 1 | 13 | 20 | 4834 | 4966 | 4715 | 1200 | -202 | -61 | -17 | -2 | -2 | -21 | 636 | 36 | 157 | 157 | 157 | 5 | 5 | 5
1207 | 380kV Niederstedem-Bertrange/Bofferdange | PINT | 4 | 8 | 2 |  | 3 | 4 | 0 | 2 | 3 | 0 | -22 | 2 | -35 | 42 | 0 | 3 | 5 | 1 | 5 | 8 | 25 | 49 | -6 |  | -2 | 0 | -8 | 0 | 0 | 0 | -13 | 9 | 0 | 0 | 0 | 0 | 0 | 0
1208 | Medlink | PINT | 545 | 568 | 526 | 1124 | 662 | 691 | 619 | 1469 | 1509 | 1428 | -5839 | -5455 | -6096 | 331 | 74 | 728 | 1177 | 4 | 41 | 67 | 22979 | 23091 | 22866 | 9016 | -2135 | -668 | -86 | -19 | -19 | -234 | 915 | 81 | 5 | 5 | 5 | 0 | 0 | 0
1209 | Latvia and Lithuania cross-border strengthening project | PINT | 16 | 16 | 15 |  | 3 | 5 | 2 | 23 | 23 | 23 | -28 | -15 | -41 | -3 | 0 | 3 | 6 | 0 | 0 | -1 | 356 | 357 | 355 |  | -10 | -5 | -3 | 0 | 0 | -2 | -34 | -1 | 2 | 2 | 2 | 0 | 0 | 0
1210 | APOLLO-LINK | Light PINT | 547 | 568 | 526 |  | 299 | 313 | 287 | 184 | 201 | 174 | -2634 | -2530 | -2756 |  | 33 | 328 | 531 |  |  |  | 2694 | 2727 | 2661 |  | -1325 | -419 | -36 | -11 | -11 | -147 |  |  | 171 | 171 | 171 | 1 | 1 | 1
1211 | Baltic WindConnector (BWC) | PINT | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6 | 0 | 0 | 0 | 0 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1213 | Offshore hybrid Interconnector (DE-NL) | Light PINT | 69 | 75 | 60 |  | 29 | 33 | 27 | 46 | 53 | 41 | -259 | -237 | -290 |  | 3 | 32 | 52 |  |  |  | 716 | 821 | 629 |  | -90 | -20 | -37 | -2 | -3 | -7 |  |  | 32 | 32 | 32 | 0 | 0 | 0
1214 | Hybrid Interconnector Denmark-Germany | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1215 | Xlinks Morocco - Germany | PINT | 1585 | 1622 | 1547 | 148 | 534 | 534 | 534 | 1733 | 1733 | 1733 | -4708 | -4707 | -4710 | 837 | 59 | 587 | 949 | 11 | 104 | 169 | 26676 | 26954 | 26398 | 15200 | -1558 | -430 | -270 | -19 | -25 | -151 | 7060 | 282 | 36 | 36 | 36 | 0 | 0 | 0
1216 | High-Voltage Direct Current Interconnector Project Romania-Hungary | PINT | 15 | 18 | 13 |  | 11 | 13 | 7 | 1 | 2 | -1 | -93 | -59 | -119 | -82 | 1 | 12 | 19 | -1 | -10 | -17 | 17 | 38 | -22 |  | -6 | -3 | -2 | 0 | 0 | -1 | 161 | -37 | 39 | 39 | 39 | 1 | 1 | 1
1217 | Further Development of Offshore Renewables (MOG 3) | Light PINT | 24 | 34 | 19 | 367 | 107 | 115 | 99 | 462 | 464 | 460 | -946 | -869 | -1012 |  | 12 | 118 | 191 |  |  |  | 7201 | 7379 | 7006 |  | -299 | -85 | -42 | -3 | -4 | -30 |  |  | 180 | 180 | 180 | 3 | 3 | 3
1218 | Hybrid HVDC Interconnector BE-NL | Light PINT | 4 | 4 | 3 |  | 1 | 2 | 0 | -1 | 0 | -2 | -9 | 3 | -20 |  | 0 | 1 | 2 |  |  |  | -16 | 4 | -37 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1219 | Bofferdange- Bertrange | Light PINT | 17 | 21 | 14 |  | 8 | 12 | 4 | 9 | 16 | 3 | -71 | -32 | -109 |  | 1 | 9 | 14 |  |  |  | 143 | 246 | 43 |  | -29 | -7 | -13 | -1 | -1 | -2 |  |  | 17 | 17 | 17 | 0 | 0 | 0
1220 | Offshore Wind Connection Viana do Castelo | TOOT | 1 | 3 | 0 | 113 | 24 | 26 | 22 | 156 | 159 | 153 | -211 | -195 | -227 | 21 | 3 | 26 | 43 | 0 | 3 | 4 | 2396 | 2424 | 2376 | 2000 | -49 | -10 | -14 | -1 | -1 | -3 | 197 | 11 | 75 | 75 | 75 | 1 | 1 | 1
1221 | Offshore Wind Connection Leixões | TOOT | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 143 | 143 | 1 | 1 | 1
1222 | Offshore Wind Connection Figueira da Foz (North) | TOOT | 2 | 10 | 0 | 137 | 28 | 33 | 24 | 190 | 194 | 184 | -246 | -213 | -289 | 16 | 3 | 31 | 50 | 0 | 2 | 3 | 2916 | 2962 | 2868 | 2000 | -26 | -10 | -7 | 0 | 0 | -3 | 185 | 9 | 94 | 94 | 94 | 1 | 1 | 1
1223 | Offshore Wind Connection Figueira da Foz (South) | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 276 | 276 | 3 | 3 | 3
1224 | Offshore Wind Connection Ericeira | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 133 | 133 | 1 | 1 | 1
1225 | Offshore Wind Connection Sines | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 202 | 202 | 2 | 2 | 2
1226 | North-South Electricity Corridor in Eastern Europe | Light PINT | 132 | 163 | 107 |  | 70 | 79 | 59 | 29 | 41 | 19 | -616 | -518 | -699 |  | 8 | 77 | 124 |  |  |  | 450 | 621 | 290 |  | -92 | -75 | -147 | -3 | -8 | -26 |  |  | 81 | 81 | 81 | 0 | 0 | 0
1229 | Rhine-Main-Link | PINT | 294 | 379 | 237 |  | 33 | 71 | -48 | 129 | 165 | 107 | -488 | -401 | -425 | -58 | 4 | 36 | 59 | -1 | -7 | -12 | 1 | 2 | 1 |  | -226 | -61 | -28 | -2 | -3 | -22 | -1 | -25 | 0 | 0 | 0 | 0 | 0 | 0
1230 | TuNur Malta | PINT | 18 | 24 | 12 | 244 | 108 | 110 | 106 | 213 | 215 | 211 | -954 | -937 | -971 | 1 | 12 | 119 | 192 | 0 | 0 | 0 | 3285 | 3291 | 3278 | 1400 | -339 | -107 | -12 | -3 | -3 | -37 | -13 | 0 | 2 | 2 | 2 | 0 | 0 | 0
1231 | Green Aegean Interconnector | Light PINT | 757 | 774 | 744 |  | 423 | 442 | 409 | 219 | 230 | 210 | -3732 | -3609 | -3897 |  | 47 | 465 | 752 |  |  |  | 3366 | 3508 | 3263 |  | -1519 | -439 | -199 | -17 | -20 | -154 |  |  | 252 | 252 | 252 | 4 | 4 | 4
1233 | Laufenburg - Beznau - Breite | Light PINT | 109 | 110 | 107 |  | 57 | 59 | 54 | 95 | 97 | 94 | -499 | -474 | -525 |  | 6 | 62 | 101 |  |  |  | 1474 | 1485 | 1463 |  | -179 | -50 | -33 | -2 | -3 | -17 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1234 | 220-kV Reitdorf (AT) - Weißenbach (AT) | TOOT | 0 | 0 | 0 | 46 | 12 | 15 | 9 | 45 | 49 | 41 | -109 | -84 | -130 | -8 | 1 | 14 | 22 | 0 | -1 | -2 | 694 | 763 | 626 | 500 | -36 | -11 | -3 | 0 | -1 | -4 | -58 | -3 | 3 | 3 | 3 | 0 | 0 | 0
1235 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | PINT | 13 | 22 | 8 |  | 8 | 14 | 5 | 3 | 9 | -3 | -73 | -42 | -127 | 98 | 1 | 9 | 15 | 1 | 12 | 20 | 42 | 133 | -46 |  | -34 | -10 | -2 | 0 | 0 | -3 | 362 | 27 | 0 | 0 | 0 | 0 | 0 | 0
1236 | Power-to-Gas for Austria (P2G4A) | PINT | 5 | 11 | 1 |  | 2 | 6 | 0 | 3 | 8 | 0 | -20 | 0 | -55 | 0 | 0 | 2 | 4 | 0 | 0 | 0 | 45 | 121 | 2 |  | -3 | -3 | -5 | 0 | 0 | -1 | 1 | 0
1239 | Interconnection Ukraine-Slovak Republic | Light PINT | 21 | 25 | 18 |  | 15 | 16 | 12 | 3 | 4 | 1 | -129 | -109 | -141 |  | 2 | 16 | 26 |  |  |  | 45 | 68 | 14 |  | -77 | -7 | -57 | -2 | -4 | -3
1240 | Interconnection Ukraine-Romania | Light PINT | 31 | 38 | 23 |  | 21 | 26 | 17 | 4 | 9 | 2 | -182 | -153 | -232 |  | 2 | 23 | 37 |  |  |  | 63 | 141 | 23 |  | -151 | -7 | -131 | -5 | -10 | -2

## 2040NT
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 52 | 74 | 28 | 43 | 20 | 25 | 15 | 196 | 238 | 153 | -136 | -102 | -173 | 4 | 26 | 66 | 70 | 1 | 2 | 2 | 3043 | 3717 | 2334 | 1154 | -33 | -9 | -3 | 0 | 0 | -3 | 345 | 8 | 3038 | 3038 | 3038 | 29 | 29 | 29
4 | Interconnection Portugal-Spain | TOOT | 50 | 51 | 50 |  | 24 | 29 | 20 | 26 | 30 | 22 | -166 | -136 | -194 | 4 | 32 | 80 | 85 | 1 | 2 | 2 | 405 | 470 | 340 |  | -24 | -7 | -2 | 0 | 0 | -3 | 58 | 8 | 92 | 92 | 92 | 1 | 1 | 1
16 | Biscay Gulf | TOOT | 695 | 700 | 685 |  | 103 | 109 | 101 | 496 | 500 | 492 | -704 | -685 | -740 | 29 | 135 | 339 | 363 | 6 | 14 | 15 | 7629 | 7642 | 7615 |  | -228 | -57 | -46 | -3 | -4 | -20 | 3406 | 98 | 3597 | 3597 | 3597 | 126 | 126 | 126
28 | Italy-Montenegro | TOOT | 100 | 103 | 97 |  | 49 | 51 | 48 | 39 | 46 | 29 | -337 | -326 | -344 | 0 | 65 | 162 | 173 | 0 | 0 | 0 | 601 | 712 | 443 |  | -108 | -36 | -1 | -1 | -1 | -13 | 228 | 10 | 184 | 184 | 184 | 3 | 3 | 3
29 | Italy-Tunisia | TOOT | 243 | 268 | 210 |  | 144 | 149 | 134 | 41 | 51 | 31 | -976 | -913 | -1016 | 0 | 187 | 470 | 503 | 0 | 0 | 0 | 626 | 794 | 483 |  | -421 | -135 | -9 | -3 | -3 | -47 | -199 | -16 | 854 | 854 | 854 | 8 | 8 | 8
33 | Central Northern Italy | TOOT | 40 | 45 | 33 |  | 13 | 17 | 10 | 16 | 22 | 13 | -87 | -67 | -114 | 3 | 17 | 42 | 45 | 1 | 1 | 1 | 228 | 340 | 148 |  | -54 | -11 | -13 | -1 | -1 | -4 | 62 | -5 | 247 | 247 | 247 | 3 | 3 | 3
35 | CZ Southwest-east corridor | TOOT | 170 | 171 | 169 |  | 96 | 100 | 92 | 67 | 78 | 58 | -651 | -627 | -680 | 7 | 125 | 313 | 335 | 1 | 3 | 3 | 1042 | 1218 | 881 |  | -277 | -85 | -20 | -3 | -3 | -30 | 427 | 21 | 288 | 288 | 288 | 0 | 0 | 0
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 42 | 52 | 31 |  | 1 | 5 | -3 | 14 | 24 | 7 | -6 | 23 | -31 |  | 1 | 3 | 3 |  |  |  | 218 | 373 | 112 |  | -1 | -1 | -6 | 0 | 0 | 0 |  |  | 104 | 104 | 104 | 2 | 2 | 2
47 | Westtirol (AT) - Vöhringen (DE) | TOOT | 108 | 118 | 94 |  | 24 | 28 | 16 | 61 | 69 | 50 | -161 | -108 | -190 | -7 | 31 | 78 | 83 | -1 | -4 | -4 | 948 | 1078 | 756 |  | -68 | -22 | -3 | -1 | -1 | -8 | 84 | 0 | 34 | 34 | 34 | 0 | 0 | 0
81 | North South Interconnector | TOOT | 121 | 123 | 119 |  | 46 | 49 | 45 | 53 | 58 | 48 | -316 | -307 | -330 | 0 | 61 | 152 | 163 | 0 | 0 | 0 | 816 | 880 | 740 |  | -129 | -38 | -12 | -1 | -1 | -13 | 41 | 3 | 448 | 448 | 448 | 8 | 8 | 8
85 | Integration of RES in Alentejo | TOOT | 8 | 17 | 3 | 1 | 3 | 5 | 1 | 10 | 13 | 8 | -19 | -7 | -37 | 0 | 4 | 9 | 10 | 0 | 0 | 0 | 156 | 199 | 123 | 553 | 0 | -3 | -5 | 0 | 0 | -1 | -37 | -1 | 0 | 0 | 0 | 0 | 0 | 0
94 | GerPol Improvements | TOOT | 312 | 313 | 311 |  | 124 | 130 | 119 | 64 | 69 | 59 | -840 | -810 | -886 | 10 | 161 | 404 | 433 | 2 | 5 | 5 | 987 | 1076 | 900 |  | -445 | -55 | -312 | -12 | -20 | -20 | 385 | 16 | 497 | 497 | 497 | 8 | 8 | 8
107 | Celtic Interconnector | TOOT | 212 | 219 | 205 |  | 31 | 33 | 30 | 206 | 208 | 205 | -210 | -201 | -221 | 14 | 40 | 101 | 108 | 3 | 7 | 7 | 3077 | 3239 | 2877 |  | -73 | -18 | -14 | -1 | -1 | -6 | 1091 | 45 | 1270 | 1270 | 1270 | 42 | 42 | 42
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 95 | 96 | 95 |  | 12 | 15 | 8 | 78 | 84 | 71 | -82 | -54 | -102 | 0 | 16 | 39 | 42 | 0 | 0 | 0 | 1205 | 1316 | 1082 |  | -11 | -4 | -1 | 0 | 0 | -1 | 60 | 4 | 707 | 707 | 707 | 9 | 9 | 9
120 | Princess Elisabeth Island (MOG 2) | TOOT | 341 | 349 | 333 | 523 | 64 | 71 | 58 | 820 | 822 | 819 | -438 | -396 | -483 | 23 | 84 | 210 | 225 | 4 | 11 | 12 | 12529 | 12827 | 12292 | 3500 | -332 | -69 | -94 | -5 | -7 | -25 | 296 | 27 | 1936 | 1936 | 1936 | 22 | 22 | 22
121 | Nautilus: multi-purpose interconnector Belgium - UK | TOOT | 219 | 230 | 207 |  | -4 | 0 | -7 | 93 | 107 | 83 | 24 | 48 | 1 | 13 | 0 | 0 | 0 | 3 | 6 | 7 | 1435 | 1674 | 1257 |  | -155 | -28 | -50 | -3 | -3 | -10 | 97 | 8 | 487 | 487 | 487 | 10 | 10 | 10
124 | Ekhyddan-Nybro-Hemsjö | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 36 | 41 | 28 |  | 1 | 3 | -1 | -13 | -1 | -29 | -8 | 5 | -19 | 12 | 1 | 4 | 4 | 2 | 6 | 6 | -189 | -21 | -433 |  | -41 | -5 | -26 | -1 | -2 | -2 | 154 | 13 | 360 | 360 | 360 | 0 | 0 | 0
127 | Central Southern Italy | TOOT | 11 | 14 | 9 |  | 6 | 8 | 5 | 4 | 5 | 2 | -43 | -32 | -55 | 11 | 8 | 21 | 22 | 2 | 6 | 6 | 55 | 81 | 29 |  | -23 | -8 | 0 | 0 | 0 | -3 | 145 | 7 | 95 | 95 | 95 | 1 | 1 | 1
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 519 | 655 | 413 |  | 30 | 38 | 23 | 192 | 238 | 158 | -204 | -159 | -259 | 3 | 39 | 98 | 105 | 1 | 2 | 2 | 2 | 2 | 2 |  | -71 | -22 | -2 | -1 | -1 | -8 | 241 | 10 | 0 | 0 | 0 | 0 | 0 | 0
132 | HVDC Line A-North | TOOT | 1640 | 1900 | 1431 |  | 99 | 121 | 81 | 620 | 749 | 519 | -676 | -549 | -826 | 45 | 130 | 325 | 348 | 9 | 22 | 23 | 6 | 7 | 5 |  | -234 | -74 | -7 | -2 | -2 | -26 | 988 | 55 | 0 | 0 | 0 | 0 | 0 | 0
138 | Black Sea Corridor | TOOT | 20 | 22 | 19 |  | 10 | 11 | 10 | 9 | 23 | -4 | -70 | -68 | -72 | 2 | 13 | 34 | 36 | 0 | 1 | 1 | 131 | 347 | -60 |  | -24 | -9 | -1 | 0 | 0 | -3 | -1 | -3 | 420 | 420 | 420 | 5 | 5 | 5
144 | Mid Continental East corridor | TOOT | 29 | 33 | 23 |  | 11 | 14 | 6 | 7 | 12 | 1 | -75 | -43 | -99 | 2 | 14 | 36 | 39 | 0 | 1 | 1 | 98 | 180 | 15 |  | -17 | -5 | -3 | 0 | 0 | -2 | -8 | -2 | 654 | 654 | 654 | 7 | 7 | 7
150 | Italy-Slovenia | TOOT | 36 | 44 | 25 |  | 24 | 26 | 22 | 11 | 15 | 7 | -163 | -147 | -174 | 5 | 31 | 78 | 84 | 1 | 2 | 3 | 160 | 233 | 102 |  | -63 | -20 | -1 | -1 | -1 | -7 | 142 | 10 | 212 | 212 | 212 | 3 | 3 | 3
153 | France-Alderney-Britain | TOOT | 231 | 243 | 223 |  | 20 | 24 | 16 | 213 | 214 | 213 | -138 | -109 | -165 | 20 | 26 | 66 | 71 | 4 | 10 | 10 | 3404 | 3618 | 3253 |  | -94 | -28 | -9 | -1 | -1 | -10 | 1134 | 55 | 2222 | 2222 | 2222 | 75 | 75 | 75
170 | Baltic States Synchronization with Continental Europe | TOOT | 435 | 457 | 419 |  | 222 | 235 | 207 | 180 | 182 | 178 | -1507 | -1406 | -1601 | 0 | 289 | 725 | 776 | 0 | 0 | 0 | 2771 | 2775 | 2767 |  | -547 | -108 | -394 | -14 | -28 | -36 | 157 | -6 | 768 | 768 | 768 | 14 | 14 | 14
174 | Greenconnector | TOOT | 147 | 173 | 119 |  | 88 | 93 | 85 | 16 | 17 | 15 | -598 | -580 | -631 | 7 | 115 | 287 | 308 | 1 | 3 | 3 | 246 | 264 | 228 |  | -302 | -84 | -32 | -3 | -4 | -30 | 545 | 35 | 479 | 479 | 479 | 6 | 6 | 6
176 | Hansa PowerBridge I | TOOT | 148 | 154 | 138 |  | 14 | 21 | 8 | 65 | 76 | 56 | -97 | -57 | -143 | -2 | 19 | 46 | 50 | 0 | -1 | -1 | 1010 | 1197 | 853 |  | -86 | -18 | -92 | -3 | -4 | -5 | -127 | -7 | 614 | 614 | 614 | 8 | 8 | 8
187 | St. Peter (AT) - Pleinting (DE) | TOOT | 445 | 448 | 442 |  | 102 | 123 | 82 | 239 | 250 | 226 | -693 | -559 | -837 | 65 | 133 | 333 | 357 | 12 | 31 | 33 | 3706 | 3928 | 3448 |  | -364 | -96 | -58 | -4 | -6 | -34 | 1576 | 77 | 305 | 305 | 305 | 3 | 3 | 3
200 | CZ Northwest-South corridor | TOOT | 170 | 171 | 169 |  | 96 | 100 | 92 | 67 | 78 | 58 | -651 | -627 | -680 | 1 | 125 | 313 | 335 | 0 | 0 | 0 | 1042 | 1218 | 881 |  | -277 | -85 | -20 | -3 | -3 | -30 | 273 | 7 | 285 | 285 | 285 | 0 | 0 | 0
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 28 | 35 | 20 |  | 12 | 14 | 9 | 2 | 6 | -2 | -81 | -64 | -98 | 2 | 16 | 39 | 42 | 0 | 1 | 1 | 24 | 87 | -43 |  | -35 | -10 | -5 | 0 | 0 | -3 | 33 | 2 | 166 | 166 | 166 | 1 | 1 | 1
219 | Great Sea Interconnector | TOOT | 576 | 606 | 535 |  | 146 | 151 | 137 | 197 | 200 | 192 | -993 | -932 | -1025 | 42 | 191 | 478 | 511 | 8 | 20 | 21 | 3040 | 3085 | 2983 |  | -475 | -149 | -14 | -4 | -4 | -52 | -2308 | -188 | 1328 | 1328 | 1328 | 13 | 13 | 13
225 | 2nd interconnector Belgium - Germany | light PINT | 162 | 173 | 150 |  | 14 | 17 | 9 | 71 | 79 | 61 | -92 | -62 | -117 | 37 | 18 | 44 | 48 | 7 | 18 | 19 | 1108 | 1235 | 926 |  | -57 | -5 | -37 | -1 | -2 | -2 | 900 | 38 | 366 | 366 | 366 | 4 | 4 | 4
227 | Transbalkan Corridor | TOOT | 28 | 39 | 19 |  | 19 | 23 | 12 | 1 | 14 | -13 | -130 | -84 | -156 | -1 | 25 | 62 | 67 | 0 | 0 | 0 | 14 | 221 | -222 |  | -62 | -18 | -9 | -1 | -1 | -6 | -97 | -7 | 507 | 507 | 507 | 0 | 0 | 0
228 | Muhlbach - Eichstetten | TOOT | 56 | 66 | 50 |  | 4 | 7 | 1 | 35 | 49 | 22 | -25 | -3 | -45 | 4 | 5 | 12 | 13 | 1 | 2 | 2 | 543 | 766 | 330 |  | -36 | -6 | -16 | -1 | -1 | -2 | 188 | 10 | 302 | 302 | 302 | 9 | 9 | 9
231 | Beznau - Tiengen | TOOT | 81 | 84 | 76 |  | 27 | 35 | 19 | 51 | 55 | 47 | -183 | -130 | -235 | -14 | 35 | 88 | 94 | -3 | -7 | -7 | 785 | 865 | 712 |  | -98 | -29 | -6 | -1 | -1 | -10 | 73 | -2 | 102 | 102 | 102 | 2 | 2 | 2
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 1511 | 1801 | 1327 |  | 89 | 112 | 73 | 589 | 721 | 505 | -608 | -493 | -764 | 58 | 117 | 292 | 313 | 11 | 28 | 30 | 6 | 7 | 5 |  | -832 | -263 | -25 | -7 | -7 | -92 | 1955 | 100 | 0 | 0 | 0 | 0 | 0 | 0
239 | Fenno-Skan 3 | Light PINT | 52 | 54 | 49 |  | 1 | 4 | -1 | 49 | 58 | 40 | -10 | 4 | -26 |  | 2 | 5 | 5 |  |  |  | 764 | 904 | 623 |  | -26 | 0 | -21 | -1 | -1 | 0 |  |  | 222 | 222 | 222 | 2 | 2 | 2
243 | New 400 kV interconnection line between Serbia and Croatia | Light PINT | 1 | 2 | 0 |  | 0 | 3 | -3 | -2 | 7 | -14 | 0 | 20 | -18 |  | 0 | 0 | 0 |  |  |  | -29 | 111 | -203 |  | -2 | 0 | -2 | 0 | 0 | 0 |  |  | 1 | 1 | 1 | 0 | 0 | 0
244 | Vigy - Uchtelfangen area | TOOT | 285 | 291 | 276 |  | 11 | 17 | 4 | 120 | 134 | 110 | -73 | -30 | -118 | 45 | 14 | 35 | 38 | 9 | 22 | 23 | 1861 | 2096 | 1675 |  | -141 | -20 | -68 | -3 | -4 | -8 | 1098 | 61 | 1689 | 1689 | 1689 | 45 | 45 | 45
247 | AQUIND Interconnector | TOOT | 392 | 395 | 390 |  | 35 | 40 | 27 | 370 | 383 | 360 | -240 | -184 | -272 | 21 | 46 | 115 | 124 | 4 | 10 | 11 | 5744 | 5994 | 5477 |  | -195 | -48 | -38 | -3 | -3 | -17 | 876 | 47 | 3749 | 3749 | 3749 | 124 | 124 | 124
250 | Merchant line Castasegna (CH) - Mese (IT) | TOOT | 34 | 37 | 29 |  | 22 | 30 | 16 | 9 | 13 | 7 | -148 | -110 | -201 | 2 | 28 | 71 | 76 | 0 | 1 | 1 | 136 | 194 | 100 |  | -58 | -18 | -5 | -1 | -1 | -6 | 26 | 5 | 52 | 52 | 52 | 1 | 1 | 1
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 713 | 814 | 635 |  | 40 | 48 | 32 | 249 | 298 | 215 | -269 | -221 | -329 | 33 | 52 | 130 | 139 | 6 | 16 | 17 | 2 | 3 | 2 |  | -210 | -66 | -6 | -2 | -2 | -23 | 845 | 45 | 0 | 0 | 0 | 0 | 0 | 0
259 | HU-RO | TOOT | 22 | 33 | 7 |  | 6 | 9 | 3 | 10 | 27 | -2 | -42 | -22 | -61 | 4 | 8 | 20 | 22 | 1 | 2 | 2 | 153 | 418 | -26 |  | -11 | -3 | -5 | 0 | 0 | -1 | 203 | 15 | 724 | 724 | 724 | 10 | 10 | 10
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | TOOT | 236 | 237 | 235 |  | -17 | -13 | -20 | 75 | 89 | 65 | 115 | 138 | 91 | 31 | 0 | 0 | 0 | 6 | 15 | 16 | 1161 | 1386 | 1007 |  | -74 | -22 | -10 | -1 | -1 | -8 | 450 | 28 | 961 | 961 | 961 | 34 | 34 | 34
267 | Hansa PowerBridge II | Light PINT | 148 | 154 | 138 |  | 14 | 21 | 8 | 65 | 76 | 56 | -97 | -57 | -143 | -2 | 19 | 46 | 50 | 0 | -1 | -1 | 1010 | 1197 | 853 |  | -86 | -18 | -92 | -3 | -4 | -5 | -127 | -7 | 614 | 614 | 614 | 8 | 8 | 8
270 | FR-ES project -Aragón-Atlantic Pyrenees | TOOT | 464 | 465 | 462 |  | 69 | 73 | 66 | 357 | 373 | 338 | -469 | -446 | -499 | 16 | 90 | 225 | 241 | 3 | 8 | 8 | 5518 | 5824 | 5144 |  | -145 | -34 | -33 | -2 | -3 | -12 | 1764 | 61 | 2286 | 2286 | 2286 | 83 | 83 | 83
276 | FR-ES project -Navarra-Landes | PINT | 423 | 436 | 411 |  | 56 | 59 | 54 | 335 | 336 | 334 | -383 | -370 | -398 | 26 | 74 | 184 | 197 | 5 | 13 | 13 | 5223 | 5244 | 5202 |  | -182 | -30 | -64 | -3 | -4 | -11 | 2571 | 85 | 1145 | 1145 | 1145 | 51 | 51 | 51
280 | FR-BE: Lonny-Achene-Gramme | TOOT | 113 | 123 | 98 |  | 2 | 6 | -4 | 61 | 63 | 59 | -11 | 26 | -39 | 15 | 2 | 5 | 6 | 3 | 7 | 8 | 952 | 976 | 928 |  | -78 | -6 | -42 | -2 | -3 | -3 | 472 | 25 | 1179 | 1179 | 1179 | 39 | 39 | 39
283 | TuNur Italy | PINT | 109 | 196 | 50 | 666 | 212 | 222 | 201 | 685 | 687 | 684 | -1442 | -1368 | -1511 | 5 | 277 | 694 | 743 | 1 | 3 | 3 | 10709 | 10713 | 10705 | 5000 | -601 | -184 | -30 | -5 | -6 | -65 | 418 | 29 | 15 | 15 | 15 | 0 | 0 | 0
285 | GridLink | TOOT | 231 | 243 | 223 |  | 20 | 24 | 16 | 213 | 214 | 213 | -138 | -109 | -165 | 20 | 26 | 66 | 71 | 4 | 10 | 10 | 3404 | 3618 | 3253 |  | -94 | -28 | -9 | -1 | -1 | -10 | 592 | 33 | 2221 | 2221 | 2221 | 75 | 75 | 75
297 | BRABO III | TOOT | 41 | 44 | 40 |  | 9 | 11 | 7 | 20 | 24 | 16 | -63 | -47 | -78 | 7 | 12 | 30 | 32 | 1 | 3 | 3 | 309 | 378 | 242 |  | -5 | -5 | -12 | 0 | 0 | -2 | 168 | 8 | 0 | 0 | 0 | 0 | 0 | 0
299 | SACOI 3 | TOOT | 182 | 183 | 182 |  | 96 | 96 | 95 | 27 | 34 | 20 | -650 | -645 | -655 | 2 | 125 | 313 | 335 | 0 | 1 | 1 | 425 | 535 | 314 |  | -2049 | -6 | -1379 | -53 | -74 | -18 | -69 | -7 | 361 | 361 | 361 | 9 | 9 | 9
309 | NeuConnect | TOOT | 403 | 407 | 398 |  | 6 | 15 | 1 | 218 | 221 | 216 | -42 | -4 | -104 | 29 | 8 | 20 | 22 | 6 | 14 | 15 | 3418 | 3448 | 3388 |  | -216 | -39 | -82 | -4 | -6 | -14 | 705 | 40 | 1820 | 1820 | 1820 | 21 | 21 | 21
312 | St. Peter (AT) - Tauern (AT) | TOOT | 343 | 344 | 342 |  | 76 | 89 | 62 | 191 | 192 | 190 | -519 | -425 | -607 | -32 | 100 | 250 | 267 | -6 | -15 | -16 | 2985 | 2997 | 2973 |  | -277 | -76 | -39 | -3 | -4 | -27 | -233 | -17 | 215 | 215 | 215 | 2 | 2 | 2
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 239 | 247 | 228 |  | 52 | 59 | 41 | 129 | 139 | 120 | -351 | -282 | -403 | 1 | 67 | 169 | 181 | 0 | 1 | 1 | 1995 | 2168 | 1827 |  | -185 | -51 | -25 | -2 | -2 | -18 | 363 | 9 | 125 | 125 | 125 | 1 | 1 | 1
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 3 | 5 | 2 |  | 1 | 3 | 0 | -7 | -3 | -15 | -9 | 2 | -23 | 1 | 2 | 5 | 5 | 0 | 1 | 1 | -118 | -46 | -247 |  | -1 | -2 | -5 | 0 | 0 | -1 | 279 | 20 | 12 | 12 | 12 | 0 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 14 | 24 | 6 |  | 8 | 13 | 4 | 0 | 1 | 0 | -54 | -28 | -87 | 2 | 10 | 26 | 28 | 0 | 1 | 1 | 3 | 7 | 0 |  | -5 | -6 | -9 | 0 | 0 | -2 | 289 | 20 | 22 | 22 | 22 | 0 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | TOOT | 186 | 201 | 172 |  | 89 | 93 | 83 | 20 | 25 | 17 | -608 | -563 | -632 | 9 | 117 | 293 | 313 | 2 | 4 | 5 | 315 | 393 | 261 |  | -270 | -69 | -42 | -3 | -4 | -25 | 191 | 11 | 915 | 915 | 915 | 9 | 9 | 9
328 | Interconnector DE-LUX | TOOT | 5 | 7 | 3 |  | 3 | 8 | 0 | 8 | 13 | 2 | -24 | 0 | -57 | -16 | 5 | 11 | 12 | -3 | -8 | -8 | 129 | 200 | 31 |  | -6 | -1 | -3 | 0 | 0 | 0 | -186 | -11 | 0 | 0 | 0 | 0 | 0 | 0
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 283 | 297 | 269 |  | 101 | 106 | 96 | 221 | 231 | 209 | -1692 | -1777 | -1595 | -11 | 574 | 1063 | 1120 | -2 | -5 | -6 | 4688 | 4435 | 4922 | 0 | -1536 | -177 | -74 | -122 | -79 | -53 | -336 | -34 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | TOOT | 72 | 76 | 64 |  | -1 | 1 | -4 | 1 | 3 | -1 | 7 | 26 | -5 | 8 | 0 | 0 | 0 | 2 | 4 | 4 | 10 | 40 | -17 |  | -20 | -4 | -27 | -1 | -1 | -1 | 72 | 7 | 639 | 639 | 639 | 1 | 1 | 1
335 | North Sea Wind Power Hub | Light PINT | 1346 | 1394 | 1298 | 1493 | 284 | 312 | 264 | 2875 | 2875 | 2874 | -1929 | -1793 | -2125 |  | 370 | 928 | 994 |  |  |  | 44719 | 44815 | 44623 | 14000 | -954 | -161 | -405 | -18 | -27 | -59 |  |  | 3397 | 3397 | 3397 | 42 | 42 | 42
338 | Adriatic HVDC link | TOOT | 98 | 109 | 88 |  | 36 | 43 | 31 | 47 | 60 | 31 | -247 | -209 | -293 | 28 | 47 | 119 | 127 | 5 | 13 | 14 | 724 | 930 | 478 |  | -78 | -29 | -4 | 0 | 0 | -10 | 337 | 13 | 687 | 687 | 687 | 9 | 9 | 9
339 | Tyrrhenian link | TOOT | 85 | 92 | 79 |  | 41 | 48 | 32 | 24 | 32 | 17 | -280 | -215 | -326 | 11 | 54 | 134 | 144 | 2 | 5 | 6 | 291 | 334 | 264 |  | -124 | -40 | -3 | -1 | -1 | -14 | 370 | 10 | 490 | 490 | 490 | 8 | 8 | 8
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 322 | 352 | 298 |  | 115 | 126 | 107 | 251 | 274 | 232 | -2907 | -3193 | -2680 | -11 | 986 | 1826 | 1925 | -2 | -5 | -6 | 4614 | 4282 | 5070 | 0 | -3069 | -252 | -2149 | -190 | -241 | -81 | -595 | -48 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | TOOT | 15 | 24 | 9 |  | 6 | 7 | 6 | 6 | 13 | 1 | -43 | -39 | -45 | 5 | 8 | 21 | 22 | 1 | 2 | 3 | 96 | 210 | 20 |  | -16 | -4 | -4 | 0 | 0 | -1 | 1223 | 90 | 454 | 454 | 454 | 0 | 0 | 0
342 | Central Balkan Corridor | TOOT | 9 | 13 | 3 |  | 5 | 7 | 3 | 2 | 7 | -4 | -37 | -22 | -49 | 2 | 7 | 18 | 19 | 0 | 1 | 1 | 28 | 110 | -57 |  | -12 | -2 | -5 | 0 | 0 | -1 | 21 | -1 | 346 | 346 | 346 | 4 | 4 | 4
343 | CSE1 New | TOOT | 7 | 7 | 7 |  | 3 | 3 | 3 | -1 | 0 | -1 | -18 | -17 | -19 | 1 | 3 | 9 | 9 | 0 | 1 | 1 | -16 | -12 | -21 |  | -2 | -2 | -4 | 0 | 0 | -1 | 98 | 7 | 37 | 37 | 37 | 0 | 0 | 0
346 | ZuidWest380 NL Oost | TOOT | 13 | 16 | 8 |  | 0 | 1 | -2 | 0 | 1 | -1 | 2 | 13 | -8 | -3 | 0 | 0 | 0 | -1 | -1 | -1 | -2 | 10 | -14 |  | -34 | -2 | -19 | -1 | -1 | -1 | -121 | -6 | 0 | 0 | 0 | 0 | 0 | 0
349 | MaresConnect | TOOT | 129 | 138 | 119 |  | 30 | 37 | 24 | 118 | 120 | 115 | -204 | -163 | -254 | 0 | 39 | 98 | 105 | 0 | 0 | 0 | 1826 | 1864 | 1758 |  | -25 | -4 | -7 | 0 | -1 | -2 | 107 | 2 | 646 | 646 | 646 | 10 | 10 | 10
350 | South Balkan Corridor | TOOT | 52 | 53 | 50 |  | 26 | 27 | 24 | 27 | 29 | 25 | -175 | -164 | -186 | 1 | 34 | 84 | 90 | 0 | 1 | 1 | 426 | 458 | 394 |  | -63 | -25 | -7 | 0 | 0 | -8 | 1231 | 90 | 233 | 233 | 233 | 3 | 3 | 3
375 | Lienz (AT) - Veneto region (IT) 220 kV | TOOT | 106 | 107 | 105 |  | 44 | 46 | 41 | 7 | 22 | -5 | -296 | -277 | -315 | 17 | 57 | 142 | 152 | 3 | 8 | 9 | 106 | 329 | -81 |  | -141 | -36 | -25 | -2 | -2 | -13 | 117 | 9 | 627 | 627 | 627 | 6 | 6 | 6
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | Light PINT | 6 | 12 | 2 |  | 2 | 5 | -1 | 4 | 8 | 2 | -14 | 4 | -33 |  | 3 | 7 | 7 |  |  |  | 61 | 114 | 33 |  | -31 | -5 | -12 | -1 | -1 | -2 |  |  | 2 | 2 | 2 | 0 | 0 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | TOOT | 38 | 40 | 33 |  | 9 | 11 | 7 | 17 | 20 | 14 | -60 | -45 | -78 | 7 | 12 | 29 | 31 | 1 | 3 | 4 | 268 | 308 | 221 |  | -13 | -5 | 0 | 0 | 0 | -2 | 191 | 9 | 0 | 0 | 0 | 0 | 0 | 0
378 | Transformer Gatica | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 339 | 352 | 331 |  | 22 | 23 | 21 | 139 | 146 | 130 | -148 | -142 | -159 | 39 | 28 | 71 | 76 | 8 | 19 | 20 | 1 | 1 | 1 |  | -51 | -16 | -2 | 0 | 0 | -6 | 896 | 51 | 0 | 0 | 0 | 0 | 0 | 0
1039 | SE North-south long-term reinforcements | PINT | 35 | 40 | 28 |  | 5 | 7 | 1 | 4 | 9 | 0 | -32 | -10 | -49 | 6 | 6 | 16 | 17 | 1 | 3 | 3 | 60 | 144 | -9 |  | -36 | -3 | -24 | -1 | -1 | -1 | 131 | 4 | 324 | 324 | 324 | 0 | 0 | 0
1040 | LirIC | TOOT | 121 | 125 | 116 |  | 29 | 37 | 20 | 118 | 139 | 101 | -196 | -139 | -252 | 1 | 38 | 94 | 101 | 0 | 0 | 1 | 1819 | 2162 | 1532 |  | -25 | -6 | -4 | 0 | 0 | -2 | 169 | 6 | 631 | 631 | 631 | 12 | 12 | 12
1041 | GREGY Green Energy Interconnector | TOOT | 462 | 535 | 367 |  | 352 | 375 | 323 | 68 | 87 | 52 | -2397 | -2200 | -2549 | 10 | 460 | 1153 | 1234 | 2 | 5 | 5 | 1054 | 1361 | 808 |  | -1390 | -450 | -19 | -11 | -11 | -157 | 1198 | 95 | 4848 | 4848 | 4848 | 48 | 48 | 48
1046 | Finnish North-South reinforcement | PINT | 156 | 156 | 156 |  | 10 | 10 | 10 | 232 | 232 | 232 | 66 | 66 | 66 | 0 | 13 | 32 | 34 | 0 | 0 | 0 | 3634 | 3634 | 3634 |  | -1 | -1 | -1 | 0 | 0 | 0 | -138 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 67 | 83 | 55 |  | 45 | 49 | 41 | 4 | 6 | 1 | -303 | -279 | -335 | 3 | 58 | 146 | 156 | 1 | 1 | 2 | 67 | 102 | 33 |  | -191 | -56 | -15 | -2 | -2 | -20 | -4472 | -325 | 61 | 61 | 61 | 0 | 0 | 0
1049 | Cronos Energy Ltd | PINT | 274 | 275 | 273 |  | -11 | -8 | -14 | 171 | 182 | 156 | 73 | 93 | 52 | 9 | 0 | 0 | 0 | 2 | 4 | 5 | 2658 | 2840 | 2464 |  | -143 | -31 | -39 | -2 | -3 | -11 | -95 | 1 | 511 | 511 | 511 | 6 | 6 | 6
1050 | Tarchon Energy Ltd | TOOT | 403 | 407 | 398 |  | 6 | 15 | 1 | 218 | 221 | 216 | -42 | -4 | -104 | 24 | 8 | 20 | 22 | 5 | 12 | 13 | 3418 | 3448 | 3388 |  | -216 | -39 | -82 | -4 | -6 | -14 | 346 | 21 | 1828 | 1828 | 1828 | 22 | 22 | 22
1052 | Lienz (AT) - Malta (AT) - Obersielach (AT) | TOOT | 478 | 510 | 446 | 164 | 167 | 172 | 163 | 239 | 244 | 235 | -1139 | -1107 | -1170 | 13 | 219 | 548 | 586 | 2 | 6 | 7 | 3746 | 3804 | 3688 | 2000 | -484 | -130 | -81 | -6 | -8 | -46 | -97 | -6 | 1731 | 1731 | 1731 | 16 | 16 | 16
1054 | 220-kV Westtirol (AT) - Zell/Ziller (AT) | TOOT | 109 | 118 | 97 |  | 24 | 28 | 16 | 61 | 69 | 51 | -162 | -110 | -190 | 15 | 31 | 78 | 83 | 3 | 7 | 8 | 952 | 1078 | 770 |  | -68 | -22 | -3 | -1 | -1 | -8 | 391 | 24 | 34 | 34 | 34 | 0 | 0 | 0
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 188 | 194 | 180 |  | 71 | 76 | 68 | 146 | 148 | 144 | -483 | -461 | -518 | 47 | 93 | 232 | 249 | 9 | 23 | 24 | 2159 | 2323 | 1917 |  | -179 | -53 | -12 | -2 | -2 | -19 | 7127 | 533 | 1245 | 1245 | 1245 | 11 | 11 | 11
1058 | HVDC Interconnector DE-CH | Light PINT | 179 | 181 | 177 |  | 22 | 27 | 15 | 75 | 77 | 73 | -151 | -105 | -185 |  | 29 | 73 | 78 |  |  |  | 1156 | 1176 | 1135 |  | -118 | -27 | -27 | -2 | -2 | -10 |  |  | 461 | 461 | 461 | 7 | 7 | 7
1059 | Southern Italy | TOOT | 8 | 13 | 5 |  | 4 | 7 | 3 | 3 | 8 | -2 | -26 | -17 | -45 | 4 | 5 | 12 | 13 | 1 | 2 | 2 | 46 | 121 | -26 |  | -4 | -3 | -3 | 0 | 0 | -1 | 120 | 1 | 96 | 96 | 96 | 1 | 1 | 1
1066 | Bulgaria - Turkey | Light PINT | 137 | 144 | 132 |  | 84 | 95 | 72 | 9 | 12 | 4 | -570 | -489 | -646 |  | 109 | 274 | 293 |  |  |  | 148 | 196 | 59 |  | -278 | -90 | -1 | -2 | -2 | -31 |  |  | 88 | 88 | 88 | 1 | 1 | 1
1067 | New AC 400 kV interconnection line Greece - Turkey | Light PINT | 85 | 87 | 83 |  | 49 | 56 | 44 | -8 | 12 | -24 | -335 | -301 | -384 |  | 64 | 161 | 172 |  |  |  | -116 | 178 | -353 |  | -218 | -68 | -9 | -2 | -2 | -24 |  |  | 141 | 141 | 141 | 1 | 1 | 1
1068 | LaSGo Link | PINT | 69 | 75 | 62 |  | 7 | 11 | 0 | 70 | 77 | 62 | -45 | -2 | -72 | 2 | 9 | 22 | 23 | 0 | 1 | 1 | 1083 | 1177 | 978 |  | -144 | -3 | -94 | -4 | -5 | -2 | 155 | 8 | 66 | 66 | 66 | 0 | 0 | 0
1074 | Pannonian Corridor | TOOT | 13 | 20 | 7 |  | 2 | 5 | -2 | -2 | 2 | -5 | -17 | 17 | -36 | 2 | 3 | 8 | 9 | 0 | 1 | 1 | -25 | 25 | -78 |  | -14 | -3 | -5 | 0 | 0 | -1 | 39 | 3 | 305 | 305 | 305 | 4 | 4 | 4
1085 | Malta-Italy Cable Link No.2 | TOOT | 90 | 108 | 68 |  | 43 | 47 | 38 | 15 | 23 | 11 | -293 | -261 | -322 | 2 | 56 | 141 | 151 | 0 | 1 | 1 | 233 | 354 | 166 |  | -130 | -42 | -2 | -1 | -1 | -15 | 41 | 2 | 336 | 336 | 336 | 3 | 3 | 3
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 0 | 3 | 0 | 35 | 3 | 6 | -1 | 45 | 58 | 33 | -18 | 6 | -41 | -1 | 3 | 9 | 9 | 0 | 0 | 0 | 706 | 917 | 522 | 700 | -140 | -1 | -96 | -4 | -5 | -1 | -371 | -5 | 6 | 6 | 6 | 0 | 0 | 0
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | TOOT | 16 | 21 | 14 | 44 | 10 | 14 | 7 | 79 | 83 | 75 | -66 | -45 | -95 | 0 | 13 | 32 | 34 | 0 | 0 | 0 | 1236 | 1302 | 1169 | 1000 | -108 | -2 | -68 | -3 | -4 | -2 | -214 | -5 | 0 | 0 | 0 | 0 | 0 | 0
1092 | TritonLink: offshore hybrid HVDC interconnector Belgium – Denmark | TOOT | 1008 | 1025 | 991 | 202 | 140 | 142 | 136 | 1180 | 1181 | 1179 | -951 | -926 | -965 | 29 | 183 | 458 | 490 | 6 | 14 | 15 | 18166 | 18401 | 17957 | 10000 | -357 | -68 | -119 | -6 | -8 | -25 | 434 | 32 | 3467 | 3467 | 3467 | 37 | 37 | 37
1094 | Estlink 3 | TOOT | 116 | 126 | 108 |  | 31 | 36 | 27 | 124 | 129 | 117 | -212 | -181 | -244 | -5 | 41 | 102 | 109 | -1 | -2 | -2 | 1914 | 2019 | 1779 |  | -294 | -14 | -173 | -7 | -10 | -7 | 523 | 17 | 760 | 760 | 760 | 10 | 10 | 10
1095 | Aurora line 2 (4th AC Finland-Sweden north) | TOOT | 60 | 64 | 57 |  | 8 | 11 | 5 | 63 | 64 | 63 | -51 | -36 | -72 | 0 | 10 | 25 | 26 | 0 | 0 | 0 | 977 | 979 | 974 |  | -11 | -1 | -4 | 0 | 0 | -1 | 43 | 3 | 708 | 708 | 708 | 9 | 9 | 9
1096 | Beznau - Mettlen | Light TOOT | 89 | 103 | 72 |  | 34 | 43 | 23 | 67 | 81 | 54 | -232 | -159 | -291 |  | 45 | 112 | 120 |  |  |  | 1046 | 1264 | 816 |  | -103 | -34 | -1 | -1 | -1 | -12 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1097 | Upgrade to Konti-Skan | PINT | 79 | 91 | 65 |  | 9 | 14 | 2 | 45 | 49 | 42 | -59 | -16 | -97 | 9 | 11 | 28 | 30 | 2 | 5 | 5 | 705 | 782 | 647 |  | -48 | -8 | -18 | -1 | -1 | -3 | 266 | 14 | 117 | 117 | 117 | 2 | 2 | 2
1098 | Offshore Wind LT 2 | TOOT | 10 | 19 | 5 | 46 | 11 | 13 | 10 | 57 | 67 | 52 | -75 | -68 | -86 | 0 | 14 | 36 | 39 | 0 | 0 | 0 | 888 | 1037 | 785 | 700 | -65 | -1 | -43 | -2 | -2 | -1 | 104 | 3 | 147 | 147 | 147 | 1 | 1 | 1
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | TOOT | 151 | 161 | 141 |  | 92 | 95 | 89 | 53 | 54 | 52 | -628 | -602 | -645 | 17 | 121 | 302 | 324 | 3 | 8 | 9 | 818 | 829 | 801 |  | -272 | -84 | -19 | -3 | -3 | -29 | 561 | 28 | 286 | 286 | 286 | 0 | 0 | 0
1102 | Mettlen - Ulrichen | Light TOOT | 21 | 21 | 21 |  | 0 | 2 | -3 | 3 | 4 | 2 | 1 | 17 | -16 |  | 0 | 0 | 0 |  |  |  | 51 | 65 | 37 |  | -19 | -1 | -11 | 0 | -1 | -1 |  |  | 221 | 221 | 221 | 0 | 0 | 0
1103 | Bickigen - Chippis | Light TOOT | 63 | 76 | 51 |  | 25 | 29 | 16 | 50 | 61 | 37 | -169 | -110 | -200 |  | 32 | 81 | 87 |  |  |  | 781 | 945 | 562 |  | -64 | -23 | -4 | 0 | 0 | -8 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1104 | Bauler - Roost | TOOT | 3 | 5 | 2 |  | 1 | 3 | 0 | 0 | 5 | -8 | -10 | -2 | -20 | -17 | 2 | 5 | 5 | -3 | -8 | -9 | -7 | 72 | -136 |  | 0 | -1 | -2 | 0 | 0 | 0 | -196 | -12 | 0 | 0 | 0 | 0 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 478 | 480 | 476 |  | 125 | 126 | 123 | 190 | 190 | 190 | -848 | -838 | -858 | 2 | 163 | 408 | 437 | 0 | 1 | 1 | 2954 | 2954 | 2954 |  | -388 | -122 | -12 | -3 | -3 | -43 | -64 | -4 | 662 | 662 | 662 | 4 | 4 | 4
1106 | Bornholm Energy Island (BEI) | TOOT | 160 | 166 | 157 | 399 | 56 | 61 | 51 | 553 | 555 | 548 | -378 | -347 | -412 | -15 | 73 | 182 | 194 | -3 | -7 | -8 | 8667 | 8680 | 8654 | 3000 | -97 | -34 | -4 | -1 | -1 | -12 | -510 | -29 | 805 | 805 | 805 | 10 | 10 | 10
1109 | Basilicata - Campania reinforcements | TOOT | 10 | 11 | 8 |  | 7 | 9 | 4 | 3 | 5 | 1 | -47 | -30 | -62 | 4 | 9 | 23 | 24 | 1 | 2 | 2 | 41 | 81 | 17 |  | -14 | -5 | -1 | 0 | 0 | -2 | -32 | -6 | 94 | 94 | 94 | 1 | 1 | 1
1110 | Sicily - Calabria | TOOT | 6 | 9 | 2 |  | 4 | 7 | 1 | 0 | 3 | -4 | -26 | -5 | -46 | 0 | 5 | 12 | 13 | 0 | 0 | 0 | -2 | 40 | -55 |  | -9 | -2 | -11 | 0 | -1 | -1 | 7 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1112 | GRITA 2 | TOOT | 212 | 213 | 211 |  | 112 | 114 | 111 | 64 | 66 | 62 | -765 | -752 | -773 | 7 | 147 | 368 | 394 | 1 | 4 | 4 | 986 | 1024 | 950 |  | -259 | -83 | -3 | -2 | -2 | -29 | 525 | 37 | 1279 | 1279 | 1279 | 16 | 16 | 16
1121 | 220-kV Hessenberg (AT) - Weißenbach (AT) | TOOT | 3 | 9 | 0 | 69 | 12 | 15 | 10 | 68 | 71 | 64 | -79 | -66 | -103 | 4 | 15 | 38 | 40 | 1 | 2 | 2 | 1053 | 1087 | 1001 | 600 | -33 | -9 | -5 | 0 | 0 | -3 | -95 | -2 | 4 | 4 | 4 | 0 | 0 | 0
1122 | Offshore Wind farm connection Centre Manche 1 | TOOT | 23 | 32 | 13 | 243 | 37 | 40 | 35 | 342 | 344 | 341 | -253 | -239 | -271 | 10 | 49 | 122 | 131 | 2 | 5 | 5 | 5347 | 5357 | 5338 | 1050 | -48 | -14 | -4 | 0 | -1 | -5 | 910 | 43 | 261 | 261 | 261 | 9 | 9 | 9
1123 | Offshore Wind farm connection Centre Manche 2 | TOOT | 23 | 32 | 13 | 243 | 37 | 40 | 35 | 342 | 344 | 341 | -253 | -239 | -271 | 8 | 49 | 122 | 131 | 1 | 4 | 4 | 5347 | 5357 | 5338 | 1250 | -48 | -14 | -4 | 0 | -1 | -5 | 659 | 31 | 261 | 261 | 261 | 9 | 9 | 9
1124 | Offshore Wind Connection South Britanny | TOOT | 16 | 19 | 14 | 152 | 23 | 24 | 22 | 200 | 203 | 196 | -156 | -150 | -161 | 7 | 30 | 75 | 81 | 1 | 3 | 4 | 3100 | 3140 | 3069 | 250 | -29 | -8 | -4 | 0 | 0 | -3 | 662 | 27 | 157 | 157 | 157 | 5 | 5 | 5
1125 | Offshore Wind Connection Occitanie | TOOT | 23 | 26 | 22 | 162 | 29 | 30 | 28 | 203 | 205 | 202 | -198 | -188 | -205 | 3 | 38 | 95 | 102 | 1 | 2 | 2 | 3148 | 3202 | 3089 | 250 | -44 | -13 | -6 | -1 | -1 | -4 | 73 | 6 | 157 | 157 | 157 | 5 | 5 | 5
1126 | Offshore Wind Connection PACA | TOOT | 22 | 22 | 21 | 159 | 33 | 41 | 27 | 199 | 204 | 195 | -221 | -181 | -279 | 2 | 43 | 107 | 114 | 0 | 1 | 1 | 3090 | 3210 | 2969 | 250 | -66 | -15 | -15 | -1 | -1 | -5 | -222 | -7 | 157 | 157 | 157 | 5 | 5 | 5
1127 | Offshore Wind Connection South Atlantic Oléron 1 | TOOT | 21 | 24 | 17 | 232 | 38 | 41 | 37 | 297 | 308 | 290 | -260 | -249 | -279 | 6 | 50 | 125 | 134 | 1 | 3 | 3 | 4599 | 4803 | 4417 | 1250 | -60 | -17 | -7 | -1 | -1 | -6 | 620 | 29 | 261 | 261 | 261 | 9 | 9 | 9
1134 | GiLA | PINT | 329 | 329 | 329 |  | 27 | 27 | 27 | 231 | 231 | 231 | -184 | -184 | -184 | 12 | 0 | 0 | 0 | 2 | 6 | 6 | 4522 | 4522 | 4522 |  | -80 | -25 | -2 | -1 | -1 | -9 | 756 | 33 | 0 | 0 | 0 | 0 | 0 | 0
1138 | 400 kV OHL Suceava (RO) - Balti (MD) | TOOT | 52 | 59 | 46 |  | 26 | 31 | 22 | 7 | 14 | 3 | -178 | -149 | -211 | 3 | 34 | 86 | 92 | 0 | 1 | 1 | 100 | 207 | 45 |  | -53 | -20 | -3 | 0 | 0 | -7 | 1629 | 106 | 226 | 226 | 226 | 3 | 3 | 3
1139 | 380-kV Westtirol (AT) – Zell/Ziller (AT) | PINT | 48 | 61 | 30 | 153 | 24 | 31 | 15 | 161 | 162 | 160 | -161 | -105 | -214 | -20 | 31 | 77 | 83 | -4 | -10 | -10 | 2572 | 2683 | 2494 | 1600 | -112 | -20 | -41 | -2 | -3 | -7 | -681 | -39 | 12 | 12 | 12 | 0 | 0 | 0
1140 | 380-kV St. Peter (AT) - Dürnrohr (AT) | PINT | 83 | 94 | 75 | 135 | 34 | 40 | 31 | 190 | 191 | 188 | -234 | -213 | -272 | -8 | 45 | 113 | 121 | -2 | -4 | -4 | 2943 | 2996 | 2859 | 1500 | -131 | -35 | -17 | -1 | -2 | -12 | -293 | -17 | 14 | 14 | 14 | 1 | 1 | 1
1145 | 380-kV Obersielach (AT) - Hessenberg (AT) | TOOT | 85 | 103 | 72 | 154 | 39 | 44 | 32 | 223 | 225 | 222 | -267 | -221 | -299 | -16 | 51 | 128 | 137 | -3 | -8 | -8 | 3439 | 3459 | 3420 | 2000 | -117 | -29 | -23 | -2 | -2 | -10 | -225 | -15 | 12 | 12 | 12 | 0 | 0 | 0
1153 | PST romands | TOOT | 104 | 124 | 90 |  | 40 | 56 | 25 | 16 | 16 | 16 | -269 | -167 | -382 | 4 | 52 | 129 | 139 | 1 | 2 | 2 | 246 | 252 | 241 |  | -173 | -51 | -14 | -2 | -2 | -18 | 729 | 37 | 1340 | 1340 | 1340 | 45 | 45 | 45
1155 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT) | TOOT | 21 | 32 | 11 | 410 | 71 | 81 | 61 | 401 | 406 | 393 | -486 | -413 | -552 | 3 | 93 | 234 | 250 | 0 | 1 | 1 | 6312 | 6332 | 6291 | 2000 | -216 | -58 | -34 | -3 | -3 | -20 | -132 | -6 | 12 | 12 | 12 | 0 | 0 | 0
1156 | 380-kV Greater Vienna (AT) - Hessenberg (AT) | TOOT | 18 | 26 | 7 | 319 | 56 | 66 | 46 | 318 | 328 | 308 | -379 | -313 | -452 | -8 | 73 | 182 | 195 | -2 | -4 | -4 | 4922 | 5136 | 4685 | 2500 | -173 | -46 | -28 | -2 | -3 | -16 | -213 | -12 | 12 | 12 | 12 | 0 | 0 | 0
1157 | HG North Tyrrhenian Corridor | TOOT | 239 | 240 | 238 |  | 90 | 97 | 86 | 94 | 102 | 82 | -615 | -585 | -661 | 51 | 118 | 296 | 317 | 10 | 25 | 26 | 1461 | 1587 | 1248 |  | -287 | -82 | -33 | -3 | -4 | -29 | 733 | 48 | 2527 | 2527 | 2527 | 37 | 37 | 37
1158 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT) | PINT | 2 | 5 | 0 | 223 | 32 | 38 | 29 | 222 | 222 | 221 | -219 | -195 | -256 | -1 | 42 | 105 | 113 | 0 | -1 | -1 | 3436 | 3469 | 3384 | 2000 | -127 | -30 | -28 | -2 | -2 | -11 | -191 | -10 | 12 | 12 | 12 | 0 | 0 | 0
1159 | 220-kV Bisamberg (AT) – Wien Südost (AT) | TOOT | 2 | 7 | 0 | 24 | 4 | 5 | 4 | 26 | 28 | 23 | -29 | -25 | -35 | 2 | 6 | 14 | 15 | 0 | 1 | 1 | 403 | 433 | 356 | 500 | -6 | -2 | 0 | 0 | 0 | -1 | -3 | 2 | 6 | 6 | 6 | 0 | 0 | 0
1161 | Offshore Wind Connection South Atlantic Oléron 2 | TOOT | 11 | 17 | 6 | 207 | 32 | 33 | 31 | 260 | 265 | 257 | -220 | -209 | -228 | 11 | 42 | 106 | 114 | 2 | 5 | 5 | 4034 | 4148 | 3914 | 1200 | -62 | -13 | -18 | -1 | -1 | -5 | 899 | 44 | 251 | 251 | 251 | 8 | 8 | 8
1162 | Offshore Wind Connection Fécamp-Grand Large 1 | TOOT | 20 | 21 | 19 | 345 | 56 | 58 | 51 | 438 | 447 | 428 | -379 | -346 | -396 | 2 | 73 | 182 | 195 | 0 | 1 | 1 | 6789 | 6987 | 6524 | 2000 | -102 | -23 | -25 | -1 | -2 | -8 | 453 | 26 | 418 | 418 | 418 | 14 | 14 | 14
1163 | Offshore Wind Connection Fécamp-Grand Large 2 | TOOT | 20 | 21 | 19 | 345 | 56 | 58 | 51 | 438 | 447 | 428 | -379 | -346 | -396 | 2 | 73 | 182 | 195 | 0 | 1 | 1 | 6789 | 6987 | 6524 | 2000 | -102 | -23 | -25 | -1 | -2 | -8 | 453 | 26 | 418 | 418 | 418 | 14 | 14 | 14
1164 | Offshore Wind Connection Golfe de Lion Centre | TOOT | 20 | 21 | 19 | 345 | 56 | 58 | 51 | 438 | 447 | 428 | -379 | -346 | -396 | -3 | 73 | 182 | 195 | -1 | -1 | -2 | 6789 | 6987 | 6524 | 2000 | -102 | -23 | -25 | -1 | -2 | -8 | -650 | -24 | 418 | 418 | 418 | 14 | 14 | 14
1165 | Offshore Wind Connection Golfe de Gascogne Sud | TOOT | 11 | 17 | 6 | 207 | 32 | 33 | 31 | 260 | 265 | 257 | -220 | -209 | -228 | 6 | 42 | 106 | 114 | 1 | 3 | 3 | 4034 | 4148 | 3914 | 1200 | -62 | -13 | -18 | -1 | -1 | -5 | 464 | 23 | 250 | 250 | 250 | 8 | 8 | 8
1166 | HG Adriatic Corridor | PINT | 110 | 115 | 105 |  | 36 | 41 | 32 | 43 | 52 | 38 | -247 | -218 | -276 | 10 | 47 | 119 | 127 | 2 | 5 | 5 | 672 | 805 | 602 |  | -121 | -35 | -12 | -1 | -1 | -12 | 404 | 30 | 35 | 35 | 35 | 1 | 1 | 1
1167 | HG Central link | TOOT | 8 | 14 | 4 |  | 4 | 8 | 3 | 3 | 6 | -1 | -30 | -20 | -54 | 10 | 6 | 14 | 15 | 2 | 5 | 5 | 37 | 87 | -14 |  | -11 | -2 | -4 | 0 | 0 | -1 | 288 | 14 | 326 | 326 | 326 | 4 | 4 | 4
1168 | HG Ionian-Tyrrhenian Corridor | TOOT | 31 | 33 | 26 |  | 13 | 16 | 10 | 8 | 8 | 7 | -85 | -71 | -109 | 10 | 16 | 41 | 44 | 2 | 5 | 5 | 112 | 128 | 87 |  | -47 | -13 | -6 | -1 | -1 | -5 | 187 | 7 | 45 | 45 | 45 | 1 | 1 | 1
1169 | SAPEI 2 | PINT | 17 | 22 | 11 |  | 4 | 8 | -2 | -2 | 4 | -13 | -30 | 11 | -57 | -8 | 6 | 14 | 15 | -1 | -4 | -4 | -40 | 58 | -195 |  | -30 | -7 | -5 | 0 | 0 | -3 | 56 | 6 | 3 | 3 | 3 | 0 | 0 | 0
1171 | Interconnection IT-CH | PINT | 119 | 137 | 106 |  | 67 | 67 | 67 | 13 | 17 | 11 | -455 | -453 | -456 | 3 | 87 | 219 | 234 | 1 | 2 | 2 | 208 | 262 | 166 |  | -211 | -71 | -2 | -2 | -1 | -25 | 347 | 22 | 69 | 69 | 69 | 1 | 1 | 1
1182 | EHV S/S Thesprotias and its connection to the 400 kV System | Light PINT | 8 | 13 | 0 |  | 6 | 8 | 2 | -3 | 7 | -17 | -39 | -12 | -56 |  | 8 | 19 | 20 |  |  |  | -47 | 116 | -257 |  | -40 | -8 | -9 | -1 | -1 | -3 |  |  | 7 | 7 | 7 | 0 | 0 | 0
1183 | New interconnection line 400 kV Greece - Albania | Light PINT | 8 | 12 | 5 |  | 2 | 4 | -1 | 1 | 5 | -2 | -14 | 7 | -26 |  | 3 | 7 | 7 |  |  |  | 20 | 75 | -34 |  | -19 | -4 | -4 | 0 | 0 | -2 |  |  | 5 | 5 | 5 | 0 | 0 | 0
1185 | South Coast Offshore Transmission Project | TOOT | 16 | 37 | 2 | 56 | 19 | 26 | 15 | 69 | 78 | 59 | -126 | -100 | -176 | 0 | 24 | 61 | 65 | 0 | 0 | 0 | 1067 | 1226 | 923 | 800 | -24 | -2 | -14 | -1 | -1 | -1 | 17 | 1 | 54 | 54 | 54 | 1 | 1 | 1
1192 | HansaLink - Phase 1 | PINT | 518 | 518 | 518 | 240 | 56 | 68 | 44 | 583 | 584 | 582 | -381 | -301 | -460 | -14 | 73 | 183 | 196 | -3 | -7 | -7 | 9103 | 9133 | 9073 | 2000 | -328 | -56 | -134 | -6 | -9 | -21 | -255 | -22 | 2249 | 2249 | 2249 | 28 | 28 | 28
1193 | HansaLink - Phase 2 | PINT | 7 | 14 | 0 | 232 | 55 | 56 | 55 | 286 | 297 | 275 | -376 | -372 | -379 | 1 | 72 | 181 | 194 | 0 | 1 | 1 | 4526 | 4528 | 4525 | 2000 | -69 | -12 | -23 | -1 | -2 | -5 | -235 | -9 | 193 | 193 | 193 | 23 | 23 | 23
1197 | NU-Link Interconnector | PINT | 205 | 233 | 169 |  | -27 | -25 | -29 | 118 | 141 | 91 | 184 | 195 | 173 | 10 | 0 | 0 | 0 | 2 | 5 | 5 | 1828 | 2151 | 1430 |  | -80 | -18 | -22 | -1 | -2 | -6 | 128 | 3 | 210 | 210 | 210 | 5 | 5 | 5
1200 | Hybrid interconnector Norway-Sørvest F Windfarm-Continent (DK, DE or BE) | PINT | 704 | 705 | 703 |  | 66 | 74 | 57 | 516 | 526 | 506 | -446 | -388 | -505 | 20 | 86 | 215 | 230 | 4 | 10 | 11 | 8108 | 8274 | 7943 |  | -228 | -51 | -63 | -3 | -4 | -18 | 248 | 14 | 868 | 868 | 868 | 11 | 11 | 11
1201 | Reinvestment of Skagerrak 1 and 2 | PINT | 180 | 202 | 162 |  | 22 | 30 | 18 | 135 | 150 | 118 | -148 | -119 | -201 | 1 | 28 | 71 | 76 | 0 | 0 | 0 | 2098 | 2361 | 1799 |  | -96 | -10 | -51 | -2 | -3 | -4 | 208 | 4 | 234 | 234 | 234 | 4 | 4 | 4
1202 | Increased capacity Norway-Finland, Back-to-Back | PINT | 33 | 35 | 30 |  | 3 | 4 | 2 | 23 | 28 | 16 | -21 | -15 | -24 | 0 | 4 | 10 | 11 | 0 | 0 | 0 | 352 | 421 | 255 |  | -17 | -1 | -15 | -1 | -1 | 0 | 156 | 6 | 55 | 55 | 55 | 1 | 1 | 1
1203 | Offshore Wind Connection Bretagne Nord-Ouest | PINT | 17 | 23 | 12 | 215 | 33 | 35 | 30 | 277 | 280 | 274 | -222 | -207 | -239 | 5 | 43 | 107 | 114 | 1 | 2 | 2 | 4066 | 4359 | 3662 | 1200 | -67 | -14 | -19 | -1 | -1 | -5 | 904 | 43 | 251 | 251 | 251 | 8 | 8 | 8
1207 | 380kV Niederstedem-Bertrange/Bofferdange | PINT | 2 | 4 | 1 |  | -2 | 0 | -5 | 1 | 2 | 1 | 12 | 32 | -1 | 13 | 0 | 0 | 0 | 3 | 6 | 7 | 19 | 27 | 11 |  | -13 | -1 | -11 | 0 | -1 | 0 | 190 | 11 | 0 | 0 | 0 | 0 | 0 | 0
1208 | Medlink | PINT | 517 | 539 | 496 | 912 | 378 | 403 | 356 | 1334 | 1350 | 1320 | -2571 | -2419 | -2742 | 105 | 494 | 1236 | 1324 | 20 | 51 | 54 | 20661 | 21040 | 20104 | 9016 | -1092 | -325 | -78 | -10 | -11 | -114 | 1068 | 104 | 18 | 18 | 18 | 0 | 0 | 0
1209 | Latvia and Lithuania cross-border strengthening project | PINT | 39 | 48 | 26 |  | 9 | 12 | 4 | 13 | 27 | 1 | -61 | -27 | -82 | 1 | 12 | 30 | 32 | 0 | 0 | 0 | 204 | 417 | 17 |  | -55 | -2 | -38 | -1 | -2 | -1 | -70 | 0 | 265 | 265 | 265 | 3 | 3 | 3
1210 | APOLLO-LINK | Light PINT | 860 | 863 | 858 |  | 258 | 278 | 242 | 472 | 484 | 464 | -1755 | -1646 | -1889 |  | 337 | 844 | 904 |  |  |  | 7303 | 7552 | 7135 |  | -877 | -271 | -39 | -8 | -8 | -95 |  |  | 302 | 302 | 302 | 3 | 3 | 3
1211 | Baltic WindConnector (BWC) | PINT | 544 | 592 | 506 | 142 | 60 | 67 | 56 | 495 | 519 | 473 | -409 | -379 | -455 | 21 | 79 | 197 | 211 | 4 | 10 | 11 | 7673 | 8101 | 7201 | 2000 | -87 | -43 | -11 | 0 | -1 | -14 | 332 | 23 | 1594 | 1594 | 1594 | 21 | 21 | 21
1213 | Offshore hybrid Interconnector (DE-NL) | Light PINT | 142 | 143 | 141 |  | 16 | 18 | 12 | 56 | 63 | 52 | -107 | -84 | -120 |  | 20 | 51 | 55 |  |  |  | 873 | 986 | 788 |  | -96 | -16 | -42 | -2 | -3 | -6 |  |  | 418 | 418 | 418 | 7 | 7 | 7
1214 | Hybrid Interconnector Denmark-Germany | TOOT | 547 | 583 | 497 | 86 | 51 | 58 | 46 | 554 | 566 | 539 | -348 | -313 | -396 | 103 | 67 | 167 | 179 | 20 | 50 | 53 | 8610 | 8784 | 8428 | 2000 | -243 | -39 | -100 | -5 | -6 | -14 | 2352 | 145 | 0 | 0 | 0 | 0 | 0 | 0
1215 | Xlinks Morocco - Germany | PINT | 1551 | 1621 | 1467 | 252 | 192 | 205 | 179 | 1535 | 1550 | 1513 | -1308 | -1217 | -1395 | 262 | 251 | 629 | 674 | 50 | 126 | 135 | 23632 | 23659 | 23605 | 15200 | -753 | -112 | -343 | -15 | -22 | -42 | 6635 | 284 | 130 | 130 | 130 | 3 | 3 | 3
1216 | High-Voltage Direct Current Interconnector Project Romania-Hungary | PINT | 21 | 24 | 17 |  | 1 | 8 | -2 | 1 | 6 | -4 | -8 | 16 | -53 | 13 | 2 | 4 | 4 | 2 | 6 | 7 | 22 | 90 | -49 |  | -5 | -1 | -10 | 0 | 0 | 0 | 5 | 1 | 36 | 36 | 36 | 0 | 0 | 0
1217 | Further Development of Offshore Renewables (MOG 3) | Light PINT | 16 | 17 | 15 | 360 | 37 | 38 | 37 | 429 | 434 | 424 | -254 | -252 | -255 |  | 49 | 122 | 131 |  |  |  | 6610 | 6610 | 6610 |  | -95 | -22 | -23 | -1 | -2 | -8 |  |  | 454 | 454 | 454 | 5 | 5 | 5
1218 | Hybrid HVDC Interconnector BE-NL | Light PINT | 34 | 34 | 33 |  | 8 | 10 | 5 | 20 | 22 | 19 | -54 | -36 | -69 |  | 10 | 26 | 28 |  |  |  | 319 | 336 | 301 |  | -52 | -13 | -9 | -1 | -1 | -5 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1219 | Bofferdange- Bertrange | Light PINT | 27 | 28 | 26 |  | 1 | 2 | -1 | 7 | 8 | 6 | -7 | 5 | -16 |  | 1 | 3 | 4 |  |  |  | 112 | 136 | 95 |  | -10 | -2 | -5 | 0 | 0 | -1 |  |  | 81 | 81 | 81 | 1 | 1 | 1
1220 | Offshore Wind Connection Viana do Castelo | TOOT | 8 | 13 | 0 | 45 | 8 | 12 | 5 | 155 | 157 | 152 | -51 | -32 | -79 | 3 | 10 | 25 | 26 | 0 | 1 | 1 | 2210 | 2453 | 1862 | 2000 | 0 | -2 | -5 | 0 | 0 | -1 | 139 | 6 | 273 | 273 | 273 | 3 | 3 | 3
1221 | Offshore Wind Connection Leixões | TOOT | 4 | 9 | 0 | 36 | 7 | 11 | 5 | 112 | 117 | 104 | -46 | -32 | -74 | 0 | 9 | 22 | 24 | 0 | 0 | 0 | 1731 | 1826 | 1631 | 1500 | -7 | -2 | 0 | 0 | 0 | -1 | 134 | 5 | 206 | 206 | 206 | 2 | 2 | 2
1222 | Offshore Wind Connection Figueira da Foz (North) | TOOT | 20 | 25 | 10 | 33 | 8 | 12 | 5 | 155 | 157 | 152 | -51 | -32 | -79 | 1 | 10 | 25 | 26 | 0 | 0 | 1 | 2210 | 2453 | 1862 | 2000 | 0 | -2 | -5 | 0 | 0 | -1 | 120 | 6 | 277 | 277 | 277 | 3 | 3 | 3
1223 | Offshore Wind Connection Figueira da Foz (South) | TOOT | 20 | 25 | 10 | 33 | 8 | 12 | 5 | 155 | 157 | 152 | -51 | -32 | -79 | 1 | 10 | 25 | 26 | 0 | 0 | 1 | 2210 | 2453 | 1862 | 2000 | 0 | -2 | -5 | 0 | 0 | -1 | 133 | 6 | 276 | 276 | 276 | 3 | 3 | 3
1224 | Offshore Wind Connection Ericeira | TOOT | 9 | 19 | 4 | 24 | 7 | 11 | 3 | 74 | 75 | 73 | -46 | -22 | -75 | 1 | 9 | 22 | 24 | 0 | 0 | 0 | 1144 | 1172 | 1116 | 1000 | -3 | -5 | -11 | 0 | -1 | -1 | 15 | 3 | 133 | 133 | 133 | 1 | 1 | 1
1225 | Offshore Wind Connection Sines | TOOT | 16 | 21 | 10 | 24 | 7 | 11 | 5 | 112 | 117 | 104 | -46 | -32 | -74 | -1 | 9 | 22 | 24 | 0 | 0 | 0 | 1731 | 1826 | 1631 | 1500 | -7 | -2 | 0 | 0 | 0 | -1 | -63 | 3 | 202 | 202 | 202 | 2 | 2 | 2
1226 | North-South Electricity Corridor in Eastern Europe | Light PINT | 214 | 309 | 148 |  | 63 | 64 | 61 | 20 | 38 | 7 | -427 | -416 | -437 |  | 82 | 205 | 220 |  |  |  | 309 | 584 | 119 |  | -303 | -98 | -9 | -2 | -2 | -34 |  |  | 150 | 150 | 150 | 2 | 2 | 2
1229 | Rhine-Main-Link | PINT | 1653 | 1994 | 1409 |  | 99 | 125 | 79 | 650 | 795 | 547 | -676 | -536 | -852 | 47 | 130 | 325 | 348 | 9 | 23 | 24 | 5 | 8 | 1 |  | -234 | -74 | -7 | -2 | -2 | -26 | 1451 | 69 | 0 | 0 | 0 | 0 | 0 | 0
1230 | TuNur Malta | PINT | 16 | 19 | 13 | 199 | 67 | 69 | 66 | 196 | 201 | 191 | -456 | -450 | -469 | 0 | 88 | 219 | 235 | 0 | 0 | 0 | 3035 | 3060 | 2988 | 1400 | -197 | -61 | -8 | -2 | -2 | -21 | -98 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1231 | Green Aegean Interconnector | Light PINT | 1152 | 1241 | 1088 |  | 417 | 441 | 394 | 307 | 309 | 304 | -2839 | -2677 | -2998 |  | 545 | 1366 | 1462 |  |  |  | 4733 | 4762 | 4704 |  | -1067 | -291 | -154 | -12 | -15 | -103 |  |  | 2377 | 2377 | 2377 | 32 | 32 | 32
1233 | Laufenburg - Beznau - Breite | Light PINT | 123 | 142 | 105 |  | 45 | 50 | 36 | 105 | 122 | 82 | -307 | -243 | -343 |  | 59 | 148 | 158 |  |  |  | 1622 | 1914 | 1282 |  | -146 | -54 | -13 | -1 | 0 | -19 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1234 | 220-kV Reitdorf (AT) - Weißenbach (AT) | TOOT | 4 | 11 | 0 | 51 | 10 | 13 | 7 | 52 | 60 | 48 | -65 | -50 | -86 | 1 | 13 | 31 | 34 | 0 | 1 | 1 | 808 | 933 | 743 | 500 | -27 | -8 | -4 | 0 | 0 | -3 | -59 | -1 | 4 | 4 | 4 | 0 | 0 | 0
1235 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | PINT | 8 | 13 | 6 |  | 3 | 5 | -1 | 2 | 4 | 1 | -19 | 4 | -31 | -1 | 4 | 9 | 10 | 0 | -1 | -1 | 34 | 67 | 13 |  | -34 | -6 | -12 | -1 | -1 | -2 | -445 | -28 | 13 | 13 | 13 | 0 | 0 | 0
1236 | Power-to-Gas for Austria (P2G4A) | PINT | 1 | 1 | 0 |  | 1 | 3 | -2 | -2 | 2 | -8 | -4 | 10 | -23 | 3 | 1 | 2 | 2 | 1 | 1 | 2 | -25 | 35 | -128 |  | -2 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0
1239 | Interconnection Ukraine-Slovak Republic | Light PINT | 74 | 79 | 68 |  | 26 | 52 | -3 | -1 | 8 | -12 | -179 | 20 | -352 |  | 34 | 86 | 92 |  |  |  | -18 | 125 | -186 |  | -239 | -18 | -195 | -7 | -13 | -7
1240 | Interconnection Ukraine-Romania | Light PINT | 89 | 89 | 88 |  | 47 | 49 | 46 | -5 | -1 | -10 | -322 | -312 | -332 |  | 62 | 155 | 166 |  |  |  | -87 | -19 | -154 |  | -439 | -30 | -378 | -14 | -25 | -11

## 2040DE
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 89 | 94 | 83 | 130.4 | 43 | 51 | 32 | 238 | 281 | 180 | -293 | -219 | -349 | 1 | 56 | 141 | 151 | 0 | 1 | 1 | 3375 | 3948 | 2572 | 1154 | -70 | -8 | -29 | -1 | -2 | -3 | 345 | 15 | 3425 | 3425 | 3425 | 30 | 30 | 30
4 | Interconnection Portugal-Spain | TOOT | 142 | 145 | 140 |  | 29 | 31 | 26 | 142 | 151 | 130 | -198 | -179 | -212 | 3 | 38 | 95 | 102 | 0 | 1 | 1 | 2016 | 2164 | 1864 |  | -49 | -9 | -16 | -1 | -1 | -3 | 58 | 9 | 546 | 546 | 546 | 3 | 3 | 3
16 | Biscay Gulf | TOOT | 353 | 360 | 347 |  | 82 | 88 | 75 | 213 | 215 | 212 | -557 | -508 | -596 | 36 | 107 | 268 | 287 | 7 | 17 | 19 | 3024 | 3080 | 2969 |  | -187 | -43 | -39 | -2 | -3 | -15 | 3406 | 128 | 3624 | 3624 | 3624 | 52 | 52 | 52
28 | Italy-Montenegro | TOOT | 100 | 104 | 95 |  | 35 | 36 | 35 | 33 | 35 | 31 | -240 | -235 | -245 | 8 | 46 | 115 | 124 | 2 | 4 | 4 | 474 | 500 | 448 |  | -101 | -34 | 0 | -1 | 0 | -12 | 228 | 11 | 288 | 288 | 288 | 0 | 0 | 0
29 | Italy-Tunisia | TOOT | 246 | 264 | 224 |  | 89 | 91 | 88 | 90 | 94 | 87 | -603 | -596 | -616 | 0 | 116 | 290 | 311 | 0 | 0 | 0 | 1283 | 1325 | 1247 |  | -355 | -112 | -13 | -3 | -3 | -39 | -138 | -10 | 1071 | 1071 | 1071 | 10 | 10 | 10
33 | Central Northern Italy | TOOT | 41 | 43 | 38 |  | 13 | 14 | 11 | 19 | 22 | 16 | -87 | -76 | -97 | -4 | 17 | 43 | 46 | -1 | -2 | -2 | 253 | 314 | 188 |  | -40 | -12 | -3 | 0 | 0 | -4 | 62 | -4 | 261 | 261 | 261 | 3 | 3 | 3
35 | CZ Southwest-east corridor | TOOT | 200 | 205 | 197 |  | 49 | 52 | 47 | 65 | 66 | 63 | -335 | -323 | -351 | 25 | 64 | 161 | 172 | 5 | 12 | 13 | 927 | 948 | 902 |  | -236 | -66 | -42 | -3 | -3 | -23 | 427 | 22 | 439 | 439 | 439 | 5 | 5 | 5
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 59 | 69 | 52 |  | 6 | 7 | 4 | 31 | 34 | 27 | -37 | -28 | -47 |  | 7 | 18 | 19 |  |  |  | 440 | 482 | 383 |  | -14 | 0 | -12 | 0 | -1 | 0 |  |  | 655 | 655 | 655 | 8 | 8 | 8
47 | Westtirol (AT) - Vöhringen (DE) | TOOT | 102 | 108 | 97 |  | 13 | 17 | 12 | 43 | 45 | 41 | -91 | -79 | -115 | 7 | 17 | 44 | 47 | 1 | 3 | 4 | 611 | 642 | 588 |  | -33 | -5 | -12 | -1 | -1 | -2 | 84 | -8 | 716 | 716 | 716 | 9 | 9 | 9
81 | North South Interconnector | TOOT | 240 | 246 | 235 |  | 68 | 69 | 68 | 119 | 126 | 113 | -465 | -460 | -468 | 4 | 89 | 224 | 239 | 1 | 2 | 2 | 1690 | 1804 | 1612 |  | -418 | -64 | -152 | -7 | -9 | -25 | 41 | 5 | 302 | 302 | 302 | 3 | 3 | 3
85 | Integration of RES in Alentejo | TOOT | 0 | 4 | 0 | 8 | 2 | 2 | 1 | 9 | 11 | 8 | -11 | -10 | -12 | -1 | 2 | 5 | 6 | 0 | -1 | -1 | 131 | 156 | 110 | 700 | 4 | 1 | 0 | 0 | 0 | 0 | -37 | -2 | 0 | 0 | 0 | 0 | 0 | 0
94 | GerPol Improvements | TOOT | 303 | 303 | 302 |  | 40 | 43 | 38 | 106 | 109 | 104 | -271 | -258 | -291 | 15 | 52 | 130 | 140 | 3 | 7 | 8 | 1511 | 1559 | 1456 |  | -209 | -39 | -95 | -4 | -7 | -14 | 385 | 20 | 1795 | 1795 | 1795 | 23 | 23 | 23
107 | Celtic Interconnector | TOOT | 213 | 216 | 208 |  | 34 | 38 | 31 | 164 | 167 | 162 | -229 | -212 | -260 | 26 | 44 | 110 | 118 | 5 | 12 | 13 | 2340 | 2401 | 2283 |  | -88 | -28 | -7 | -1 | -1 | -10 | 1091 | 54 | 1295 | 1295 | 1295 | 13 | 13 | 13
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 62 | 68 | 55 |  | 6 | 6 | 5 | 43 | 44 | 42 | -38 | -33 | -42 | 2 | 7 | 18 | 20 | 0 | 1 | 1 | 615 | 638 | 594 |  | -47 | -3 | -31 | -1 | -2 | -1 | 60 | 2 | 1052 | 1052 | 1052 | 8 | 8 | 8
120 | Princess Elisabeth Island (MOG 2) | TOOT | 332 | 339 | 324 | 594 | 100 | 109 | 92 | 845 | 855 | 835 | -683 | -623 | -743 | 25 | 131 | 328 | 352 | 5 | 12 | 13 | 11989 | 12000 | 11979 | 3500 | -435 | -55 | -229 | -10 | -15 | -21 | 296 | 28 | 4126 | 4126 | 4126 | 175 | 175 | 175
121 | Nautilus: multi-purpose interconnector Belgium - UK | TOOT | 207 | 209 | 205 |  | 6 | 10 | 2 | 76 | 83 | 71 | -41 | -14 | -71 | 12 | 8 | 20 | 21 | 2 | 6 | 6 | 1080 | 1184 | 999 |  | -75 | -19 | -9 | -1 | -1 | -7 | 97 | 8 | 1088 | 1088 | 1088 | 52 | 52 | 52
124 | Ekhyddan-Nybro-Hemsjö | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 60 | 73 | 45 |  | 7 | 13 | 2 | 15 | 16 | 15 | -47 | -12 | -86 | 21 | 9 | 23 | 24 | 4 | 10 | 11 | 221 | 234 | 208 |  | -29 | -4 | -19 | -1 | -1 | -1 | 154 | 14 | 73 | 73 | 73 | 0 | 0 | 0
127 | Central Southern Italy | TOOT | 15 | 22 | 8 |  | 6 | 8 | 4 | 2 | 6 | -2 | -49 | -30 | -73 | 18 | 8 | 20 | 21 | 3 | 8 | 9 | 31 | 84 | -25 |  | -28 | -8 | -5 | 0 | 0 | -3 | 145 | 6 | 408 | 408 | 408 | 0 | 0 | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 606 | 699 | 541 |  | 15 | 19 | 13 | 225 | 270 | 195 | -105 | -90 | -128 | 8 | 20 | 50 | 54 | 1 | 4 | 4 | 2 | 3 | 2 |  | -79 | -25 | -2 | -1 | -1 | -9 | 241 | 8 | 0 | 0 | 0 | 0 | 0 | 0
132 | HVDC Line A-North | TOOT | 970 | 1172 | 841 |  | 25 | 32 | 20 | 357 | 452 | 294 | -168 | -139 | -216 | 47 | 32 | 81 | 87 | 9 | 23 | 24 | 4 | 5 | 3 |  | -127 | -40 | -4 | -1 | -1 | -14 | 988 | 56 | 0 | 0 | 0 | 0 | 0 | 0
138 | Black Sea Corridor | TOOT | 12 | 15 | 10 |  | 5 | 7 | 4 | 4 | 9 | 0 | -36 | -29 | -45 | -10 | 7 | 17 | 18 | -2 | -5 | -5 | 51 | 125 | 0 |  | -15 | -5 | -2 | 0 | 0 | -2 | -1 | -3 | 471 | 471 | 471 | 0 | 0 | 0
144 | Mid Continental East corridor | TOOT | 35 | 38 | 33 |  | 14 | 19 | 12 | 4 | 5 | 3 | -97 | -81 | -127 | 4 | 19 | 47 | 50 | 1 | 2 | 2 | 59 | 68 | 46 |  | -56 | -2 | -81 | -2 | -3 | -1 | -8 | -1 | 855 | 855 | 855 | 7 | 7 | 7
150 | Italy-Slovenia | TOOT | 57 | 59 | 55 |  | 25 | 30 | 20 | 10 | 14 | 9 | -173 | -133 | -203 | 12 | 33 | 83 | 89 | 2 | 6 | 6 | 149 | 194 | 122 |  | -79 | -19 | -46 | -2 | -2 | -7 | 142 | 10 | 234 | 234 | 234 | 3 | 3 | 3
153 | France-Alderney-Britain | TOOT | 240 | 246 | 237 |  | 31 | 32 | 28 | 179 | 181 | 177 | -208 | -189 | -220 | 17 | 40 | 100 | 107 | 3 | 8 | 9 | 2666 | 2898 | 2493 |  | -71 | -16 | -14 | -1 | -1 | -6 | 1134 | 61 | 832 | 832 | 832 | 23 | 23 | 23
170 | Baltic States Synchronization with Continental Europe | TOOT | 177 | 178 | 175 |  | 80 | 81 | 78 | 78 | 79 | 77 | -544 | -533 | -551 | 2 | 104 | 262 | 280 | 0 | 1 | 1 | 1109 | 1115 | 1105 |  | -301 | -51 | -194 | -7 | -13 | -18 | 157 | 10 | 1241 | 1241 | 1241 | 21 | 21 | 21
174 | Greenconnector | TOOT | 112 | 126 | 99 |  | 53 | 58 | 47 | 24 | 28 | 20 | -358 | -318 | -397 | 36 | 69 | 172 | 184 | 7 | 18 | 19 | 342 | 384 | 284 |  | -177 | -55 | -6 | -2 | -1 | -19 | 545 | 36 | 714 | 714 | 714 | 22 | 22 | 22
176 | Hansa PowerBridge I | TOOT | 160 | 163 | 155 |  | 11 | 15 | 9 | 86 | 87 | 84 | -77 | -63 | -100 | -2 | 15 | 37 | 40 | 0 | -1 | -1 | 1228 | 1257 | 1184 |  | -39 | -12 | 1 | 0 | 0 | -4 | 21 | 0 | 1323 | 1323 | 1323 | 16 | 16 | 16
187 | St. Peter (AT) - Pleinting (DE) | TOOT | 482 | 492 | 469 |  | 62 | 69 | 56 | 201 | 208 | 194 | -425 | -384 | -467 | 53 | 82 | 204 | 219 | 10 | 26 | 27 | 2852 | 2915 | 2776 |  | -195 | -31 | -76 | -4 | -5 | -12 | 1576 | 72 | 4204 | 4204 | 4204 | 51 | 51 | 51
200 | CZ Northwest-South corridor | TOOT | 200 | 205 | 197 |  | 49 | 52 | 47 | 65 | 66 | 63 | -335 | -323 | -351 | -10 | 64 | 161 | 172 | -2 | -5 | -5 | 927 | 948 | 902 |  | -236 | -66 | -42 | -3 | -3 | -23 | 273 | 8 | 444 | 444 | 444 | 5 | 5 | 5
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 34 | 35 | 33 |  | 12 | 13 | 12 | 10 | 13 | 6 | -84 | -79 | -91 | 2 | 16 | 40 | 43 | 0 | 1 | 1 | 139 | 180 | 83 |  | -42 | -12 | -6 | 0 | 0 | -4 | 33 | 2 | 85 | 85 | 85 | 1 | 1 | 1
219 | Great Sea Interconnector | TOOT | 390 | 408 | 377 |  | 118 | 122 | 115 | 135 | 138 | 133 | -802 | -783 | -829 | 73 | 154 | 386 | 413 | 14 | 35 | 38 | 1919 | 1984 | 1862 |  | -554 | -175 | -17 | -5 | -5 | -61 | -2308 | -168 | 1613 | 1613 | 1613 | 16 | 16 | 16
225 | 2nd interconnector Belgium - Germany | light PINT | 199 | 201 | 198 |  | 19 | 24 | 12 | 116 | 122 | 109 | -129 | -82 | -163 | 13 | 25 | 62 | 67 | 3 | 6 | 7 | 1645 | 1707 | 1565 |  | -69 | -4 | -61 | -2 | -4 | -2 | 900 | 47 | 1837 | 1837 | 1837 | 22 | 22 | 22
227 | Transbalkan Corridor | TOOT | 98 | 100 | 97 |  | 52 | 57 | 43 | 15 | 24 | 9 | -351 | -293 | -389 | -12 | 67 | 169 | 181 | -2 | -6 | -6 | 220 | 336 | 125 |  | -314 | -87 | -81 | -4 | -5 | -31 | -97 | -7 | 1686 | 1686 | 1686 | 18 | 18 | 18
228 | Muhlbach - Eichstetten | TOOT | 70 | 71 | 68 |  | 4 | 5 | 3 | 34 | 39 | 29 | -25 | -20 | -33 | 6 | 5 | 12 | 13 | 1 | 3 | 3 | 484 | 561 | 405 |  | -18 | -5 | -3 | 0 | 0 | -2 | 188 | 9 | 567 | 567 | 567 | 7 | 7 | 7
231 | Beznau - Tiengen | TOOT | 81 | 87 | 75 |  | 21 | 28 | 16 | 63 | 66 | 60 | -144 | -108 | -193 | 8 | 28 | 69 | 74 | 1 | 4 | 4 | 892 | 944 | 853 |  | -87 | -26 | -5 | -1 | -1 | -9 | 73 | -10 | 115 | 115 | 115 | 1 | 1 | 1
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 1438 | 1656 | 1233 |  | 34 | 43 | 29 | 508 | 619 | 423 | -232 | -198 | -290 | 74 | 45 | 112 | 120 | 14 | 35 | 38 | 5 | 6 | 4 |  | -176 | -55 | -5 | -1 | -1 | -19 | 1955 | 101 | 0 | 0 | 0 | 0 | 0 | 0
239 | Fenno-Skan 3 | Light PINT | 62 | 70 | 59 |  | 4 | 5 | 4 | 47 | 52 | 42 | -30 | -26 | -33 |  | 6 | 15 | 16 |  |  |  | 665 | 745 | 592 |  | -58 | -3 | -32 | -1 | -2 | -2 |  |  | 154 | 154 | 154 | 1 | 1 | 1
243 | New 400 kV interconnection line between Serbia and Croatia | Light PINT | 16 | 27 | 8 |  | 9 | 9 | 8 | 3 | 7 | 1 | -59 | -53 | -64 |  | 11 | 28 | 30 |  |  |  | 42 | 100 | 8 |  | -32 | -11 | 3 | 0 | 0 | -4 |  |  | 5 | 5 | 5 | 0 | 0 | 0
244 | Vigy - Uchtelfangen area | TOOT | 356 | 364 | 347 |  | 24 | 27 | 20 | 157 | 158 | 156 | -161 | -134 | -186 | 57 | 31 | 78 | 83 | 11 | 27 | 29 | 2236 | 2246 | 2226 |  | -137 | -24 | -58 | -3 | -4 | -9 | 1098 | 62 | 2888 | 2888 | 2888 | 35 | 35 | 35
247 | AQUIND Interconnector | TOOT | 413 | 421 | 408 |  | 56 | 62 | 51 | 307 | 309 | 306 | -382 | -346 | -420 | 20 | 73 | 184 | 197 | 4 | 10 | 10 | 4373 | 4402 | 4345 |  | -121 | -27 | -24 | -2 | -2 | -10 | 876 | 51 | 1679 | 1679 | 1679 | 43 | 43 | 43
250 | Merchant line Castasegna (CH) - Mese (IT) | TOOT | 19 | 20 | 19 |  | 10 | 14 | 8 | 5 | 6 | 3 | -70 | -52 | -93 | 5 | 13 | 34 | 36 | 1 | 2 | 3 | 69 | 94 | 43 |  | -33 | -12 | 4 | 0 | 0 | -4 | 26 | 4 | 79 | 79 | 79 | 3 | 3 | 3
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 276 | 313 | 236 |  | 5 | 5 | 5 | 80 | 88 | 74 | -33 | -31 | -35 | 36 | 6 | 16 | 17 | 7 | 18 | 19 | 1 | 1 | 1 |  | -25 | -8 | -1 | 0 | 0 | -3 | 845 | 46 | 0 | 0 | 0 | 0 | 0 | 0
259 | HU-RO | TOOT | 46 | 51 | 42 |  | 7 | 8 | 6 | 2 | 3 | 2 | -49 | -42 | -57 | 48 | 9 | 23 | 25 | 9 | 23 | 25 | 34 | 40 | 26 |  | -45 | -3 | -27 | -1 | -2 | -1 | 203 | 18 | 979 | 979 | 979 | 9 | 9 | 9
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | TOOT | 269 | 271 | 268 |  | 12 | 18 | 5 | 105 | 115 | 96 | -80 | -32 | -123 | 39 | 15 | 39 | 41 | 8 | 19 | 20 | 1498 | 1644 | 1382 |  | -99 | -23 | -27 | -1 | -2 | -8 | 450 | 33 | 1139 | 1139 | 1139 | 43 | 43 | 43
267 | Hansa PowerBridge II | Light PINT | 160 | 163 | 155 |  | 11 | 15 | 9 | 86 | 87 | 84 | -77 | -63 | -100 | -2 | 15 | 37 | 40 | 0 | -1 | -1 | 1228 | 1257 | 1184 |  | -39 | -12 | 1 | 0 | 0 | -4 | 21 | 0 | 1323 | 1323 | 1323 | 16 | 16 | 16
270 | FR-ES project -Aragón-Atlantic Pyrenees | TOOT | 228 | 231 | 226 |  | 57 | 60 | 53 | 149 | 154 | 144 | -385 | -357 | -409 | 19 | 74 | 185 | 198 | 4 | 9 | 10 | 2114 | 2166 | 2063 |  | -142 | -29 | -35 | -2 | -2 | -11 | 1764 | 68 | 2290 | 2290 | 2290 | 31 | 31 | 31
276 | FR-ES project -Navarra-Landes | PINT | 204 | 206 | 203 |  | 50 | 51 | 50 | 129 | 130 | 128 | -342 | -337 | -346 | 32 | 66 | 165 | 176 | 6 | 15 | 16 | 1829 | 1837 | 1820 |  | -49 | -19 | 8 | 0 | 0 | -7 | 2571 | 103 | 834 | 834 | 834 | 10 | 10 | 10
280 | FR-BE: Lonny-Achene-Gramme | TOOT | 158 | 162 | 156 |  | 7 | 10 | 5 | 61 | 71 | 55 | -48 | -31 | -67 | 20 | 9 | 23 | 25 | 4 | 10 | 10 | 872 | 1017 | 769 |  | -39 | -13 | 4 | 0 | 0 | -5 | 472 | 25 | 750 | 750 | 750 | 30 | 30 | 30
283 | TuNur Italy | PINT | 254 | 266 | 242 | 445 | 140 | 153 | 127 | 714 | 723 | 705 | -952 | -861 | -1044 | 12 | 183 | 458 | 490 | 2 | 6 | 6 | 10127 | 10141 | 10113 | 5000 | -446 | -119 | -72 | -5 | -7 | -42 | -76 | -3 | 0 | 0 | 0 | 0 | 0 | 0
285 | GridLink | TOOT | 240 | 246 | 237 |  | 31 | 32 | 28 | 179 | 181 | 177 | -208 | -189 | -220 | 18 | 40 | 100 | 107 | 3 | 9 | 9 | 2666 | 2898 | 2493 |  | -71 | -16 | -14 | -1 | -1 | -6 | 592 | 34 | 837 | 837 | 837 | 23 | 23 | 23
297 | BRABO III | TOOT | 73 | 75 | 71 |  | 8 | 9 | 7 | 51 | 55 | 48 | -56 | -49 | -63 | 7 | 11 | 27 | 29 | 1 | 4 | 4 | 724 | 786 | 671 |  | -33 | -3 | -25 | -1 | -2 | -1 | 168 | 8 | 470 | 470 | 470 | 27 | 27 | 27
299 | SACOI 3 | TOOT | 178 | 178 | 177 |  | 93 | 98 | 85 | 15 | 20 | 6 | -631 | -576 | -664 | -3 | 121 | 303 | 325 | -1 | -1 | -1 | 212 | 279 | 91 |  | -2059 | -1 | -1369 | -53 | -74 | -20 | -69 | -6 | 851 | 851 | 851 | 15 | 15 | 15
309 | NeuConnect | TOOT | 398 | 405 | 394 |  | 27 | 30 | 24 | 193 | 196 | 189 | -181 | -164 | -204 | 42 | 35 | 87 | 93 | 8 | 20 | 21 | 2749 | 2794 | 2718 |  | -164 | -27 | -65 | -3 | -4 | -10 | 705 | 44 | 2712 | 2712 | 2712 | 33 | 33 | 33
312 | St. Peter (AT) - Tauern (AT) | TOOT | 373 | 379 | 365 |  | 47 | 50 | 44 | 156 | 158 | 153 | -320 | -302 | -337 | -35 | 61 | 154 | 165 | -7 | -17 | -18 | 2211 | 2235 | 2184 |  | -145 | -23 | -54 | -3 | -4 | -9 | -233 | -16 | 3230 | 3230 | 3230 | 40 | 40 | 40
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 250 | 251 | 248 |  | 30 | 30 | 29 | 104 | 106 | 103 | -202 | -200 | -204 | -24 | 39 | 97 | 104 | -5 | -11 | -12 | 1477 | 1481 | 1473 |  | -92 | -14 | -33 | -2 | -2 | -5 | 363 | 5 | 2077 | 2077 | 2077 | 25 | 25 | 25
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 7 | 11 | 4 |  | 2 | 4 | 1 | 3 | 5 | 1 | -17 | -9 | -28 | 28 | 3 | 8 | 9 | 5 | 14 | 14 | 37 | 65 | 20 |  | -17 | -2 | -14 | 0 | -1 | -1 | 279 | 18 | 14 | 14 | 14 | 0 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 10 | 15 | 3 |  | 3 | 5 | 1 | 1 | 2 | 1 | -21 | -8 | -33 | 29 | 4 | 10 | 11 | 6 | 14 | 15 | 20 | 28 | 14 |  | -11 | -3 | -8 | 0 | 0 | -1 | 289 | 19 | 27 | 27 | 27 | 0 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | TOOT | 229 | 231 | 228 |  | 88 | 96 | 81 | 58 | 63 | 50 | -602 | -551 | -652 | 6 | 116 | 290 | 310 | 1 | 3 | 3 | 832 | 907 | 700 |  | -300 | -98 | -10 | -2 | -2 | -34 | 191 | 10 | 658 | 658 | 658 | 8 | 8 | 8
328 | Interconnector DE-LUX | TOOT | 48 | 54 | 42 |  | 0 | 1 | -3 | 6 | 7 | 4 | 8 | 19 | -5 | 5 | 0 | 0 | 0 | 1 | 3 | 3 | 78 | 101 | 57 |  | -3 | 1 | -5 | 0 | 0 | 0 | -186 | -18 | 41 | 41 | 41 | 1 | 1 | 1
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 232 | 269 | 219 |  | 83 | 96 | 78 | 180 | 209 | 170 | -1816 | -2843 | -1503 | -9 | 615 | 1140 | 1202 | -2 | -4 | -5 | 3630 | 3568 | 3690 |  | -2080 | -138 | -2107 | -111 | -190 | -47 | -336 | -31 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | TOOT | 133 | 143 | 123 |  | 2 | 7 | -5 | 5 | 7 | 3 | 22 | 51 | -22 | 20 | 2 | 6 | 6 | 4 | 9 | 10 | 68 | 98 | 50 |  | -7 | 5 | -27 | -1 | -1 | -2 | 72 | 8 | 231 | 231 | 231 | 2 | 2 | 2
335 | North Sea Wind Power Hub | Light PINT | 1652 | 1666 | 1639 | 1326 | 367 | 399 | 334 | 2814 | 2820 | 2809 | -2496 | -2275 | -2717 |  | 479 | 1201 | 1286 |  |  |  | 39903 | 40255 | 39551 | 14000 | -1173 | -169 | -545 | -24 | -34 | -64 |  |  | 4477 | 4477 | 4477 | 55 | 55 | 55
338 | Adriatic HVDC link | TOOT | 108 | 112 | 100 |  | 36 | 38 | 34 | 52 | 60 | 45 | -244 | -229 | -260 | 27 | 47 | 117 | 126 | 5 | 13 | 14 | 719 | 847 | 526 |  | -128 | -33 | -24 | -2 | -2 | -12 | 337 | 13 | 1219 | 1219 | 1219 | 10 | 10 | 10
339 | Tyrrhenian link | TOOT | 100 | 104 | 95 |  | 9 | 40 | -32 | 53 | 61 | 48 | -243 | -220 | -271 | 10 | 11 | 28 | 30 | 2 | 5 | 5 | 713 | 740 | 678 |  | -118 | -35 | -8 | -1 | -1 | -12 | 370 | 9 | 1293 | 1293 | 1293 | 0 | 0 | 0
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 258 | 294 | 189 |  | 92 | 105 | 68 | 201 | 229 | 147 | -2563 | -3132 | -1285 | -6 | 869 | 1610 | 1697 | -1 | -3 | -3 | 3659 | 3094 | 4045 |  | -3036 | -182 | -3444 | -152 | -293 | -63 | -595 | -46 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | TOOT | 15 | 24 | 9 |  | 8 | 11 | 4 | 2 | 8 | -2 | -53 | -29 | -73 | 133 | 10 | 26 | 27 | 25 | 64 | 68 | 36 | 108 | -22 |  | -23 | -2 | -37 | -1 | -1 | -1 | 1223 | 81 | 94 | 94 | 94 | 0 | 0 | 0
342 | Central Balkan Corridor | TOOT | 10 | 13 | 8 |  | 6 | 10 | 4 | 2 | 6 | 1 | -41 | -25 | -71 | 3 | 8 | 20 | 21 | 1 | 1 | 1 | 34 | 77 | 7 |  | 31 | 0 | 49 | 1 | 2 | 0 | 21 | 0 | 303 | 303 | 303 | 3 | 3 | 3
343 | CSE1 New | TOOT | 8 | 10 | 6 |  | 5 | 6 | 3 | -1 | 0 | -4 | -35 | -23 | -43 | 14 | 7 | 17 | 18 | 3 | 7 | 7 | -17 | 4 | -56 |  | -33 | -7 | -16 | -1 | -1 | -2 | 98 | 8 | 84 | 84 | 84 | 0 | 0 | 0
346 | ZuidWest380 NL Oost | TOOT | 23 | 30 | 14 |  | 0 | 1 | 0 | 8 | 11 | 6 | -2 | 3 | -6 | -4 | 0 | 1 | 1 | -1 | -2 | -2 | 110 | 157 | 84 |  | 4 | -1 | 5 | 0 | 0 | 0 | -121 | -6 | 299 | 299 | 299 | 25 | 25 | 25
349 | MaresConnect | TOOT | 169 | 188 | 155 |  | 22 | 24 | 19 | 104 | 110 | 100 | -150 | -130 | -165 | -1 | 29 | 72 | 77 | 0 | 0 | 0 | 1481 | 1545 | 1436 |  | -84 | -24 | -14 | -1 | -1 | -8 | 107 | 4 | 1386 | 1386 | 1386 | 14 | 14 | 14
350 | South Balkan Corridor | TOOT | 56 | 73 | 44 |  | 29 | 32 | 26 | 17 | 22 | 9 | -200 | -179 | -218 | 113 | 38 | 96 | 103 | 22 | 55 | 58 | 246 | 324 | 126 |  | -152 | -50 | -4 | -1 | -1 | -17 | 1231 | 80 | 428 | 428 | 428 | 0 | 0 | 0
375 | Lienz (AT) - Veneto region (IT) 220 kV | TOOT | 122 | 122 | 121 |  | 42 | 47 | 38 | 31 | 34 | 28 | -283 | -257 | -320 | 14 | 54 | 136 | 146 | 3 | 7 | 7 | 447 | 487 | 385 |  | -132 | -37 | -17 | -1 | -2 | -13 | 117 | 8 | 350 | 350 | 350 | 5 | 5 | 5
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | Light PINT | 18 | 22 | 16 |  | 11 | 14 | 8 | 7 | 9 | 5 | -73 | -56 | -99 |  | 14 | 35 | 38 |  |  |  | 99 | 129 | 64 |  | -75 | -24 | 1 | -1 | -1 | -8 |  |  | 13 | 13 | 13 | 0 | 0 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | TOOT | 74 | 75 | 71 |  | 8 | 9 | 7 | 51 | 55 | 48 | -55 | -49 | -63 | 9 | 11 | 27 | 29 | 2 | 4 | 5 | 722 | 780 | 671 |  | -33 | -3 | -25 | -1 | -2 | -1 | 191 | 9 | 463 | 463 | 463 | 27 | 27 | 27
378 | Transformer Gatica | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 226 | 292 | 184 |  | 7 | 10 | 5 | 106 | 151 | 78 | -48 | -32 | -70 | 41 | 9 | 23 | 25 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | -36 | -11 | -1 | 0 | 0 | -4 | 886 | 51 | 0 | 0 | 0 | 0 | 0 | 0
1039 | SE North-south long-term reinforcements | PINT | 46 | 47 | 44 |  | 6 | 8 | 4 | 9 | 9 | 8 | -41 | -25 | -51 | 6 | 8 | 20 | 21 | 1 | 3 | 3 | 125 | 129 | 121 |  | -22 | -3 | -12 | 0 | -1 | -1 | 131 | 4 | 74 | 74 | 74 | 0 | 0 | 0
1040 | LirIC | TOOT | 139 | 153 | 131 |  | 22 | 24 | 17 | 52 | 60 | 43 | -148 | -114 | -166 | 7 | 28 | 71 | 76 | 1 | 3 | 4 | 737 | 851 | 620 |  | -240 | -38 | -87 | -4 | -5 | -15 | 169 | 10 | 891 | 891 | 891 | 9 | 9 | 9
1041 | GREGY Green Energy Interconnector | TOOT | 720 | 725 | 714 |  | 397 | 399 | 395 | 239 | 240 | 237 | -2701 | -2686 | -2716 | 150 | 519 | 1299 | 1391 | 29 | 72 | 77 | 3385 | 3431 | 3339 |  | -1835 | -588 | -29 | -15 | -14 | -206 | 1198 | 92 | 4265 | 4265 | 4265 | 43 | 43 | 43
1046 | Finnish North-South reinforcement | PINT | 287 | 287 | 287 |  | 14 | 14 | 14 | 413 | 413 | 413 | 95.093 | 95.093 | 95.093 | -1 | 18 | 46 | 49 | 0 | 0 | 0 | 6463 | 6463 | 6463 |  | -15 | -4 | -14 | 0 | -1 | -1 | -138 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 105 | 114 | 96 |  | 61 | 64 | 58 | 49 | 51 | 48 | -412 | -398 | -433 | -37 | 79 | 198 | 212 | -7 | -18 | -19 | 697 | 724 | 669 |  | -298 | -94 | -9 | -3 | -3 | -33 | -4472 | -280 | 6 | 6 | 6 | 0 | 0 | 0
1049 | Cronos Energy Ltd | PINT | 258 | 271 | 247 |  | 5 | 6 | 4 | 137 | 146 | 129 | -36 | -25 | -44 | 8 | 7 | 17 | 18 | 2 | 4 | 4 | 1959 | 2083 | 1851 |  | -138 | -22 | -61 | -3 | -4 | -8 | -95 | 0 | 529 | 529 | 529 | 13 | 13 | 13
1050 | Tarchon Energy Ltd | TOOT | 398 | 405 | 394 |  | 27 | 30 | 24 | 193 | 196 | 189 | -181 | -164 | -204 | 25 | 35 | 87 | 93 | 5 | 12 | 13 | 2749 | 2794 | 2718 |  | -164 | -27 | -65 | -3 | -4 | -10 | 346 | 22 | 2704 | 2704 | 2704 | 33 | 33 | 33
1052 | Lienz (AT) - Malta (AT) - Obersielach (AT) | TOOT | 509 | 512 | 506 | 124 | 162 | 165 | 159 | 328 | 360 | 295 | -1101 | -1082 | -1120 | 4 | 211 | 530 | 567 | 1 | 2 | 2 | 4649 | 5162 | 4135 | 2000 | -516 | -157 | -52 | -5 | -6 | -55 | -97 | -7 | 924 | 924 | 924 | 12 | 12 | 12
1054 | 220-kV Westtirol (AT) - Zell/Ziller (AT) | TOOT | 104 | 108 | 101 |  | 13 | 17 | 12 | 44 | 45 | 43 | -92 | -79 | -115 | 14 | 18 | 44 | 47 | 3 | 7 | 7 | 626 | 642 | 603 |  | -33 | -5 | -12 | -1 | -1 | -2 | 391 | 20 | 700 | 700 | 700 | 9 | 9 | 9
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 104 | 113 | 97 |  | 30 | 31 | 27 | 70 | 76 | 64 | -202 | -184 | -212 | 237 | 39 | 97 | 104 | 45 | 114 | 122 | 989 | 1065 | 909 |  | -111 | -34 | -8 | -1 | -1 | -12 | 7127 | 458 | 1320 | 1320 | 1320 | 13 | 13 | 13
1058 | HVDC Interconnector DE-CH | Light PINT | 221 | 225 | 218 |  | 23 | 27 | 18 | 103 | 104 | 103 | -155 | -126 | -182 |  | 30 | 75 | 80 |  |  |  | 1472 | 1486 | 1449 |  | -102 | -21 | -37 | -2 | -2 | -8 |  |  | 298 | 298 | 298 | 4 | 4 | 4
1059 | Southern Italy | TOOT | 8 | 12 | 2 |  | 0 | 3 | -8 | 1 | 3 | 0 | -25 | -11 | -52 | 4 | 0 | 0 | 0 | 1 | 2 | 2 | 16 | 36 | -4 |  | -17 | -4 | -5 | 0 | 0 | -1 | 120 | 0 | 621 | 621 | 621 | 0 | 0 | 0
1066 | Bulgaria - Turkey | Light PINT | 152 | 153 | 150 |  | 76 | 94 | 63 | 18 | 24 | 13 | -520 | -425 | -637 |  | 100 | 250 | 268 |  |  |  | 260 | 343 | 181 |  | -294 | -88 | -32 | -3 | -3 | -31 |  |  | 48 | 48 | 48 | 2 | 2 | 2
1067 | New AC 400 kV interconnection line Greece - Turkey | Light PINT | 138 | 156 | 123 |  | 69 | 74 | 65 | 32 | 35 | 30 | -467 | -445 | -500 |  | 90 | 225 | 241 |  |  |  | 456 | 507 | 419 |  | -369 | -120 | -1 | -3 | -3 | -42 |  |  | 263 | 263 | 263 | 3 | 3 | 3
1068 | LaSGo Link | PINT | 58 | 61 | 53 |  | 7 | 8 | 6 | 41 | 43 | 39 | -48 | -41 | -54 | 1 | 9 | 23 | 25 | 0 | 1 | 1 | 585 | 613 | 554 |  | -151 | -3 | -97 | -4 | -5 | -2 | 53 | 3 | 116 | 116 | 116 | 0 | 0 | 0
1074 | Pannonian Corridor | TOOT | 17 | 25 | 13 |  | 1 | 3 | -2 | 0 | 4 | -6 | 8 | 14 | -1 | 10 | 1 | 2 | 2 | 2 | 5 | 5 | -4 | 53 | -86 |  | -12 | -2 | 11 | 0 | 0 | -1 | 39 | 3 | 569 | 569 | 569 | 5 | 5 | 5
1085 | Malta-Italy Cable Link No.2 | TOOT | 85 | 87 | 81 |  | 25 | 29 | 20 | 22 | 24 | 20 | -172 | -133 | -195 | 3 | 33 | 83 | 89 | 0 | 1 | 1 | 309 | 336 | 285 |  | -95 | -33 | 7 | -1 | 0 | -11 | 41 | 4 | 325 | 325 | 325 | 3 | 3 | 3
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 1 | 2 | 0 | 75 | 10 | 13 | 7 | 91 | 94 | 88 | -71 | -50 | -89 | -2 | 14 | 34 | 37 | 0 | -1 | -1 | 1299 | 1346 | 1255 | 700 | -126 | -2 | -86 | -3 | -5 | -2 | -371 | -13 | 0 | 0 | 0 | 0 | 0 | 0
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | TOOT | 54 | 55 | 54 | 114 | 22 | 23 | 20 | 176 | 177 | 176 | -147 | -138 | -157 | 0 | 28 | 71 | 76 | 0 | 0 | 0 | 2501 | 2524 | 2477 | 1000 | -87 | -7 | -52 | -2 | -3 | -3 | -214 | -10 | 0 | 0 | 0 | 0 | 0 | 0
1092 | TritonLink: offshore hybrid HVDC interconnector Belgium – Denmark | TOOT | 1118 | 1133 | 1101 | 151 | 164 | 164 | 163 | 1169 | 1177 | 1162 | -1114 | -1109 | -1118 | 29 | 214 | 536 | 574 | 6 | 14 | 15 | 16570 | 16640 | 16500 | 10000 | -563 | -76 | -294 | -12 | -20 | -28 | 434 | 30 | 5875 | 5875 | 5875 | 197 | 197 | 197
1094 | Estlink 3 | TOOT | 76 | 80 | 72 |  | 11 | 12 | 10 | 58 | 60 | 56 | -77 | -69 | -85 | 6 | 15 | 37 | 40 | 1 | 3 | 3 | 823 | 837 | 808 |  | -59 | -10 | -17 | -1 | -1 | -4 | 63 | 4 | 687 | 687 | 687 | 5 | 5 | 5
1095 | Aurora line 2 (4th AC Finland-Sweden north) | TOOT | 64 | 65 | 62 |  | 5 | 7 | 4 | 43 | 44 | 43 | -36 | -27 | -44 | 2 | 7 | 17 | 18 | 0 | 1 | 1 | 615 | 616 | 614 |  | -53 | -5 | -29 | -1 | -2 | -2 | 43 | 2 | 1057 | 1057 | 1057 | 8 | 8 | 8
1096 | Beznau - Mettlen | Light TOOT | 80 | 89 | 73 |  | 25 | 32 | 19 | 72 | 73 | 70 | -171 | -127 | -220 |  | 33 | 82 | 88 |  |  |  | 1019 | 1044 | 981 |  | -107 | -32 | -5 | -1 | -1 | -11 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1097 | Upgrade to Konti-Skan | PINT | 140 | 142 | 139 |  | 11 | 15 | 10 | 127 | 132 | 121 | -77 | -65 | -102 | 10 | 15 | 37 | 40 | 2 | 5 | 5 | 1809 | 1854 | 1722 |  | -20 | -4 | -3 | 0 | 0 | -1 | 266 | 14 | 165 | 165 | 165 | 0 | 0 | 0
1098 | Offshore Wind LT 2 | TOOT | 5 | 8 | 1 | 96 | 13 | 14 | 12 | 113 | 114 | 111 | -88 | -80 | -95 | 0 | 17 | 42 | 45 | 0 | 0 | 0 | 1600 | 1609 | 1586 | 700 | -64 | -4 | -36 | -1 | -2 | -2 | 104 | 5 | 109 | 109 | 109 | 1 | 1 | 1
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | TOOT | 202 | 207 | 195 |  | 49 | 51 | 47 | 67 | 69 | 64 | -333 | -318 | -349 | 22 | 64 | 160 | 171 | 4 | 11 | 11 | 956 | 982 | 912 |  | -237 | -67 | -43 | -3 | -3 | -23 | 561 | 25 | 0 | 0 | 0 | 0 | 0 | 0
1102 | Mettlen - Ulrichen | Light TOOT | 28 | 32 | 24 |  | 0 | 2 | -2 | 1 | 3 | -3 | 1 | 11 | -6 |  | 0 | 1 | 1 |  |  |  | 10 | 47 | -36 |  | -2 | -2 | 1 | 0 | 0 | -1 |  |  | 254 | 254 | 254 | 0 | 0 | 0
1103 | Bickigen - Chippis | Light TOOT | 54 | 59 | 44 |  | 17 | 23 | 13 | 51 | 52 | 51 | -116 | -89 | -154 |  | 22 | 56 | 60 |  |  |  | 732 | 753 | 717 |  | -66 | -21 | 0 | 0 | 0 | -7 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1104 | Bauler - Roost | TOOT | 5 | 5 | 4 |  | 0 | 2 | -3 | 2 | 4 | -1 | 0 | 17 | -16 | 4 | 0 | 0 | 0 | 1 | 2 | 2 | 28 | 53 | -10 |  | -1 | 0 | -3 | 0 | 0 | 0 | -196 | -19 | 0 | 0 | 0 | 0 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 472 | 478 | 467 |  | 79 | 92 | 64 | 198 | 201 | 195 | -535 | -436 | -625 | -23 | 103 | 257 | 276 | -4 | -11 | -12 | 2835 | 2878 | 2793 |  | -326 | -96 | -55 | -4 | -4 | -34 | -64 | -5 | 358 | 358 | 358 | 4 | 4 | 4
1106 | Bornholm Energy Island (BEI) | TOOT | 310 | 310 | 310 | 299 | 72 | 76 | 70 | 538 | 548 | 525 | -491 | -478 | -516 | -7 | 94 | 236 | 253 | -1 | -3 | -3 | 7717 | 7739 | 7694 | 3000 | -117 | -32 | -19 | -1 | -2 | -11 | -433 | -20 | 3070 | 3070 | 3070 | 38 | 38 | 38
1109 | Basilicata - Campania reinforcements | TOOT | 17 | 22 | 8 |  | 6 | 8 | 4 | 2 | 6 | -2 | -48 | -30 | -73 | -7 | 8 | 19 | 21 | -1 | -3 | -3 | 26 | 84 | -25 |  | -28 | -8 | -5 | 0 | 0 | -3 | -32 | -7 | 404 | 404 | 404 | 0 | 0 | 0
1110 | Sicily - Calabria | TOOT | 5 | 7 | 3 |  | 1 | 1 | 0 | 2 | 5 | 0 | 0 | 6 | -9 | -5 | 1 | 2 | 2 | -1 | -3 | -3 | 28 | 76 | 5 |  | -9 | -1 | -5 | 0 | 0 | -1 | 7 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1112 | GRITA 2 | TOOT | 224 | 224 | 223 |  | 76 | 83 | 69 | 84 | 84 | 83 | -518 | -472 | -564 | 40 | 99 | 249 | 267 | 8 | 19 | 20 | 1185 | 1191 | 1179 |  | -187 | -65 | 10 | -1 | -1 | -23 | 525 | 38 | 1491 | 1491 | 1491 | 0 | 0 | 0
1121 | 220-kV Hessenberg (AT) - Weißenbach (AT) | TOOT | 0 | 1 | 0 | 51 | 4 | 5 | 4 | 58 | 60 | 57 | -29 | -25 | -35 | -1 | 6 | 14 | 15 | 0 | -1 | -1 | 823 | 846 | 810 | 600 | -12 | -3 | -3 | 0 | 0 | -1 | -95 | -3 | 0 | 0 | 0 | 0 | 0 | 0
1122 | Offshore Wind farm connection Centre Manche 1 | TOOT | 20 | 25 | 13 | 249 | 43 | 48 | 41 | 334 | 344 | 321 | -296 | -279 | -330 | 105 | 57 | 142 | 152 | 20 | 51 | 54 | 4830 | 4832 | 4827 | 1050 | -101 | -12 | -51 | -2 | -3 | -5 | 910 | 45 | 149 | 149 | 149 | 3 | 3 | 3
1123 | Offshore Wind farm connection Centre Manche 2 | TOOT | 89 | 94 | 82 | 180 | 43 | 48 | 41 | 334 | 344 | 321 | -296 | -279 | -330 | 79 | 57 | 142 | 152 | 15 | 38 | 41 | 4830 | 4832 | 4827 | 1250 | -101 | -12 | -51 | -2 | -3 | -5 | 659 | 34 | 150 | 150 | 150 | 2 | 2 | 2
1124 | Offshore Wind Connection South Britanny | TOOT | 14 | 18 | 10 | 155 | 27 | 30 | 25 | 204 | 211 | 197 | -182 | -169 | -205 | 63 | 35 | 87 | 94 | 12 | 30 | 32 | 2904 | 2966 | 2809 | 250 | -55 | -7 | -27 | -1 | -2 | -3 | 662 | 28 | 89 | 89 | 89 | 2 | 2 | 2
1125 | Offshore Wind Connection Occitanie | TOOT | 60 | 62 | 57 | 125 | 31 | 35 | 28 | 208 | 216 | 200 | -209 | -188 | -235 | 11 | 40 | 101 | 108 | 2 | 5 | 6 | 2952 | 3030 | 2851 | 250 | -73 | -11 | -29 | -1 | -2 | -4 | 73 | 4 | 89 | 89 | 89 | 1 | 1 | 1
1126 | Offshore Wind Connection PACA | TOOT | 58 | 60 | 56 | 120 | 30 | 33 | 28 | 199 | 207 | 191 | -207 | -191 | -228 | -17 | 40 | 99 | 106 | -3 | -8 | -9 | 2827 | 2904 | 2731 | 250 | -79 | -11 | -35 | -2 | -2 | -4 | -222 | -9 | 89 | 89 | 89 | 2 | 2 | 2
1127 | Offshore Wind Connection South Atlantic Oléron 1 | TOOT | 16 | 18 | 13 | 234 | 40 | 47 | 34 | 296 | 304 | 286 | -272 | -234 | -317 | 70 | 52 | 131 | 140 | 13 | 33 | 36 | 4210 | 4281 | 4088 | 1250 | -92 | -12 | -46 | -2 | -3 | -5 | 620 | 30 | 148 | 148 | 148 | 3 | 3 | 3
1134 | GiLA | PINT | 455 | 455 | 455 |  | 39 | 39 | 39 | 287 | 287 | 287 | -264 | -264 | -264 | 13 | 0 | 0 | 0 | 2 | 6 | 7 | 5647 | 5647 | 5647 |  | -115 | -36 | -5 | -1 | -1 | -13 | 756 | 31 | 0 | 0 | 0 | 0 | 0 | 0
1138 | 400 kV OHL Suceava (RO) - Balti (MD) | TOOT | 127 | 134 | 121 |  | 39 | 42 | 37 | 10 | 12 | 7 | -265 | -250 | -287 | 59 | 51 | 128 | 137 | 11 | 28 | 30 | 138 | 172 | 106 |  | -142 | -57 | 40 | 0 | 1 | -20 | 1629 | 90 | 227 | 227 | 227 | 0 | 0 | 0
1139 | 380-kV Westtirol (AT) – Zell/Ziller (AT) | PINT | 68 | 100 | 31 | 77 | 7 | 26 | -14 | 157 | 180 | 128 | -111 | -63 | -177 | -22 | 9 | 24 | 25 | -4 | -11 | -11 | 2231 | 2531 | 1826 | 1600 | -71 | -12 | -35 | -1 | -2 | -4 | -681 | -35 | 0 | 0 | 0 | 0 | 0 | 0
1140 | 380-kV St. Peter (AT) - Dürnrohr (AT) | PINT | 115 | 121 | 110 | 68 | 20 | 24 | 17 | 161 | 165 | 157 | -139 | -115 | -162 | -12 | 27 | 67 | 71 | -2 | -6 | -6 | 2289 | 2318 | 2260 | 1500 | -76 | -11 | -37 | -2 | -2 | -4 | -293 | -17 | 258 | 258 | 258 | 3 | 3 | 3
1145 | 380-kV Obersielach (AT) - Hessenberg (AT) | TOOT | 1 | 3 | 0 | 170 | 19 | 22 | 17 | 194 | 200 | 190 | -131 | -116 | -149 | -17 | 25 | 63 | 67 | -3 | -8 | -9 | 2763 | 2804 | 2723 | 2000 | -61 | -12 | -23 | -1 | -2 | -4 | -225 | -13 | 0 | 0 | 0 | 0 | 0 | 0
1153 | PST romands | TOOT | 111 | 121 | 100 |  | 34 | 39 | 26 | 37 | 45 | 31 | -233 | -179 | -266 | 94 | 45 | 112 | 120 | 18 | 45 | 49 | 527 | 636 | 444 |  | -175 | -56 | -5 | -1 | -1 | -20 | 729 | 39 | 346 | 346 | 346 | 8 | 8 | 8
1155 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT) | TOOT | 11 | 16 | 8 | 298 | 33 | 36 | 31 | 342 | 352 | 332 | -225 | -213 | -244 | -1 | 43 | 108 | 116 | 0 | 0 | 0 | 4857 | 4937 | 4745 | 2000 | -94 | -21 | -28 | -1 | -2 | -8 | -132 | -5 | 0 | 0 | 0 | 0 | 0 | 0
1156 | 380-kV Greater Vienna (AT) - Hessenberg (AT) | TOOT | 6 | 9 | 4 | 233 | 25 | 25 | 25 | 261 | 262 | 261 | -171 | -170 | -173 | -12 | 33 | 82 | 88 | -2 | -6 | -6 | 3786 | 3882 | 3727 | 2500 | -75 | -17 | -23 | -1 | -2 | -6 | -213 | -12 | 0 | 0 | 0 | 0 | 0 | 0
1157 | HG North Tyrrhenian Corridor | TOOT | 279 | 284 | 276 |  | 96 | 100 | 95 | 130 | 138 | 116 | -655 | -643 | -679 | 96 | 126 | 315 | 337 | 18 | 46 | 50 | 1850 | 1986 | 1663 |  | -343 | -92 | -56 | -4 | -5 | -33 | 733 | 48 | 3821 | 3821 | 3821 | 40 | 40 | 40
1158 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT) | PINT | 5 | 11 | 0 | 163 | 17 | 22 | 12 | 189 | 198 | 184 | -116 | -80 | -150 | -2 | 22 | 56 | 60 | 0 | -1 | -1 | 2691 | 2781 | 2633 | 2000 | -53 | -12 | -19 | -1 | -1 | -4 | -191 | -7 | 0 | 0 | 0 | 0 | 0 | 0
1159 | 220-kV Bisamberg (AT) – Wien Südost (AT) | TOOT | 1 | 3 | 0 | 19 | 1 | 2 | 0 | 24 | 27 | 22 | -7 | 0 | -12 | -1 | 1 | 3 | 3 | 0 | -1 | -1 | 340 | 391 | 310 | 500 | -4 | -2 | 2 | 0 | 0 | -1 | -3 | 1 | 0 | 0 | 0 | 0 | 0 | 0
1161 | Offshore Wind Connection South Atlantic Oléron 2 | TOOT | 5 | 8 | 2 | 210 | 34 | 38 | 32 | 262 | 272 | 253 | -234 | -215 | -262 | 107 | 45 | 113 | 121 | 20 | 51 | 55 | 3731 | 3811 | 3608 | 1200 | -85 | -11 | -40 | -2 | -3 | -4 | 899 | 46 | 142 | 142 | 142 | 2 | 2 | 2
1162 | Offshore Wind Connection Fécamp-Grand Large 1 | TOOT | 10 | 14 | 4 | 351 | 58 | 64 | 53 | 439 | 454 | 420 | -392 | -362 | -435 | 72 | 75 | 189 | 202 | 14 | 34 | 37 | 6356 | 6375 | 6337 | 2000 | -116 | -17 | -50 | -2 | -3 | -6 | 453 | 29 | 237 | 237 | 237 | 4 | 4 | 4
1163 | Offshore Wind Connection Fécamp-Grand Large 2 | TOOT | 120 | 124 | 114 | 241 | 58 | 64 | 53 | 439 | 454 | 420 | -392 | -362 | -435 | 72 | 75 | 189 | 202 | 14 | 34 | 37 | 6356 | 6375 | 6337 | 2000 | -116 | -17 | -50 | -2 | -3 | -6 | 453 | 29 | 236 | 236 | 236 | 3 | 3 | 3
1164 | Offshore Wind Connection Golfe de Lion Centre | TOOT | 120 | 124 | 114 | 241 | 58 | 64 | 53 | 439 | 454 | 420 | -392 | -362 | -435 | -62 | 75 | 189 | 202 | -12 | -30 | -32 | 6356 | 6375 | 6337 | 2000 | -116 | -17 | -50 | -2 | -3 | -6 | -650 | -29 | 238 | 238 | 238 | 4 | 4 | 4
1165 | Offshore Wind Connection Golfe de Gascogne Sud | TOOT | 70 | 73 | 67 | 145 | 34 | 38 | 32 | 262 | 272 | 253 | -234 | -215 | -262 | 57 | 45 | 113 | 121 | 11 | 27 | 29 | 3731 | 3811 | 3608 | 1200 | -85 | -11 | -40 | -2 | -3 | -4 | 464 | 25 | 143 | 143 | 143 | 2 | 2 | 2
1166 | HG Adriatic Corridor | PINT | 139 | 155 | 125 |  | 45 | 53 | 41 | 68 | 70 | 64 | -307 | -279 | -362 | 41 | 59 | 148 | 158 | 8 | 20 | 21 | 964 | 993 | 918 |  | -133 | -36 | -22 | -2 | -2 | -13 | 404 | 32 | 107 | 107 | 107 | 1 | 1 | 1
1167 | HG Central link | TOOT | 8 | 11 | 3 |  | 3 | 4 | 3 | 4 | 5 | 1 | -28 | 18 | -76 | 16 | 4 | 11 | 11 | 3 | 8 | 8 | 47 | 71 | 13 |  | -19 | -7 | 2 | 0 | 0 | -2 | 288 | 13 | 644 | 644 | 644 | 5 | 5 | 5
1168 | HG Ionian-Tyrrhenian Corridor | TOOT | 38 | 40 | 33 |  | 10 | 14 | 2 | 13 | 18 | 5 | -72 | -13 | -98 | 8 | 13 | 33 | 35 | 2 | 4 | 4 | 167 | 216 | 74 |  | -45 | -13 | -5 | 0 | -1 | -5 | 187 | 6 | 0 | 0 | 0 | 0 | 0 | 0
1169 | SAPEI 2 | PINT | 25 | 34 | 21 |  | 10 | 12 | 6 | 9 | 10 | 8 | -73 | -66 | -79 | -2 | 12 | 31 | 33 | 0 | -1 | -1 | 120 | 129 | 115 |  | -26 | -9 | 0 | 0 | 0 | -3 | 56 | 6 | 12 | 12 | 12 | 0 | 0 | 0
1171 | Interconnection IT-CH | PINT | 73 | 76 | 70 |  | 35 | 38 | 33 | 14 | 16 | 13 | -238 | -227 | -260 | 18 | 46 | 115 | 123 | 3 | 9 | 9 | 204 | 234 | 181 |  | -119 | -35 | -14 | -1 | -1 | -12 | 347 | 22 | 77 | 77 | 77 | 1 | 1 | 1
1182 | EHV S/S Thesprotias and its connection to the 400 kV System | Light PINT | 30 | 33 | 29 |  | 10 | 13 | 7 | 12 | 16 | 9 | -66 | -48 | -89 |  | 13 | 32 | 34 |  |  |  | 178 | 225 | 133 |  | -13 | -3 | -1 | 0 | 0 | -1 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1183 | New interconnection line 400 kV Greece - Albania | Light PINT | 7 | 13 | 4 |  | 1 | 3 | -3 | 0 | 2 | -2 | -8 | 19 | -23 |  | 2 | 4 | 4 |  |  |  | 1 | 23 | -22 |  | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1185 | South Coast Offshore Transmission Project | TOOT | 6 | 8 | 3 | 117 | 22 | 24 | 21 | 125 | 132 | 119 | -150 | -144 | -161 | 0 | 29 | 72 | 77 | 0 | 0 | 0 | 1767 | 1844 | 1700 | 800 | -37 | -9 | -11 | -1 | -1 | -3 | 17 | 1 | 159 | 159 | 159 | 2 | 2 | 2
1192 | HansaLink - Phase 1 | PINT | 514 | 517 | 512 | 319 | 111 | 124 | 97 | 626 | 635 | 617 | -753 | -661 | -845 | -46 | 145 | 362 | 388 | -9 | -22 | -24 | 8876 | 8909 | 8843 | 2000 | -291 | -49 | -130 | -6 | -8 | -18 | -255 | -23 | 3484 | 3484 | 3484 | 43 | 43 | 43
1193 | HansaLink - Phase 2 | PINT | 7 | 8 | 5 | 308 | 82 | 83 | 80 | 365 | 371 | 360 | -557 | -546 | -567 | 2 | 107 | 268 | 287 | 0 | 1 | 1 | 5186 | 5196 | 5176 | 2000 | -78 | -17 | -25 | -1 | -2 | -6 | -235 | -9 | 21 | 21 | 21 | 42 | 42 | 42
1197 | NU-Link Interconnector | PINT | 222 | 223 | 221 |  | 5 | 8 | 2 | 113 | 117 | 106 | -37 | -12 | -52 | -12 | 7 | 18 | 19 | -2 | -6 | -6 | 1612 | 1681 | 1496 |  | -105 | -15 | -44 | -2 | -3 | -6 | 128 | 4 | 252 | 252 | 252 | 9 | 9 | 9
1200 | Hybrid interconnector Norway-Sørvest F Windfarm-Continent (DK, DE or BE) | PINT | 803 | 807 | 798 |  | 68 | 68 | 68 | 579 | 582 | 576 | -465 | -465 | -465 | 7 | 89 | 224 | 239 | 1 | 3 | 4 | 8256 | 8386 | 8126 |  | -210 | -53 | -36 | -2 | -2 | -19 | 248 | 10 | 2798 | 2798 | 2798 | 34 | 34 | 34
1201 | Reinvestment of Skagerrak 1 and 2 | PINT | 181 | 184 | 178 |  | 29 | 35 | 23 | 150 | 151 | 150 | -200 | -159 | -241 | 1 | 38 | 96 | 103 | 0 | 0 | 0 | 2136 | 2147 | 2125 |  | -99 | -8 | -70 | -3 | -5 | -3 | 208 | 4 | 269 | 269 | 269 | 0 | 0 | 0
1202 | Increased capacity Norway-Finland, Back-to-Back | PINT | 41 | 50 | 31 |  | 7 | 10 | 5 | 29 | 31 | 28 | -48 | -36 | -68 | 1 | 9 | 23 | 25 | 0 | 0 | 0 | 421 | 441 | 404 |  | -41 | -1 | -31 | -1 | -2 | -1 | 156 | 7 | 61 | 61 | 61 | 0 | 0 | 0
1203 | Offshore Wind Connection Bretagne Nord-Ouest | PINT | 3 | 6 | 1 | 236 | 36 | 41 | 31 | 285 | 297 | 271 | -247 | -209 | -278 | 99 | 47 | 119 | 127 | 19 | 47 | 51 | 4136 | 4165 | 4108 | 1200 | -48 | -9 | -22 | -1 | -1 | -3 | 904 | 45 | 141 | 141 | 141 | 2 | 2 | 2
1207 | 380kV Niederstedem-Bertrange/Bofferdange | PINT | 2 | 4 | 0 |  | 1 | 2 | 0 | 1 | 3 | 0 | -5 | -1 | -12 | -8 | 1 | 2 | 3 | -1 | -4 | -4 | 21 | 44 | -1 |  | -1 | 1 | -5 | 0 | 0 | 0 | 190 | 18 | 0 | 0 | 0 | 0 | 0 | 0
1208 | Medlink | PINT | 816 | 844 | 779 | 620 | 271 | 276 | 266 | 1419 | 1473 | 1339 | -1842 | -1810 | -1875 |  | 354 | 886 | 949 |  |  |  | 20692 | 20706 | 20678 | 9016 | -869 | -245 | -107 | -10 | -11 | -86 | 1068 | 80 | 0 | 0 | 0 | 0 | 0 | 0
1209 | Latvia and Lithuania cross-border strengthening project | PINT | 34 | 44 | 28 |  | 4 | 7 | 2 | 32 | 33 | 30 | -25 | -12 | -45 | 0 | 5 | 12 | 13 | 0 | 0 | 0 | 455 | 477 | 424 |  | -162 | -2 | -108 | -4 | -6 | -2 | -70 | -2 | 10 | 10 | 10 | 0 | 0 | 0
1210 | APOLLO-LINK | Light PINT | 391 | 392 | 390 |  | 138 | 147 | 132 | 200 | 214 | 188 | -938 | -899 | -1000 |  | 180 | 451 | 483 |  |  |  | 2839 | 3068 | 2685 |  | -597 | -193 | -12 | -5 | -5 | -67 |  |  | 564 | 564 | 564 | 5 | 5 | 5
1211 | Baltic WindConnector (BWC) | PINT | 469 | 474 | 465 | 248 | 61 | 64 | 59 | 517 | 521 | 512 | -416 | -399 | -433 | 13 | 80 | 200 | 214 | 2 | 6 | 7 | 7342 | 7361 | 7324 | 2000 | -209 | -38 | -88 | -4 | -6 | -14 | 332 | 20 | 2528 | 2528 | 2528 | 31 | 31 | 31
1213 | Offshore hybrid Interconnector (DE-NL) | Light PINT | 168 | 169 | 168 |  | 14 | 20 | 7 | 83 | 88 | 76 | -87 | -50 | -123 |  | 18 | 45 | 48 |  |  |  | 1178 | 1245 | 1088 |  | -50 | -5 | -35 | -1 | -2 | -2 |  |  | 1232 | 1232 | 1232 | 15 | 15 | 15
1214 | Hybrid Interconnector Denmark-Germany | TOOT | 705 | 705 | 704 | 51 | 83 | 93 | 73 | 637 | 639 | 635 | -635 | -635 | -635 | 107 | 108 | 271 | 290 | 21 | 52 | 55 | 9058 | 9155 | 8962 | 2000 | -242 | -42 | -105 | -5 | -7 | -15 | 2352 | 139 | 0 | 0 | 0 | 0 | 0 | 0
1215 | Xlinks Morocco - Germany | PINT | 1782 | 1789 | 1773 | 158 | 246 | 275 | 212 | 1610 | 1652 | 1557 | -1676 | -1445 | -1867 | 282 | 322 | 806 | 863 | 54 | 136 | 145 | 23212 | 23238 | 23186 | 15200 | -704 | -115 | -321 | -14 | -21 | -42 | 4043 | 273 | 0 | 0 | 0 | 0 | 0 | 0
1216 | High-Voltage Direct Current Interconnector Project Romania-Hungary | PINT | 43 | 50 | 37 |  | 4 | 6 | 2 | -3 | 2 | -10 | -24 | -13 | -38 | 22 | 5 | 12 | 13 | 4 | 11 | 11 | -44 | 24 | -151 |  | 22 | -5 | 49 | 1 | 2 | -2 | 5 | 2 | 99 | 99 | 99 | 1 | 1 | 1
1217 | Further Development of Offshore Renewables (MOG 3) | Light PINT | 10 | 14 | 7 | 409 | 55 | 64 | 50 | 453 | 466 | 441 | -374 | -342 | -432 |  | 72 | 180 | 192 |  |  |  | 6447 | 6547 | 6305 |  | -195 | -23 | -112 | -5 | -7 | -9 |  |  | 295 | 295 | 295 | 17 | 17 | 17
1218 | Hybrid HVDC Interconnector BE-NL | Light PINT | 105 | 113 | 98 |  | 13 | 18 | 8 | 81 | 91 | 67 | -87 | -56 | -119 |  | 17 | 42 | 45 |  |  |  | 1154 | 1286 | 958 |  | -84 | -8 | -64 | -2 | -4 | -3 |  |  | 1 | 1 | 1 | 6 | 6 | 6
1219 | Bofferdange- Bertrange | Light PINT | 26 | 40 | 16 |  | 3 | 4 | 2 | 12 | 15 | 10 | -19 | -14 | -27 |  | 4 | 9 | 10 |  |  |  | 171 | 218 | 144 |  | -2 | 0 | -5 | 0 | 0 | 0 |  |  | 421 | 421 | 421 | 5 | 5 | 5
1220 | Offshore Wind Connection Viana do Castelo | TOOT | 27 | 35 | 17 | 161 | 36 | 39 | 34 | 203 | 216 | 189 | -242 | -231 | -263 | 1 | 47 | 117 | 125 | 0 | 1 | 1 | 2885 | 3026 | 2714 | 2000 | -64 | -6 | -32 | -1 | -2 | -3 | 139 | 14 | 328 | 328 | 328 | 3 | 3 | 3
1221 | Offshore Wind Connection Leixões | TOOT | 17 | 24 | 10 | 116 | 26 | 28 | 24 | 148 | 156 | 137 | -174 | -165 | -190 | 6 | 34 | 84 | 90 | 1 | 3 | 3 | 2106 | 2194 | 1963 | 1500 | -40 | -4 | -20 | -1 | -1 | -2 | 134 | 13 | 242 | 242 | 242 | 2 | 2 | 2
1222 | Offshore Wind Connection Figueira da Foz (North) | TOOT | 29 | 37 | 19 | 159 | 36 | 39 | 34 | 203 | 216 | 189 | -242 | -231 | -263 | 4 | 47 | 117 | 125 | 1 | 2 | 2 | 2885 | 3026 | 2714 | 2000 | -64 | -6 | -32 | -1 | -2 | -3 | 120 | 13 | 327 | 327 | 327 | 3 | 3 | 3
1223 | Offshore Wind Connection Figueira da Foz (South) | TOOT | 29 | 37 | 19 | 159 | 36 | 39 | 34 | 203 | 216 | 189 | -242 | -231 | -263 | 4 | 47 | 117 | 125 | 1 | 2 | 2 | 2885 | 3026 | 2714 | 2000 | -64 | -6 | -32 | -1 | -2 | -3 | 133 | 13 | 329 | 329 | 329 | 3 | 3 | 3
1224 | Offshore Wind Connection Ericeira | TOOT | 9 | 13 | 1 | 77 | 16 | 18 | 15 | 95 | 101 | 86 | -109 | -101 | -121 | 4 | 21 | 52 | 56 | 1 | 2 | 2 | 1352 | 1421 | 1239 | 1000 | -35 | -3 | -18 | -1 | -1 | -1 | 15 | 3 | 159 | 159 | 159 | 1 | 1 | 1
1225 | Offshore Wind Connection Sines | TOOT | 14 | 22 | 7 | 119 | 26 | 28 | 24 | 148 | 156 | 137 | -174 | -165 | -190 | 3 | 34 | 84 | 90 | 1 | 2 | 2 | 2106 | 2194 | 1963 | 1500 | -40 | -4 | -20 | -1 | -1 | -2 | -63 | 0 | 241 | 241 | 241 | 2 | 2 | 2
1226 | North-South Electricity Corridor in Eastern Europe | Light PINT | 554 | 578 | 531 |  | 174 | 184 | 163 | 161 | 164 | 158 | -1181 | -1107 | -1255 |  | 227 | 568 | 608 |  |  |  | 2293 | 2307 | 2279 |  | -1020 | -278 | -246 | -14 | -17 | -98 |  |  | 600 | 600 | 600 | 7 | 7 | 7
1229 | Rhine-Main-Link | PINT | 1887 | 2170 | 1705 |  | 46 | 56 | 40 | 683 | 813 | 602 | -315 | -271 | -382 | 52 | 61 | 152 | 162 | 10 | 25 | 27 | 7 | 8 | 6 |  | -238 | -75 | -7 | -2 | -2 | -26 | 1451 | 69 | 0 | 0 | 0 | 0 | 0 | 18
1230 | TuNur Malta | PINT | 27 | 41 | 16 | 296 | 68 | 70 | 67 | 243 | 247 | 239 | -463 | -455 | -474 | -1 | 89 | 223 | 239 | 0 | -1 | -1 | 3462 | 3495 | 3426 | 1400 | -91 | -28 | -6 | -1 | -1 | -10 | -98 | -3 | 0 | 0 | 0 | 0 | 0 | 0
1231 | Green Aegean Interconnector | Light PINT | 1088 | 1114 | 1058 |  | 219 | 219 | 219 | 376 | 379 | 372 | -1490 | -1490 | -1490 |  | 286 | 717 | 767 |  |  |  | 5351 | 5408 | 5305 |  | -434 | -140 | -25 | -4 | -3 | -49 |  |  | 1455 | 1455 | 1455 | 18 | 18 | 18
1233 | Laufenburg - Beznau - Breite | Light PINT | 151 | 155 | 143 |  | 35 | 44 | 27 | 148 | 150 | 145 | -239 | -185 | -298 |  | 46 | 115 | 123 |  |  |  | 2112 | 2163 | 2067 |  | -138 | -46 | -1 | -1 | -1 | -16 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1234 | 220-kV Reitdorf (AT) - Weißenbach (AT) | TOOT | 1 | 5 | 0 | 37 | 4 | 4 | 3 | 43 | 47 | 39 | -26 | -23 | -31 | -3 | 5 | 13 | 14 | -1 | -1 | -1 | 608 | 654 | 555 | 500 | -17 | -3 | -8 | 0 | 0 | -1 | -59 | -2 | 0 | 0 | 0 | 0 | 0 | 0
1235 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | PINT | 20 | 23 | 14 |  | 8 | 9 | 6 | 3 | 6 | 0 | -52 | -38 | -59 | -52 | 10 | 25 | 27 | -10 | -25 | -27 | 39 | 84 | 0 |  | -2 | -8 | 40 | 1 | 2 | -3 | -445 | -30 | 29 | 29 | 29 | 0 | 0 | 0
1236 | Power-to-Gas for Austria (P2G4A) | PINT | 3 | 5 | 0 |  | 1 | 2 | 0 | -1 | 7 | -8 | -9 | -3 | -12 | -1 | 2 | 4 | 5 | 0 | 0 | 0 | -11 | 97 | -114 |  | -1 | 1 | -4 | 0 | 0 | 0 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0
1239 | Interconnection Ukraine-Slovak Republic | Light PINT | 158 | 167 | 146 |  | 66 | 75 | 56 | 6 | 10 | 3 | -448 | -382 | -510 |  | 86 | 216 | 231 |  |  |  | 86 | 148 | 46 |  | -350 | -48 | -204 | -8 | -15 | -17
1240 | Interconnection Ukraine-Romania | Light PINT | 249 | 252 | 247 |  | 112 | 131 | 99 | 20 | 29 | 14 | -764 | -671 | -894 |  | 147 | 367 | 393 |  |  |  | 285 | 419 | 200 |  | -607 | -87 | -303 | -14 | -26 | -31

## 2030NT-ENTSO-E
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 62 | 62 | 62 | 62 | 54 | 55 | 52 | 132 | 138 | 127 | -474 | -463 | -485 | 53 | 6 | 59 | 96 | 1 | 7 | 11 | 2043 | 2142 | 1944 | 1154 | -74 | -23 | -3 | -1 | -1 | -8 | 157 | 12 | 1957 | 1957 | 1957 | 14 | 14 | 14
4 | Interconnection Portugal-Spain | TOOT | 29 | 32 | 27 |  | 13 | 16 | 11 | 21 | 23 | 18 | -117 | -93 | -145 | 23 | 1 | 15 | 24 | 0 | 3 | 5 | 325 | 361 | 281 |  | -22 | -8 | -5 | 0 | 0 | -3 | 41 | 5 | 245 | 245 | 245 | 3 | 3 | 3
16 | Biscay Gulf | TOOT | 401 | 405 | 397 |  | 133 | 136 | 129 | 224 | 256 | 200 | -1170 | -1134 | -1196 | 356 | 15 | 146 | 236 | 4 | 44 | 72 | 3443 | 3977 | 3051 |  | -536 | -159 | -58 | -6 | -6 | -56 | 2591 | 123 | 2304 | 2304 | 2304 | 76 | 76 | 76
28 | Italy-Montenegro | TOOT | 30 | 39 | 16 |  | 18 | 23 | 13 | 16 | 18 | 14 | -156 | -111 | -206 | 28 | 2 | 19 | 31 | 0 | 3 | 6 | 244 | 277 | 220 |  | -69 | -22 | -2 | -1 | -1 | -8 | 102 | 8 | 21 | 21 | 21 | 0 | 0 | 0
29 | Italy-Tunisia | TOOT | 62 | 63 | 61 |  | -112 | -103 | -121 | 22 | 24 | 21 | 1070 | 1070 | 1070 | -18 | 0 | 0 | 0 | 0 | -2 | -4 | 343 | 371 | 316 |  | -329 | -103 | -14 | -3 | -3 | -36 | -64 | -5 | 115 | 115 | 115 | 2 | 2 | 2
33 | Central Northern Italy | TOOT | 6 | 13 | 2 |  | 2 | 4 | 1 | 4 | 8 | 2 | -20 | -7 | -34 | -13 | 0 | 3 | 4 | 0 | -2 | -3 | 70 | 118 | 30 |  | -28 | -3 | -12 | -1 | -1 | -1 | 59 | -3 | 17 | 17 | 17 | 0 | 0 | 0
35 | CZ Southwest-east corridor | TOOT | 86 | 96 | 79 |  | 58 | 59 | 55 | 26 | 27 | 25 | -511 | -486 | -524 | 32 | 6 | 64 | 103 | 0 | 4 | 6 | 403 | 416 | 381 |  | -210 | -63 | -14 | -2 | -2 | -22 | 289 | 14 | 179 | 179 | 179 | 3 | 3 | 3
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 21 | 23 | 18 |  | 8 | 10 | 5 | 16 | 18 | 13 | -67 | -41 | -88 |  | 1 | 8 | 14 |  |  |  | 244 | 278 | 205 |  | -39 | -9 | -14 | -1 | -1 | -3 |  |  | 11 | 11 | 11 | 0 | 0 | 0
47 | Westtirol (AT) - Vöhringen (DE) | TOOT | 39 | 44 | 36 |  | 17 | 20 | 15 | 27 | 28 | 25 | -152 | -136 | -180 | 27 | 2 | 19 | 31 | 0 | 3 | 5 | 413 | 433 | 389 |  | -61 | -18 | -6 | -1 | -1 | -6 | 147 | 9 | 196 | 196 | 196 | 3 | 3 | 3
81 | North South Interconnector | TOOT | 76 | 88 | 67 |  | 30 | 33 | 26 | 30 | 39 | 21 | -267 | -227 | -289 | -1 | 3 | 33 | 54 | 0 | 0 | 0 | 457 | 588 | 325 |  | -85 | -28 | -6 | -1 | 0 | -10 | -40 | 0 | 153 | 153 | 153 | 3 | 3 | 3
85 | Integration of RES in Alentejo | TOOT | 1 | 3 | 0 | 12 | 1 | 4 | -2 | 20 | 20 | 19 | -9 | 17 | -33 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 302 | 311 | 293 | 442 | -3 | -2 | -1 | 0 | 0 | -1 | 19 | 1 | 0 | 0 | 0 | 0 | 0 | 0
94 | GerPol Improvements | TOOT | 153 | 185 | 132 |  | 76 | 83 | 67 | 37 | 38 | 36 | -672 | -590 | -728 | 79 | 8 | 84 | 135 | 1 | 10 | 16 | 564 | 584 | 543 |  | -387 | -52 | -259 | -10 | -17 | -19 | 478 | 27 | 473 | 473 | 473 | 8 | 8 | 8
107 | Celtic Interconnector | TOOT | 251 | 257 | 247 |  | 52 | 57 | 49 | 199 | 202 | 195 | -460 | -433 | -500 | 90 | 6 | 57 | 93 | 1 | 11 | 18 | 3057 | 3089 | 3033 |  | -107 | -39 | -44 | 0 | 0 | -14 | 866 | 32 | 828 | 828 | 828 | 27 | 27 | 27
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 45 | 46 | 45 |  | 10 | 16 | 4 | 43 | 45 | 42 | -87 | -32 | -144 | 6 | 1 | 11 | 18 | 0 | 1 | 1 | 670 | 690 | 652 |  | -107 | -1 | -79 | -3 | -5 | -1 | 4 | 2 | 602 | 602 | 602 | 8 | 8 | 8
120 | Princess Elisabeth Island (MOG 2) | TOOT | 307 | 336 | 279 | 559 | 240 | 245 | 236 | 853 | 854 | 852 | -2116 | -2080 | -2164 | 136 | 27 | 264 | 427 | 2 | 17 | 27 | 13266 | 13526 | 12974 | 3600 | -742 | -208 | -112 | -9 | -11 | -73 | 648 | 42 | 1121 | 1121 | 1121 | 16 | 16 | 16
121 | Nautilus: multi-purpose interconnector Belgium - UK | TOOT | 98 | 100 | 97 |  | 70 | 70 | 68 | 13 | 17 | 11 | -613 | -601 | -620 | 37 | 8 | 76 | 124 | 0 | 5 | 8 | 206 | 264 | 168 |  | -220 | -59 | -37 | -3 | -4 | -21 | 158 | 11 | 622 | 622 | 622 | 8 | 8 | 8
124 | Ekhyddan-Nybro-Hemsjö | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 37 | 39 | 36 |  | 20 | 24 | 16 | 2 | 4 | 1 | -177 | -140 | -209 | 22 | 2 | 22 | 36 | 0 | 3 | 4 | 34 | 69 | 9 |  | -211 | -20 | -110 | -5 | -6 | -8 | 177 | 11 | 100 | 100 | 100 | 0 | 0 | 0
127 | Central Southern Italy | TOOT | 29 | 34 | 23 |  | 13 | 14 | 12 | 12 | 14 | 10 | -117 | -105 | -126 | 29 | 1 | 15 | 24 | 0 | 4 | 6 | 185 | 215 | 157 |  | -39 | -14 | -2 | 0 | 0 | -5 | 132 | 8 | 348 | 348 | 348 | 0 | 0 | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 233 | 299 | 176 |  | 90 | 151 | 41 | 96 | 124 | 71 | -793 | -365 | -1330 | 27 | 10 | 99 | 160 | 0 | 3 | 5 | 1 | 1 | 1 |  | -379 | -98 | -55 | -4 | -5 | -35 | 0 | -9
132 | HVDC Line A-North | TOOT | 812 | 932 | 721 |  | 121 | 196 | 27 | 413 | 476 | 363 | -1071 | -239 | -1461 | 52 | 13 | 133 | 216 | 1 | 6 | 10 | 4 | 5 | 4 |  | -466 | -135 | -38 | -5 | -5 | -48 | 0 | -18
138 | Black Sea Corridor | TOOT | 11 | 17 | 8 |  | -6 | 9 | -19 | -2 | 0 | -3 | 105 | 171 | 65 | 26 | 0 | 0 | 0 | 0 | 3 | 5 | -26 | 6 | -52 |  | -18 | -6 | -4 | 0 | 0 | -2 | 94 | 7 | 296 | 296 | 296 | 0 | 0 | 0
144 | Mid Continental East corridor | TOOT | 16 | 26 | 7 |  | 9 | 14 | 3 | -1 | 2 | -3 | -83 | -26 | -126 | 22 | 1 | 10 | 17 | 0 | 3 | 4 | -11 | 26 | -43 |  | -33 | -8 | -6 | 0 | -1 | -3 | 82 | 6 | 459 | 459 | 459 | 7 | 7 | 7
150 | Italy-Slovenia | TOOT | 16 | 19 | 13 |  | 12 | 15 | 9 | 1 | 7 | -4 | -102 | -82 | -131 | 30 | 1 | 13 | 20 | 0 | 4 | 6 | 17 | 112 | -58 |  | -38 | -10 | -8 | -1 | -1 | -3 | 98 | 8 | 86 | 86 | 86 | 1 | 1 | 1
153 | France-Alderney-Britain | TOOT | 90 | 95 | 86 |  | 79 | 80 | 78 | 28 | 29 | 25 | -695 | -689 | -705 | 120 | 9 | 87 | 140 | 2 | 15 | 24 | 428 | 449 | 386 |  | -201 | -63 | -9 | -2 | -2 | -22 | 688 | 40 | 1426 | 1426 | 1426 | 29 | 29 | 29
170 | Baltic States Synchronization with Continental Europe | TOOT | 276 | 282 | 269 |  | 189 | 196 | 180 | 130 | 132 | 127 | -1670 | -1592 | -1727 | -198 | 21 | 208 | 337 | -3 | -25 | -40 | 2004 | 2047 | 1957 |  | -64 | -111 | -113 | -3 | -15 | -31 | -1083 | -64 | 594 | 594 | 594 | 10 | 10 | 10
174 | Greenconnector | TOOT | 109 | 114 | 104 |  | 85 | 90 | 81 | 1 | 5 | -2 | -750 | -712 | -797 | 98 | 9 | 93 | 151 | 1 | 12 | 20 | 11 | 74 | -30 |  | -353 | -102 | -49 | -4 | -5 | -36 | 567 | 34 | 74 | 74 | 74 | 2 | 2 | 2
176 | Hansa PowerBridge I | TOOT | 137 | 142 | 129 |  | 69 | 75 | 61 | 24 | 27 | 22 | -612 | -540 | -664 | 57 | 8 | 76 | 123 | 1 | 7 | 11 | 361 | 413 | 333 |  | -145 | -69 | -26 | 0 | 0 | -23 | 245 | 18 | 265 | 265 | 265 | 4 | 4 | 4
187 | St. Peter (AT) - Pleinting (DE) | TOOT | 221 | 234 | 207 |  | 100 | 114 | 83 | 126 | 132 | 121 | -881 | -736 | -1003 | 18 | 11 | 110 | 178 | 0 | 2 | 4 | 1937 | 2016 | 1855 |  | -363 | -94 | -92 | -5 | -7 | -33 | 73 | 4 | 1670 | 1670 | 1670 | 26 | 26 | 26
200 | CZ Northwest-South corridor | TOOT | 86 | 96 | 79 |  | 58 | 59 | 55 | 26 | 27 | 25 | -511 | -486 | -524 | 6 | 6 | 64 | 103 | 0 | 1 | 1 | 403 | 416 | 381 |  | -210 | -63 | -14 | -2 | -2 | -22 | 198 | 7 | 183 | 183 | 183 | 3 | 3 | 3
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 21 | 26 | 18 |  | 12 | 13 | 10 | 0 | 2 | -1 | -104 | -89 | -111 | 3 | 1 | 13 | 21 | 0 | 0 | 1 | 1 | 26 | -14 |  | -53 | -12 | -14 | -1 | -1 | -4 | 35 | 2 | 28 | 28 | 28 | 0 | 0 | 0
219 | Great Sea Interconnector | TOOT | 159 | 166 | 150 |  | -139 | -130 | -148 | 2 | 4 | 0 | 1295 | 1307 | 1283 | 244 | 0 | 0 | 0 | 3 | 30 | 49 | 26 | 59 | -6 |  | -466 | -154 | -3 | -4 | -3 | -54 | 597 | 60 | 147 | 147 | 147 | 1 | 1 | 1
225 | 2nd interconnector Belgium - Germany | light PINT | 56 | 61 | 53 |  | 24 | 26 | 22 | 51 | 58 | 42 | -216 | -191 | -232 | 128 | 3 | 27 | 43 | 2 | 16 | 26 | 778 | 882 | 637 |  | -85 | -23 | -21 | -1 | -2 | -8 | 630 | 38 | 43 | 43 | 43 | 1 | 1 | 1
227 | Transbalkan Corridor | TOOT | 6 | 10 | 1 |  | 3 | 6 | 0 | -2 | -1 | -4 | -22 | 3 | -51 | -25 | 0 | 3 | 4 | 0 | -3 | -5 | -34 | -16 | -56 |  | -3 | 0 | -3 | 0 | 0 | 0 | -91 | -7 | 116 | 116 | 116 | 2 | 2 | 2
228 | Muhlbach - Eichstetten | TOOT | 24 | 27 | 21 |  | 9 | 11 | 8 | 16 | 20 | 12 | -81 | -71 | -96 | 27 | 1 | 10 | 16 | 0 | 3 | 5 | 252 | 313 | 184 |  | -32 | -8 | -7 | 0 | -1 | -3 | 177 | 9 | 259 | 259 | 259 | 9 | 9 | 9
231 | Beznau - Tiengen | TOOT | 44 | 48 | 39 |  | 18 | 25 | 14 | 36 | 40 | 32 | -162 | -125 | -217 | 60 | 2 | 20 | 33 | 1 | 7 | 12 | 552 | 611 | 482 |  | -83 | -24 | -13 | -1 | -1 | -8 | 122 | 16 | 24 | 24 | 24 | 0 | 0 | 0
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 845 | 1049 | 715 |  | 163 | 206 | 135 | 385 | 488 | 316 | -1441 | -1192 | -1278 | 80 | 18 | 180 | 291 | 1 | 10 | 16 | 4 | 5 | 3 |  | -657 | -180 | -74 | -7 | -8 | -64 | -1 | -32
239 | Fenno-Skan 3 | Light PINT | 32 | 38 | 26 |  | 9 | 11 | 5 | 20 | 22 | 18 | -80 | -46 | -99 |  | 1 | 10 | 16 |  |  |  | 308 | 335 | 282 |  | -76 | -9 | -37 | -2 | -2 | -3 |  |  | 103 | 103 | 103 | 1 | 1 | 1
243 | New 400 kV interconnection line between Serbia and Croatia | Light PINT | 5 | 6 | 4 |  | 3 | 3 | 1 | 4 | 6 | 2 | -21 | -6 | -30 |  | 0 | 3 | 4 |  |  |  | 55 | 87 | 25 |  | -9 | -2 | -1 | 0 | 0 | -1 |  |  | 4 | 4 | 4 | 0 | 0 | 0
244 | Vigy - Uchtelfangen area | TOOT | 131 | 133 | 129 |  | 57 | 57 | 57 | 93 | 94 | 91 | -503 | -500 | -506 | 173 | 6 | 63 | 101 | 2 | 22 | 35 | 1428 | 1460 | 1396 |  | -249 | -52 | -101 | -5 | -7 | -19 | 1051 | 56 | 1430 | 1430 | 1430 | 50 | 50 | 50
247 | AQUIND Interconnector | TOOT | 138 | 138 | 137 |  | 124 | 127 | 122 | 42 | 45 | 38 | -1090 | -1072 | -1118 | 128 | 14 | 136 | 220 | 2 | 16 | 26 | 648 | 687 | 590 |  | -306 | -98 | -2 | -2 | -3 | -34 | 622 | 39 | 2231 | 2231 | 2231 | 40 | 40 | 40
250 | Merchant line Castasegna (CH) - Mese (IT) | TOOT | 19 | 25 | 13 |  | 14 | 15 | 13 | -2 | 0 | -3 | -124 | -116 | -134 | 26 | 2 | 15 | 25 | 0 | 3 | 5 | -25 | 1 | -46 |  | -47 | -16 | -2 | 0 | 0 | -5 | 128 | 8 | 6 | 6 | 6 | 0 | 0 | 0
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 168 | 196 | 151 |  | 32 | 35 | 29 | 70 | 81 | 62 | -284 | -254 | -278 | 49 | 4 | 35 | 57 | 1 | 6 | 10 | 1 | 1 | 1 |  | -140 | -35 | -23 | -2 | -2 | -13 | -0.310590856 | -18
259 | HU-RO | TOOT | 8 | 11 | 5 |  | 8 | 11 | 4 | 3 | 3 | 2 | -67 | -35 | -96 | 36 | 1 | 8 | 13 | 0 | 4 | 7 | 42 | 47 | 34 |  | -26 | -8 | -2 | 0 | 0 | -3 | 120 | 10 | 41 | 41 | 41 | 1 | 1 | 1
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | TOOT | 100 | 104 | 97 |  | 88 | 90 | 84 | 57 | 64 | 48 | -774 | -741 | -795 | -166 | 10 | 96 | 156 | -2 | -21 | -34 | 871 | 998 | 735 |  | -297 | -77 | -68 | -4 | -6 | -27 | -894 | -58 | 952 | 952 | 952 | 30 | 30 | 30
267 | Hansa PowerBridge II | Light PINT | 120 | 125 | 113 |  | 60 | 67 | 53 | 22 | 26 | 20 | -526 | -466 | -590 |  | 7 | 65 | 106 |  |  |  | 344 | 401 | 308 |  | -72 | -63 | -164 | -5 | -7 | -19 |  |  | 55 | 55 | 55 | 1 | 1 | 1
270 | FR-ES project -Aragón-Atlantic Pyrenees | TOOT | 219 | 220 | 217 |  | 73 | 85 | 58 | 132 | 150 | 115 | -647 | -514 | -754 | 232 | 8 | 81 | 130 | 3 | 29 | 47 | 2030 | 2323 | 1744 |  | -308 | -91 | -34 | -3 | -4 | -32 | 1544 | 79 | 584 | 584 | 584 | 19 | 19 | 19
276 | FR-ES project -Navarra-Landes | PINT | 219 | 220 | 217 |  | 73 | 85 | 58 | 132 | 150 | 115 | -647 | -514 | -754 | 229 | 8 | 81 | 130 | 3 | 29 | 46 | 2030 | 2323 | 1744 |  | -308 | -91 | -34 | -3 | -4 | -32 | 1555 | 79 | 581 | 581 | 581 | 19 | 19 | 19
280 | FR-BE: Lonny-Achene-Gramme | TOOT | 45 | 48 | 42 |  | 20 | 21 | 19 | 27 | 29 | 24 | -179 | -169 | -189 | 69 | 2 | 22 | 36 | 1 | 9 | 14 | 420 | 445 | 369 |  | -75 | -18 | -25 | -1 | -2 | -6 | 408 | 23 | 0 | 0 | 0 | 0 | 0 | 0
283 | TuNur Italy | PINT | 15 | 20 | 10 | 0 | 346 | 360 | 335 | -24 | -24 | -25 | -3054 | -2958 | -3172 | 104 | 38 | 381 | 616 | 1 | 13 | 21 | -371 | -360 | -382 | 5000 | -1095 | -346 | -36 | -9 | -9 | -121 | 367 | 27 | 11 | 11 | 11 | 0 | 0 | 0
285 | GridLink | TOOT | 90 | 95 | 86 |  | 79 | 80 | 78 | 28 | 29 | 25 | -695 | -689 | -705 | 101 | 9 | 87 | 140 | 1 | 13 | 20 | 428 | 449 | 386 |  | -201 | -63 | -9 | -2 | -2 | -22 | 561 | 33 | 1425 | 1425 | 1425 | 29 | 29 | 29
297 | BRABO III | TOOT | 37 | 38 | 34 |  | 8 | 10 | 5 | 48 | 53 | 40 | -72 | -48 | -92 | 18 | 1 | 9 | 14 | 0 | 2 | 4 | 745 | 818 | 608 |  | -11 | -4 | -1 | 0 | 0 | -2 | 86 | 5 | 84 | 84 | 84 | 1 | 1 | 1
299 | SACOI 3 | TOOT | 120 | 134 | 103 |  | 55 | 58 | 49 | 6 | 9 | 2 | -483 | -430 | -511 | 23 | 6 | 60 | 97 | 0 | 3 | 5 | 93 | 134 | 30 |  | -1922 | -15 | -1308 | -50 | -70 | -14 | 79 | 6 | 307 | 307 | 307 | 7 | 7 | 7
309 | NeuConnect | TOOT | 92 | 94 | 89 |  | 131 | 135 | 124 | 43 | 48 | 40 | -1155 | -1097 | -1194 | 140 | 15 | 144 | 233 | 2 | 17 | 28 | 668 | 739 | 604 |  | -435 | -114 | -94 | -6 | -8 | -40 | 682 | 43 | 755 | 755 | 755 | 11 | 11 | 11
312 | St. Peter (AT) - Tauern (AT) | TOOT | 160 | 165 | 154 |  | 73 | 82 | 61 | 95 | 99 | 93 | -645 | -541 | -726 | -102 | 8 | 80 | 130 | -1 | -13 | -20 | 1467 | 1503 | 1421 |  | -278 | -72 | -68 | -4 | -5 | -25 | -545 | -32 | 1199 | 1199 | 1199 | 19 | 19 | 19
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 103 | 105 | 98 |  | 47 | 53 | 40 | 64 | 65 | 62 | -415 | -349 | -470 | 100 | 5 | 52 | 84 | 1 | 13 | 20 | 984 | 1004 | 955 |  | -176 | -47 | -34 | -2 | -3 | -17 | 108 | 31 | 700 | 700 | 700 | 11 | 11 | 11
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 5 | 8 | 0 |  | -1 | 2 | -3 | -2 | -1 | -3 | 5 | 30 | -16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | -30 | -19 | -44 |  | -6 | -1 | -2 | 0 | 0 | 0 | 5 | 1 | 6 | 6 | 6 | 0 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 2 | 4 | 1 |  | 1 | 2 | -1 | -2 | -1 | -4 | -5 | 13 | -19 | 5 | 0 | 1 | 1 | 0 | 1 | 1 | -30 | -9 | -57 |  | -6 | -1 | -2 | 0 | 0 | -1 | 13 | 1 | 9 | 9 | 9 | 0 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | TOOT | 108 | 116 | 99 |  | 65 | 69 | 62 | 21 | 24 | 16 | -571 | -547 | -605 | 64 | 7 | 71 | 115 | 1 | 8 | 13 | 321 | 365 | 241 |  | -238 | -68 | -35 | -3 | -3 | -24 | -352 | -21 | 29 | 29 | 29 | 0 | 0 | 0
328 | Interconnector DE-LUX | TOOT | 0 | 0 | 0 |  | -2 | 0 | -4 | -1 | 2 | -3 | 17 | 34 | -1 | -86 | 0 | 0 | 0 | -1 | -11 | -17 | -14 | 27 | -39 |  | -2 | -2 | -2 | 0 | 0 | -1 | -220 | -23 | 0 | 0 | 0 | 0 | 0 | 0
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 352 | 370 | 325 |  | 126 | 132 | 117 | 274 | 288 | 253 | -2831 | -2978 | -2613 | -20 | 357 | 674 | 892 | 0 | -2 | -4 | 5776 | 5371 | 6046 | 0 | -3728 | -156 | -5563 | -151 | -414 | -61 | 641 | 13 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | TOOT | 25 | 29 | 18 |  | 7 | 11 | 4 | 10 | 13 | 8 | -64 | -38 | -100 | 32 | 1 | 8 | 13 | 0 | 4 | 6 | 154 | 200 | 126 |  | -21 | -3 | -19 | -1 | -1 | -1 | 121 | 9 | 18 | 18 | 18 | 0 | 0 | 0
335 | North Sea Wind Power Hub | Light PINT | 1519 | 1564 | 1474 | 1656 | 735 | 745 | 725 | 3491 | 3552 | 3430 | -6480 | -6393 | -6567 |  | 82 | 807 | 1306 |  |  |  | 53852 | 54361 | 53343 | 14000 | -2310 | -631 | -425 | -29 | -37 | -222 |  |  | 488 | 488 | 488 | 8 | 8 | 8
338 | Adriatic HVDC link | TOOT | 17 | 28 | 9 |  | 6 | 8 | 5 | 13 | 20 | 9 | -53 | -41 | -71 | 16 | 1 | 7 | 11 | 0 | 2 | 3 | 204 | 310 | 133 |  | -23 | -8 | -2 | 0 | 0 | -3 | 181 | 6 | 463 | 463 | 463 | 0 | 0 | 0
339 | Tyrrhenian link | TOOT | 102 | 105 | 101 |  | 49 | 51 | 46 | 42 | 43 | 40 | -432 | -405 | -448 | 80 | 5 | 54 | 87 | 1 | 10 | 16 | 639 | 665 | 607 |  | -162 | -50 | -6 | -1 | -2 | -18 | 353 | 23 | 1495 | 1495 | 1495 | 0 | 0 | 0
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 112 | 140 | 67 |  | 40 | 50 | 24 | 87 | 109 | 52 | -1213 | -1429 | -745 | -76 | 153 | 289 | 382 | -1 | -9 | -15 | 2030 | 1235 | 2599 | 0 | -2007 | -17 | -4309 | -45 | -277 | -16 | 310 | -6 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | TOOT | 6 | 12 | 0 |  | 2 | 5 | -1 | -1 | 2 | -5 | -16 | 11 | -45 | 29 | 0 | 2 | 3 | 0 | 4 | 6 | -22 | 31 | -79 |  | -1 | 0 | -1 | 0 | 0 | 0 | 21 | 7 | 278 | 278 | 278 | 4 | 4 | 4
342 | Central Balkan Corridor | TOOT | 9 | 9 | 7 |  | 3 | 6 | 0 | 3 | 4 | 3 | -23 | -1 | -52 | 12 | 0 | 4 | 6 | 0 | 2 | 3 | 50 | 56 | 41 |  | -16 | -6 | -2 | 0 | 0 | -2 | 43 | 4 | 17 | 17 | 17 | 0 | 0 | 0
343 | CSE1 New | TOOT | 3 | 4 | 2 |  | 3 | 5 | 2 | 2 | 4 | 0 | -27 | -19 | -40 | -25 | 0 | 3 | 5 | 0 | -3 | -5 | 29 | 67 | 3 |  | -14 | -4 | -5 | 0 | 0 | -1 | -79 | -6 | 2 | 2 | 2 | 0 | 0 | 0
346 | ZuidWest380 NL Oost | TOOT | 3 | 4 | 2 |  | 2 | 3 | 1 | 2 | 3 | 2 | -17 | -8 | -25 | -16 | 0 | 2 | 3 | 0 | -2 | -3 | 39 | 41 | 36 |  | -8 | -2 | -2 | 0 | 0 | -1 | -90 | -5 | 1 | 1 | 1 | 0 | 0 | 0
349 | MaresConnect | TOOT | 68 | 70 | 64 |  | 11 | 15 | 8 | 94 | 98 | 92 | -95 | -69 | -132 | 3 | 1 | 12 | 19 | 0 | 0 | 1 | 1448 | 1497 | 1411 |  | -3 | -5 | -42 | -1 | -1 | -2 | 61 | 1 | 418 | 418 | 418 | 7 | 7 | 7
350 | South Balkan Corridor | TOOT | 3 | 5 | 1 |  | 6 | 8 | 5 | 3 | 11 | -1 | 58 | 150 | -43 | 32 | 1 | 7 | 11 | 0 | 4 | 7 | 55 | 173 | -15 |  | -28 | -5 | -5 | 0 | -1 | -2 | 25 | 8 | 16 | 16 | 16 | 0 | 0 | 0
375 | Lienz (AT) - Veneto region (IT) 220 kV | TOOT | 65 | 78 | 54 |  | 40 | 42 | 37 | 11 | 12 | 10 | -355 | -324 | -371 | 25 | 4 | 44 | 72 | 0 | 3 | 5 | 167 | 182 | 156 |  | -150 | -43 | -24 | -2 | -2 | -15 | -135 | -8 | 33 | 33 | 33 | 0 | 0 | 0
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | Light PINT | 4 | 5 | 1 |  | 1 | 2 | 1 | 2 | 4 | 1 | -9 | 1 | -15 |  | 0 | 1 | 2 |  |  |  | 33 | 61 | 17 |  | -8 | -1 | -8 | 0 | 0 | 0 |  |  | 1 | 1 | 1 | 0 | 0 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | TOOT | 27 | 31 | 23 |  | 5 | 7 | 4 | 38 | 43 | 31 | -48 | -40 | -59 | 5 | 1 | 6 | 10 | 0 | 1 | 1 | 592 | 662 | 466 |  | -20 | -5 | -6 | 0 | 0 | -2 | 41 | 1 | 17 | 17 | 17 | 0 | 0 | 0
378 | Transformer Gatica | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 356 | 457 | 290 |  | 44 | 95 | -64 | 179 | 229 | 147 | -655 | -538 | -568 | -8 | 5 | 49 | 79 | 0 | -1 | -2 | 2 | 2 | 1 |  | -291 | -82 | -28 | -3 | -3 | -29 | -128 | -4 | 0 | 0 | 0 | 0 | 0
1039 | SE North-south long-term reinforcements | PINT | 25 | 26 | 23 |  | 14 | 16 | 13 | 2 | 3 | 1 | -128 | -114 | -140 |  | 2 | 16 | 26 |  |  |  | 35 | 53 | 16 |  | -140 | -15 | -70 | -3 | -4 | -6 |  |  | 93 | 93 | 93 | 0 | 0 | 0
1040 | LirIC | TOOT | 68 | 71 | 65 |  | 7 | 10 | 4 | 80 | 83 | 77 | -58 | -38 | -85 | 4 | 1 | 7 | 12 | 0 | 0 | 1 | 1228 | 1258 | 1202 |  | -1 | -7 | -42 | -1 | -1 | -2 | 163 | 1 | 32 | 32 | 32 | 1 | 1 | 1
1041 | GREGY Green Energy Interconnector | TOOT | 112 | 151 | 75 |  | -34 | 317 | -311 | 0 | 3 | -2 | 2768 | 2792 | 2743 | 349 | 0 | 0 | 0 | 4 | 44 | 70 | 0 | 50 | -38 |  | -357 | -110 | -23 | -3 | -4 | -39 | 1142 | 91 | 151 | 151 | 151 | 2 | 2 | 2
1046 | Finnish North-South reinforcement | PINT | 391 | 391 | 391 |  | 49 | 49 | 49 | 480 | 480 | 480 | 436 | 436 | 436 | -7 | 5 | 54 | 88 | 0 | -1 | -1 | 7505 | 7505 | 7505 |  | -2 | 0 | -2 | 0 | 0 | 0 | -495 | -25 | 0 | 0 | 0 | 0 | 0 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 15 | 21 | 9 |  | 0 | 7 | -6 | 2 | 3 | 2 | 16 | 49 | -19 | -4 | 0 | 0 | 0 | 0 | 0 | -1 | 37 | 48 | 27 |  | -14 | -6 | -4 | 0 | 0 | -2 | -30 | -2 | 5 | 5 | 5 | 0 | 0 | 0
1049 | Cronos Energy Ltd | PINT | 94 | 109 | 84 |  | 107 | 109 | 106 | 3 | 4 | 2 | -946 | -936 | -965 | -6 | 12 | 118 | 191 | 0 | -1 | -1 | 43 | 58 | 31 |  | -314 | -91 | -37 | -3 | -4 | -32 | -910 | -27 | 161 | 161 | 161 | 2 | 2 | 2
1050 | Tarchon Energy Ltd | TOOT | 91 | 106 | 77 |  | 126 | 128 | 124 | 46 | 48 | 43 | -1113 | -1098 | -1127 | 106 | 14 | 139 | 224 | 1 | 13 | 21 | 708 | 743 | 653 |  | -389 | -106 | -72 | -5 | -7 | -37 | 539 | 33 | 227 | 227 | 227 | 2 | 2 | 2
1052 | Lienz (AT) - Malta (AT) - Obersielach (AT) | TOOT | 247 | 273 | 222 | 165 | 193 | 207 | 178 | 235 | 241 | 229 | -1698 | -1573 | -1823 | 56 | 21 | 212 | 342 | 1 | 7 | 11 | 3620 | 3685 | 3554 | 2000 | -712 | -198 | -125 | -9 | -11 | -70 | -330 | -20 | 45 | 45 | 45 | 1 | 1 | 1
1054 | 220-kV Westtirol (AT) - Zell/Ziller (AT) | TOOT | 36 | 37 | 35 |  | 16 | 18 | 16 | 25 | 27 | 22 | -145 | -137 | -156 | 40 | 2 | 18 | 29 | 1 | 5 | 8 | 379 | 416 | 333 |  | -61 | -16 | -10 | -1 | -1 | -6 | 189 | 13 | 199 | 199 | 199 | 3 | 3 | 3
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 102 | 104 | 100 |  | -124 | -113 | -134 | 0 | 2 | -2 | 999 | 1001 | 997 | 557 | 0 | 0 | 0 | 7 | 69 | 112 | 2 | 25 | -36 |  | -398 | -136 | -6 | -3 | -3 | -47 | 1659 | 144 | 83 | 83 | 83 | 0 | 0 | 0
1058 | HVDC Interconnector DE-CH | Light PINT | 90 | 96 | 83 |  | 40 | 44 | 35 | 56 | 61 | 51 | -349 | -308 | -392 |  | 4 | 44 | 70 |  |  |  | 862 | 944 | 778 |  | -129 | -38 | -22 | -2 | -2 | -13 |  |  | 103 | 103 | 103 | 2 | 2 | 2
1059 | Southern Italy | TOOT | 9 | 14 | 4 |  | 5 | 6 | 4 | 7 | 11 | 5 | -47 | -38 | -54 | 5 | 1 | 6 | 10 | 0 | 1 | 1 | 110 | 168 | 72 |  | -19 | -6 | 0 | 0 | 0 | -2 | 97 | 2 | 210 | 210 | 210 | 0 | 0 | 0
1066 | Bulgaria - Turkey | Light PINT | 74 | 75 | 73 |  | -246 | -237 | -255 | 2 | 3 | 0 | 2101 | 2248 | 1963 |  | 0 | 0 | 0 |  |  |  | 30 | 47 | 6 |  | -819 | -257 | -28 | -7 | -7 | -90 |  |  | 153 | 153 | 153 | 2 | 2 | 2
1067 | New AC 400 kV interconnection line Greece - Turkey | Light PINT | 43 | 44 | 41 |  | -116 | -111 | -121 | 1 | 2 | 0 | 1005 | 1063 | 972 |  | 0 | 0 | 0 |  |  |  | 14 | 28 | 6 |  | -389 | -122 | -13 | -3 | -3 | -43 |  |  | 68 | 68 | 68 | 1 | 1 | 1
1068 | LaSGo Link | PINT | 45 | 49 | 41 |  | 24 | 26 | 20 | 22 | 22 | 21 | -209 | -173 | -232 | 10 | 3 | 26 | 42 | 0 | 1 | 2 | 331 | 341 | 319 |  | -670 | -15 | -420 | -17 | -23 | -11 | 122 | 6 | 12 | 12 | 12 | 0 | 0 | 0
1074 | Pannonian Corridor | TOOT | 8 | 8 | 8 |  | 4 | 6 | 3 | 2 | 3 | 1 | -36 | -23 | -49 | 14 | 0 | 4 | 7 | 0 | 2 | 3 | 28 | 43 | 13 |  | -4 | -3 | -2 | 0 | 0 | -1 | 45 | 4 | 21 | 21 | 21 | 0 | 0 | 0
1085 | Malta-Italy Cable Link No.2 | TOOT | 0 | 0 | 0 |  | -32 | -31 | -32 | 4 | 6 | 2 | 279 | 283 | 273 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 87 | 27 |  | -106 | -33 | -2 | -1 | -1 | -12 | 8 | 1 | 11 | 11 | 11 | 0 | 0 | 0
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 6 | 11 | 2 | 84 | 15 | 16 | 12 | 133 | 136 | 129 | -128 | -110 | -139 | 0 | 2 | 16 | 26 | 0 | 0 | 0 | 2050 | 2106 | 1964 | 700 | -378 | -6 | -247 | -10 | -13 | -6 | 76 | 3 | 2 | 2 | 2 | 0 | 0 | 0
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | TOOT | 24 | 30 | 16 | 70 | 14 | 18 | 11 | 134 | 136 | 132 | -124 | -95 | -156 | 2 | 2 | 15 | 25 | 0 | 0 | 0 | 2058 | 2076 | 2048 | 1000 | -194 | -6 | -119 | -5 | -6 | -4 | 41 | 3 | 67 | 67 | 67 | 1 | 1 | 1
1092 | TritonLink: offshore hybrid HVDC interconnector Belgium – Denmark | TOOT | 568 | 582 | 552 | 412 | 212 | 217 | 207 | 1078 | 1107 | 1054 | -1870 | -1830 | -1914 | 50 | 24 | 233 | 377 | 1 | 6 | 10 | 16553 | 16934 | 16052 | 4000 | -636 | -178 | -105 | -8 | -10 | -62 | 138 | 14 | 362 | 362 | 362 | 6 | 6 | 6
1094 | Estlink 3 | TOOT | 41 | 45 | 38 |  | 36 | 39 | 34 | 4 | 5 | 2 | -321 | -302 | -341 | 17 | 4 | 40 | 65 | 0 | 2 | 3 | 62 | 80 | 29 |  | -1592 | -14 | -1024 | -40 | -55 | -20 | 129 | 6 | 7 | 7 | 7 | 0 | 0 | 0
1095 | Aurora line 2 (4th AC Finland-Sweden north) | TOOT | 34 | 35 | 33 |  | 6 | 8 | 5 | 30 | 33 | 28 | -55 | -42 | -73 | 3 | 1 | 7 | 11 | 0 | 0 | 1 | 467 | 508 | 432 |  | -72 | -4 | -48 | -2 | -3 | -2 | 0 | 1 | 36 | 36 | 36 | 0 | 0 | 0
1096 | Beznau - Mettlen | Light TOOT | 55 | 59 | 48 |  | 29 | 36 | 21 | 42 | 43 | 41 | -258 | -183 | -315 |  | 3 | 32 | 52 |  |  |  | 643 | 660 | 626 |  | -116 | -39 | -5 | -1 | -1 | -13 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1097 | Upgrade to Konti-Skan | PINT | 111 | 118 | 106 |  | 44 | 51 | 37 | 35 | 39 | 30 | -391 | -325 | -448 | 63 | 5 | 49 | 79 | 1 | 8 | 13 | 530 | 590 | 458 |  | -120 | -45 | -6 | -1 | -1 | -15 | 294 | 13 | 76 | 76 | 76 | 1 | 1 | 1
1098 | Offshore Wind LT 2 | TOOT | 6 | 9 | 5 | 45 | 11 | 12 | 10 | 73 | 74 | 71 | -97 | -87 | -104 | 19 | 1 | 12 | 20 | 0 | 2 | 4 | 1115 | 1151 | 1081 | 700 | -214 | -7 | -132 | -5 | -7 | -4 | 132 | 7 | 45 | 45 | 45 | 1 | 1 | 1
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | TOOT | 85 | 94 | 76 |  | 57 | 60 | 52 | 26 | 31 | 23 | -506 | -461 | -533 | 54 | 6 | 63 | 102 | 1 | 7 | 11 | 403 | 474 | 358 |  | -205 | -63 | -13 | -2 | -2 | -22 | 391 | 20 | 29 | 29 | 29 | 0 | 0 | 0
1102 | Mettlen - Ulrichen | Light TOOT | 7 | 10 | 5 |  | 2 | 4 | 0 | 3 | 5 | 1 | -19 | 2 | -39 |  | 0 | 2 | 4 |  |  |  | 47 | 71 | 16 |  | -16 | -3 | -10 | 0 | -1 | -1 |  |  | 42 | 42 | 42 | 1 | 1 | 1
1103 | Bickigen - Chippis | Light TOOT | 34 | 37 | 32 |  | 17 | 20 | 14 | 28 | 28 | 27 | -149 | -127 | -173 |  | 2 | 19 | 30 |  |  |  | 428 | 441 | 418 |  | -57 | -17 | -2 | 0 | -1 | -6 |  |  | 1 | 1 | 1 | 0 | 0 | 0
1104 | Bauler - Roost | TOOT | 1 | 2 | 0 |  | -2 | 0 | -4 | -1 | 1 | -3 | 21 | 36 | -1 | -41 | 0 | 0 | 0 | -1 | -5 | -8 | -15 | 13 | -42 |  | -9 | -3 | -2 | 0 | 0 | -1 | 10 | -9 | 0 | 0 | 0 | 0 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 32 | 49 | 21 |  | -84 | -75 | -93 | 1 | 2 | -1 | 655 | 665 | 645 | -103 | 0 | 0 | 0 | -1 | -13 | -21 | 11 | 27 | -10 |  | -240 | -75 | -10 | -2 | -2 | -26 | 12 | -44 | 233 | 233 | 233 | 3 | 3 | 3
1106 | Bornholm Energy Island (BEI) | TOOT | 150 | 161 | 139 | 466 | 157 | 158 | 156 | 661 | 670 | 653 | -1384 | -1378 | -1389 | -21 | 17 | 172 | 279 | 0 | -3 | -4 | 10207 | 10255 | 10159 | 3000 | -440 | -136 | -29 | -4 | -5 | -48 | -90 | -6 | 233 | 233 | 233 | 3 | 3 | 3
1109 | Basilicata - Campania reinforcements | TOOT | 24 | 27 | 21 |  | 14 | 16 | 12 | 10 | 14 | 4 | -119 | -108 | -140 | 11 | 2 | 15 | 24 | 0 | 1 | 2 | 156 | 217 | 62 |  | -47 | -15 | -4 | 0 | 0 | -5 | -10 | 1 | 41 | 41 | 41 | 0 | 0 | 0
1110 | Sicily - Calabria | TOOT | 6 | 15 | 0 |  | 0 | 2 | -1 | 7 | 12 | 4 | -2 | 12 | -17 | -16 | 0 | 0 | 1 | 0 | -2 | -3 | 106 | 189 | 55 |  | -28 | -1 | -15 | -1 | -1 | -1 | 30 | -3 | 52 | 52 | 52 | 0 | 0 | 0
1112 | GRITA 2 | TOOT | 108 | 108 | 108 |  | 1 | 6 | -4 | 39 | 41 | 38 | -6 | 36 | -49 | 75 | 0 | 1 | 1 | 1 | 9 | 15 | 607 | 633 | 577 |  | -152 | -48 | -4 | -1 | -1 | -17 | 282 | 22 | 32 | 32 | 32 | 0 | 0 | 0
1121 | 220-kV Hessenberg (AT) - Weißenbach (AT) | TOOT | 0 | 0 | 0 | 63 | 17 | 19 | 15 | 61 | 63 | 60 | -153 | -136 | -169 | -11 | 2 | 19 | 31 | 0 | -1 | -2 | 946 | 974 | 917 | 600 | -51 | -14 | -9 | -1 | -1 | -5 | -78 | -4 | 2 | 2 | 2 | 0 | 0 | 0
1122 | Offshore Wind farm connection Centre Manche 1 | TOOT | 16 | 19 | 14 | 237 | 54 | 56 | 52 | 293 | 301 | 289 | -478 | -463 | -496 | 87 | 6 | 60 | 96 | 1 | 11 | 17 | 4507 | 4603 | 4395 | 1050 | -136 | -42 | -8 | -1 | -1 | -15 | 584 | 32 | 138 | 138 | 138 | 4 | 4 | 4
1123 | Offshore Wind farm connection Centre Manche 2 | TOOT | 25 | 28 | 21 | 277 | 64 | 67 | 62 | 355 | 366 | 346 | -567 | -547 | -590 | 75 | 7 | 71 | 114 | 1 | 9 | 15 | 5461 | 5609 | 5267 | 1250 | -169 | -53 | -11 | -2 | -2 | -18 | 499 | 28 | 163 | 163 | 163 | 5 | 5 | 5
1124 | Offshore Wind Connection South Britanny | TOOT | 1 | 3 | 0 | 58 | 12 | 13 | 12 | 69 | 72 | 67 | -109 | -105 | -114 | 13 | 1 | 14 | 22 | 0 | 2 | 3 | 1065 | 1098 | 1028 | 250 | -31 | -10 | -2 | 0 | 0 | -4 | 87 | 5 | 33 | 33 | 33 | 1 | 1 | 1
1125 | Offshore Wind Connection Occitanie | TOOT | 0 | 2 | 0 | 60 | 12 | 13 | 12 | 67 | 69 | 66 | -110 | -105 | -114 | 12 | 1 | 14 | 22 | 0 | 2 | 2 | 1033 | 1068 | 1002 | 250 | -34 | -11 | 0 | 0 | 0 | -4 | 9 | 2 | 33 | 33 | 33 | 1 | 1 | 1
1126 | Offshore Wind Connection PACA | TOOT | 0 | 1 | 0 | 59 | 12 | 13 | 12 | 67 | 69 | 65 | -109 | -105 | -114 | 2 | 1 | 14 | 22 | 0 | 0 | 0 | 1028 | 1068 | 987 | 250 | -28 | -10 | -2 | 0 | 0 | 3 | -69 | -2 | 33 | 33 | 33 | 1 | 1 | 1
1127 | Offshore Wind Connection South Atlantic Oléron 1 | TOOT | 13 | 14 | 12 | 261 | 61 | 63 | 59 | 316 | 320 | 312 | -540 | -523 | -557 | 105 | 7 | 67 | 109 | 1 | 13 | 21 | 4876 | 4894 | 4858 | 1250 | -174 | -52 | -18 | -2 | -2 | -18 | 617 | 36 | 163 | 163 | 163 | 5 | 5 | 5
1134 | GiLA | PINT | 79 | 79 | 79 |  | 17 | 17 | 17 | 71 | 71 | 71 | -152 | -152 | -152 | 63 | 2 | 19 | 31 | 1 | 8 | 13 | 1398 | 1398 | 1398 |  | -54 | -17 | -2 | 0 | 0 | -6 | 517 | 25
1138 | 400 kV OHL Suceava (RO) - Balti (MD) | TOOT | 12 | 18 | 8 |  | 10 | 15 | 6 | 3 | 3 | 2 | -85 | -50 | -135 | 4 | 1 | 11 | 17 | 0 | 1 | 1 | 43 | 49 | 35 |  | -22 | -4 | -10 | 0 | -1 | -1 | 309 | 8 | 106 | 106 | 106 | 2 | 2 | 2
1139 | 380-kV Westtirol (AT) – Zell/Ziller (AT) | PINT | 37 | 47 | 25 | 143 | 56 | 61 | 51 | 168 | 169 | 168 | -497 | -450 | -537 | -63 | 6 | 62 | 100 | -1 | -8 | -13 | 2587 | 2610 | 2564 | 1600 | -193 | -52 | -38 | -2 | -3 | -18 | 334 | 21 | 8 | 8 | 8 | 0 | 0 | 0
1140 | 380-kV St. Peter (AT) - Dürnrohr (AT) | PINT | 39 | 41 | 37 | 124 | 51 | 54 | 50 | 161 | 164 | 160 | -453 | -437 | -474 | -39 | 6 | 56 | 91 | 0 | -5 | -8 | 2482 | 2514 | 2435 | 1500 | -164 | -47 | -19 | -2 | -2 | -17 | 242 | 14 | 47 | 47 | 47 | 1 | 1 | 1
1145 | 380-kV Obersielach (AT) - Hessenberg (AT) | TOOT | 8 | 11 | 5 | 200 | 58 | 61 | 56 | 215 | 218 | 213 | -512 | -497 | -534 | 12 | 6 | 64 | 103 | 0 | 1 | 2 | 3304 | 3343 | 3241 | 2000 | -189 | -54 | -27 | -2 | -3 | -19 | 33 | -1 | 9 | 9 | 9 | 0 | 0 | 0
1153 | PST romands | TOOT | 69 | 71 | 66 |  | 48 | 55 | 42 | 5 | 8 | 3 | -427 | -373 | -488 | 93 | 5 | 53 | 86 | 1 | 12 | 19 | 80 | 124 | 47 |  | -207 | -53 | -35 | -3 | -3 | -19 | 586 | 30 | 662 | 662 | 662 | 23 | 23 | 23
1155 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT) | TOOT | 16 | 19 | 11 | 345 | 101 | 102 | 99 | 364 | 367 | 362 | -889 | -871 | -904 | 50 | 11 | 111 | 179 | 1 | 6 | 10 | 5590 | 5640 | 5509 | 2000 | -319 | -91 | -47 | -4 | -5 | -32 | -163 | -14 | 9 | 9 | 9 | 0 | 0 | 0
1156 | 380-kV Greater Vienna (AT) - Hessenberg (AT) | TOOT | 12 | 17 | 6 | 273 | 80 | 82 | 78 | 289 | 293 | 287 | -707 | -684 | -720 | 24 | 9 | 88 | 143 | 0 | 3 | 5 | 4445 | 4494 | 4375 | 2500 | -249 | -73 | -31 | -3 | -3 | -26 | -36 | -5 | 9 | 9 | 9 | 0 | 0 | 0
1157 | HG North Tyrrhenian Corridor | TOOT | 57 | 60 | 53 |  | 20 | 27 | 15 | 36 | 37 | 35 | -176 | -130 | -241 | 135 | 2 | 22 | 36 | 2 | 17 | 27 | 553 | 567 | 546 |  | -56 | -13 | -14 | -1 | -1 | -5 | 609 | 38 | 2249 | 2249 | 2249 | 0 | 0 | 0
1158 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT) | PINT | 8 | 11 | 5 | 200 | 58 | 61 | 56 | 215 | 218 | 213 | -512 | -497 | -534 | 36 | 6 | 64 | 103 | 0 | 4 | 7 | 3304 | 3343 | 3241 | 2000 | -189 | -54 | -27 | -2 | -3 | -19 | -129 | -10 | 8 | 8 | 8 | 0 | 0 | 0
1159 | 220-kV Bisamberg (AT) – Wien Südost (AT) | TOOT | 4 | 7 | 0 | 24 | 8 | 10 | 6 | 32 | 35 | 28 | -66 | -53 | -85 | 1 | 1 | 8 | 13 | 0 | 0 | 0 | 492 | 539 | 433 | 500 | -26 | -8 | -3 | 0 | 0 | -3 | 9 | 0 | 5 | 5 | 5 | 0 | 0 | 0
1161 | Offshore Wind Connection South Atlantic Oléron 2 | TOOT | 23 | 23 | 21 | 266 | 62 | 63 | 60 | 337 | 344 | 330 | -543 | -525 | -555 | 123 | 7 | 68 | 110 | 2 | 15 | 25 | 5184 | 5274 | 5033 | 1200 | -160 | -49 | -12 | -2 | -2 | -17 | 705 | 41 | 156 | 156 | 156 | 5 | 5 | 5
1162 | Offshore Wind Connection Fécamp-Grand Large 1 | TOOT | 43 | 49 | 39 | 438 | 103 | 105 | 98 | 564 | 575 | 554 | -906 | -868 | -927 | 96 | 11 | 113 | 183 | 1 | 12 | 19 | 8660 | 8810 | 8443 | 2000 | -277 | -84 | -24 | -3 | -3 | -29 | 477 | 31 | 260 | 260 | 260 | 9 | 9 | 9
1163 | Offshore Wind Connection Fécamp-Grand Large 2 | TOOT | 43 | 49 | 39 | 438 | 103 | 105 | 98 | 564 | 575 | 554 | -906 | -868 | -927 | 90 | 11 | 113 | 183 | 1 | 11 | 18 | 8660 | 8810 | 8443 | 2000 | -277 | -84 | -24 | -3 | -3 | -29 | 477 | 31 | 261 | 261 | 261 | 9 | 9 | 9
1164 | Offshore Wind Connection Golfe de Lion Centre | TOOT | 43 | 49 | 39 | 438 | 103 | 105 | 98 | 564 | 575 | 554 | -906 | -868 | -927 | 59 | 11 | 113 | 183 | 1 | 7 | 12 | 8660 | 8810 | 8443 | 2000 | -277 | -84 | -24 | -3 | -3 | -29 | -131 | 6 | 261 | 261 | 261 | 9 | 9 | 9
1165 | Offshore Wind Connection Golfe de Gascogne Sud | TOOT | 23 | 23 | 21 | 266 | 62 | 63 | 60 | 337 | 344 | 330 | -543 | -525 | -555 | 86 | 7 | 68 | 110 | 1 | 11 | 17 | 5184 | 5274 | 5033 | 1200 | -160 | -49 | -12 | -2 | -2 | -17 | 594 | 32 | 156 | 156 | 156 | 5 | 5 | 5
1166 | HG Adriatic Corridor | PINT | 40 | 45 | 33 |  | 17 | 21 | 12 | 28 | 33 | 18 | -148 | -110 | -187 | 94 | 2 | 18 | 30 | 1 | 12 | 19 | 430 | 508 | 281 |  | -63 | -20 | -5 | -1 | -1 | -7 | 374 | 26 | 87 | 87 | 87 | 0 | 0 | 0
1167 | HG Central link | TOOT | 3 | 4 | 1 |  | -1 | 0 | -2 | -2 | 0 | -3 | 9 | 20 | -4 | 24 | 0 | 0 | 0 | 0 | 3 | 5 | -25 | 2 | -43 |  | -7 | -2 | -3 | 0 | 0 | -1 | 131 | 6 | 188 | 188 | 188 | 0 | 0 | 0
1168 | HG Ionian-Tyrrhenian Corridor | TOOT | 5 | 6 | 4 |  | 2 | 4 | 0 | 5 | 7 | 1 | -20 | -3 | -38 | 37 | 0 | 3 | 4 | 0 | 5 | 7 | 72 | 108 | 10 |  | -20 | -4 | -7 | 0 | 0 | -1 | 132 | 9 | 1 | 1 | 1 | 0 | 0 | 0
1169 | SAPEI 2 | PINT | 22 | 24 | 19 |  | 14 | 16 | 11 | 8 | 11 | 4 | -120 | -96 | -145 | 17 | 2 | 15 | 24 | 0 | 2 | 3 | 120 | 176 | 60 |  | -53 | -15 | -7 | -1 | -1 | -5 | 35 | 3 | 15 | 15 | 15 | 0 | 0 | 0
1171 | Interconnection IT-CH | PINT | 97 | 113 | 83 |  | 71 | 74 | 68 | 4 | 7 | 2 | -625 | -599 | -651 | 80 | 8 | 78 | 126 | 1 | 10 | 16 | 61 | 107 | 37 |  | -271 | -86 | -9 | -2 | -2 | -30 | 436 | 27 | 5 | 5 | 5 | 0 | 0 | 0
1182 | EHV S/S Thesprotias and its connection to the 400 kV System | Light PINT | 4 | 7 | 1 |  | -1 | 10 | -14 | 2 | 6 | 0 | 65 | 125 | -13 | 23 | 0 | 0 | 0 | 0 | 3 | 5 | 30 | 90 | -5 |  | -5 | 0 | -5 | 0 | 0 | 0 | 78 | 6 | 0 | 0 | 0 | 0 | 0 | 0
1183 | New interconnection line 400 kV Greece - Albania | Light PINT | 3 | 4 | 0 |  | 0 | 4 | -5 | 2 | 3 | 0 | -1 | 47 | -31 | -14 | 0 | 0 | 0 | 0 | -2 | -3 | 24 | 43 | -1 |  | -1 | -2 | -1 | 0 | 0 | -1 | -44 | -4 | 1 | 1 | 1 | 0 | 0 | 0
1185 | South Coast Offshore Transmission Project | TOOT | 0 | 0 | 0 | 64 | 17 | 20 | 14 | 85 | 93 | 80 | -148 | -123 | -176 | 0 | 2 | 18 | 30 | 0 | 0 | 0 | 1309 | 1439 | 1225 | 800 | -66 | -12 | -51 | -2 | -2 | -4 | 14 | 0 | 30 | 30 | 30 | 1 | 1 | 1
1192 | HansaLink - Phase 1 | PINT | 398 | 627 | 168 | 0 | 212 | 214 | 210 | 306 | 583 | 30 | -1868 | -1849 | -1888 | -44 | 24 | 233 | 377 | -1 | -5 | -9 | 4760 | 9069 | 450 | 2000 | -656 | -180 | -116 | -8 | -11 | -63 | -289 | -16 | 381 | 381 | 381 | 5 | 5 | 5
1193 | HansaLink - Phase 2 | PINT | 59 | 62 | 56 | 0 | 36 | 36 | 36 | -29 | -28 | -30 | -318 | -316 | -319 | -11 | 4 | 40 | 64 | 0 | -1 | -2 | -443 | -425 | -462 | 2000 | -111 | -30 | -22 | -1 | -2 | -11 | -92 | -4 | 379 | 379 | 379 | 5 | 5 | 5
1197 | NU-Link Interconnector | PINT | 83 | 93 | 73 |  | 92 | 96 | 89 | 42 | 47 | 35 | -811 | -783 | -847 | 44 | 10 | 101 | 164 | 1 | 5 | 9 | 645 | 722 | 529 |  | -284 | -79 | -45 | -3 | -4 | -28 | 261 | 14 | 138 | 138 | 138 | 4 | 4 | 4
1200 | Hybrid interconnector Norway-Sørvest F Windfarm-Continent (DK, DE or BE) | PINT | 350 | 364 | 336 |  | 185 | 186 | 185 | 74 | 86 | 61 | -1635 | -1632 | -1639 | 68 | 21 | 204 | 330 | 1 | 9 | 14 | 1147 | 1329 | 965 |  | -551 | -159 | -80 | -6 | -8 | -56 | 623 | 31 | 260 | 260 | 260 | 4 | 4 | 4
1201 | Reinvestment of Skagerrak 1 and 2 | PINT | 138 | 142 | 135 |  | 52 | 52 | 51 | 59 | 66 | 52 | -455 | -448 | -462 | 24 | 6 | 57 | 92 | 0 | 3 | 5 | 914 | 1023 | 805 |  | -159 | -42 | -39 | -2 | -3 | -15 | 569 | 20 | 97 | 97 | 97 | 1 | 1 | 1
1202 | Increased capacity Norway-Finland, Back-to-Back | PINT | 15 | 18 | 12 |  | 3 | 4 | 2 | 11 | 13 | 9 | -30 | -20 | -35 | 1 | 0 | 4 | 6 | 0 | 0 | 0 | 174 | 202 | 147 |  | -19 | -2 | -11 | 0 | -1 | -1 | 63 | 3 | 25 | 25 | 25 | 0 | 0 | 0
1203 | Offshore Wind Connection Bretagne Nord-Ouest | PINT | 16 | 16 | 15 | 250 | 58 | 61 | 56 | 307 | 310 | 304 | -515 | -494 | -535 | 101 | 6 | 64 | 104 | 1 | 13 | 20 | 4735 | 4749 | 4722 | 1200 | -165 | -50 | -14 | -2 | -2 | -17 | 635 | 36 | 157 | 157 | 157 | 5 | 5 | 5
1207 | 380kV Niederstedem-Bertrange/Bofferdange | PINT | 2 | 3 | 1 |  | 1 | 3 | 1 | 0 | 3 | -2 | -11 | -1 | -23 | 42 | 0 | 2 | 3 | 1 | 5 | 8 | -5 | 40 | -34 |  | -4 | -1 | 0 | 0 | 0 | 0 | -13 | 9 | 0 | 0 | 0 | 0 | 0 | 0
1208 | Medlink | PINT | 277 | 288 | 266 | 0 | 632 | 636 | 627 | -48 | -48 | -48 | -5569 | -5528 | -5610 | 188 | 70 | 694 | 1123 | 2 | 23 | 38 | -727 | -727 | -727 | 9016 | -2036 | -637 | -82 | -18 | -18 | -223 | 498 | 45 | 5 | 5 | 5 | 0 | 0 | 0
1209 | Latvia and Lithuania cross-border strengthening project | PINT | 14 | 18 | 10 |  | 1 | 4 | -2 | 21 | 23 | 17 | -9 | 22 | -33 | -3 | 0 | 1 | 2 | 0 | 0 | -1 | 324 | 354 | 267 |  | -6 | -1 | -1 | 0 | 0 | 0 | -34 | -1 | 2 | 2 | 2 | 0 | 0 | 0
1210 | APOLLO-LINK | Light PINT | 534 | 549 | 520 |  | 293 | 307 | 277 | 184 | 200 | 170 | -2580 | -2445 | -2708 |  | 33 | 322 | 520 |  |  |  | 2825 | 3105 | 2600 |  | -1306 | -412 | -38 | -11 | -11 | -144 |  |  | 213 | 213 | 213 | 2 | 2 | 2
1211 | Baltic WindConnector (BWC) | PINT | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1213 | Offshore hybrid Interconnector (DE-NL) | Light PINT | 60 | 65 | 53 |  | 25 | 30 | 21 | 43 | 49 | 39 | -224 | -183 | -264 |  | 3 | 28 | 45 |  |  |  | 659 | 758 | 588 |  | -78 | -22 | -18 | -1 | -1 | -8 |  |  | 32 | 32 | 32 | 0 | 0 | 0
1214 | Hybrid Interconnector Denmark-Germany | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1215 | Xlinks Morocco - Germany | PINT | 850 | 891 | 817 | 0 | 473 | 482 | 468 | -17 | 4 | -39 | -4167 | -4125 | -4247 | 780 | 53 | 519 | 840 | 10 | 97 | 157 | -263 | 68 | -593 | 15200 | -1440 | -397 | -252 | -18 | -23 | -140 | 4268 | 263 | 35 | 35 | 35 | 0 | 0 | 0
1216 | High-Voltage Direct Current Interconnector Project Romania-Hungary | PINT | 15 | 16 | 15 |  | 15 | 15 | 14 | 1 | 2 | -2 | -130 | -123 | -135 | -92 | 2 | 16 | 26 | -1 | -11 | -18 | 11 | 29 | -24 |  | -24 | -12 | -7 | 0 | 0 | -4 | 76 | -40 | 46 | 46 | 46 | 1 | 1 | 1
1217 | Further Development of Offshore Renewables (MOG 3) | Light PINT | 46 | 52 | 41 | 367 | 87 | 91 | 83 | 475 | 476 | 474 | -769 | -735 | -799 |  | 10 | 96 | 155 |  |  |  | 7396 | 7565 | 7217 |  | -258 | -75 | -31 | -3 | -3 | -26 |  |  | 180 | 180 | 180 | 3 | 3 | 3
1218 | Hybrid HVDC Interconnector BE-NL | Light PINT | 3 | 4 | 3 |  | 1 | 2 | 0 | -1 | -1 | -2 | -5 | 4 | -14 |  | 0 | 1 | 2 |  |  |  | -22 | -12 | -32 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1219 | Bofferdange- Bertrange | Light PINT | 12 | 12 | 11 |  | 6 | 8 | 4 | 7 | 11 | 3 | -57 | -36 | -70 |  | 1 | 7 | 12 |  |  |  | 110 | 173 | 42 |  | -23 | -7 | -4 | 0 | 0 | -2 |  |  | 17 | 17 | 17 | 0 | 0 | 0
1220 | Offshore Wind Connection Viana do Castelo | TOOT | 3 | 8 | 0 | 113 | 22 | 23 | 21 | 157 | 161 | 152 | -194 | -186 | -207 | 21 | 2 | 24 | 39 | 0 | 3 | 4 | 2419 | 2468 | 2368 | 2000 | -43 | -7 | -14 | -1 | -1 | -3 | 197 | 11 | 75 | 75 | 75 | 1 | 1 | 1
1221 | Offshore Wind Connection Leixões | TOOT | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 142 | 142 | 142 | 1 | 1 | 1
1222 | Offshore Wind Connection Figueira da Foz (North) | TOOT | 5 | 9 | 0 | 137 | 26 | 27 | 24 | 191 | 196 | 184 | -228 | -210 | -237 | 16 | 3 | 28 | 46 | 0 | 2 | 3 | 2937 | 3004 | 2863 | 2000 | -27 | -7 | -1 | 0 | 0 | -3 | 186 | 9 | 92 | 92 | 92 | 1 | 1 | 1
1223 | Offshore Wind Connection Figueira da Foz (South) | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1224 | Offshore Wind Connection Ericeira | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1225 | Offshore Wind Connection Sines | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1226 | North-South Electricity Corridor in Eastern Europe | Light PINT | 112 | 141 | 91 |  | 52 | 78 | 22 | 26 | 39 | 17 | -456 | -198 | -686 |  | 6 | 57 | 92 |  |  |  | 406 | 596 | 264 |  | -105 | -86 | -168 | -4 | -9 | -30 |  |  | 99 | 99 | 99 | 0 | 0 | 0
1229 | Rhine-Main-Link | PINT | 294 | 379 | 237 |  | 33 | 71 | -48 | 129 | 165 | 107 | -488 | -401 | -425 | -58 | 4 | 36 | 59 | -1 | -7 | -12 | 1 | 2 | 1 |  | -226 | -61 | -28 | -2 | -3 | -22 | -1 | -25 | 0 | 0 | 0 | 0 | 0 | 0
1230 | TuNur Malta | PINT | 0 | 0 | 0 | 0 | 52 | 54 | 50 | -1 | 2 | -4 | -459 | -445 | -473 | 12 | 6 | 57 | 93 | 0 | 2 | 2 | -19 | 25 | -63 | 1400 | -171 | -54 | -8 | -2 | -2 | -19 | 28 | 3 | 0 | 0 | 0 | 0 | 0 | 0
1231 | Green Aegean Interconnector | Light PINT | 704 | 704 | 704 |  | 361 | 371 | 352 | 196 | 196 | 195 | -3187 | -3101 | -3272 |  | 40 | 397 | 642 |  |  |  | 3018 | 3028 | 3008 |  | -1280 | -373 | -162 | -14 | -16 | -131 |  |  | 413 | 413 | 413 | 6 | 6 | 6
1233 | Laufenburg - Beznau - Breite | Light PINT | 95 | 104 | 83 |  | 43 | 51 | 35 | 81 | 87 | 73 | -380 | -308 | -447 |  | 5 | 47 | 77 |  |  |  | 1242 | 1352 | 1104 |  | -165 | -51 | -15 | -2 | -2 | -18 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1234 | 220-kV Reitdorf (AT) - Weißenbach (AT) | TOOT | 0 | 3 | 0 | 46 | 13 | 14 | 11 | 47 | 49 | 46 | -110 | -93 | -125 | -8 | 1 | 14 | 22 | 0 | -1 | -2 | 726 | 767 | 705 | 500 | -33 | -11 | -1 | 0 | 0 | -4 | -58 | -3 | 3 | 3 | 3 | 0 | 0 | 0
1235 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | PINT | 9 | 13 | 7 |  | 6 | 8 | 4 | 1 | 3 | -3 | -52 | -32 | -74 | 97 | 1 | 6 | 10 | 1 | 12 | 20 | 13 | 47 | -43 |  | -18 | -7 | -7 | 0 | 0 | -3 | 362 | 27 | 0 | 0 | 0 | 0 | 0 | 0
1236 | Power-to-Gas for Austria (P2G4A) | PINT | 2 | 3 | 1 |  | 1 | 3 | 0 | 1 | 2 | 0 | -10 | -1 | -28 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 13 | 23 | -1 |  | -9 | -2 | -4 | 0 | 0 | -1 | 1 | 0
1239 | Interconnection Ukraine-Slovak Republic | Light PINT | 23 | 27 | 21 |  | 13 | 16 | 10 | 3 | 4 | 2 | -115 | -91 | -138 |  | 1 | 14 | 23 |  |  |  | 47 | 65 | 24 |  | -232 | -16 | -195 | -7 | -13 | -6
1240 | Interconnection Ukraine-Romania | Light PINT | 27 | 27 | 26 |  | 22 | 29 | 17 | 2 | 3 | 2 | -190 | -154 | -256 |  | 2 | 24 | 38 |  |  |  | 30 | 40 | 23 |  | -435 | -29 | -378 | -14 | -25 | -11

## 2040NT-ENTSO-E
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 49 | 68 | 29 | 43 | 14 | 16 | 12 | 196 | 238 | 154 | -95 | -80 | -108 | 4 | 18 | 46 | 49 | 1 | 2 | 2 | 3039 | 3718 | 2338 | 1154 | -25 | -7 | -3 | 0 | 0 | -2 | 346 | 8 | 2906 | 2906 | 2906 | 27 | 27 | 27
4 | Interconnection Portugal-Spain | TOOT | 45 | 50 | 40 |  | 16 | 16 | 16 | 31 | 66 | 6 | -109 | -107 | -111 | 4 | 21 | 52 | 56 | 1 | 2 | 2 | 480 | 1025 | 86 |  | -21 | -7 | -2 | 0 | 0 | -2 | 56 | 8 | 93 | 93 | 93 | 1 | 1 | 1
16 | Biscay Gulf | TOOT | 764 | 769 | 760 |  | 53 | 55 | 51 | 512 | 513 | 510 | -361 | -347 | -372 | 29 | 69 | 174 | 186 | 5 | 14 | 15 | 8103 | 8558 | 7768 |  | -195 | -46 | -45 | -3 | -4 | -17 | 3409 | 98 | 3925 | 3925 | 3925 | 129 | 129 | 129
28 | Italy-Montenegro | TOOT | 93 | 97 | 88 |  | 39 | 41 | 37 | 35 | 44 | 30 | -265 | -254 | -281 | 0 | 51 | 127 | 136 | 0 | 0 | 0 | 540 | 677 | 461 |  | -74 | -25 | -2 | 0 | 0 | -9 | 228 | 10 | 148 | 148 | 148 | 2 | 2 | 2
29 | Italy-Tunisia | TOOT | 133 | 136 | 130 |  | -69 | -62 | -74 | 42 | 48 | 37 | 469 | 504 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654 | 750 | 582 |  | -175 | -53 | -10 | -2 | -2 | -19 | -198 | -16 | 152 | 152 | 152 | 2 | 2 | 2
33 | Central Northern Italy | TOOT | 43 | 49 | 34 |  | 11 | 12 | 9 | 16 | 22 | 13 | -73 | -61 | -82 | 3 | 14 | 35 | 38 | 1 | 1 | 2 | 230 | 334 | 148 |  | -51 | -10 | -13 | -1 | -1 | -4 | 63 | -5 | 243 | 243 | 243 | 3 | 3 | 3
35 | CZ Southwest-east corridor | TOOT | 144 | 157 | 129 |  | 88 | 92 | 83 | 57 | 62 | 54 | -601 | -567 | -624 | 7 | 115 | 289 | 309 | 1 | 3 | 3 | 880 | 968 | 816 |  | -252 | -77 | -19 | -2 | -3 | -27 | 424 | 21 | 290 | 290 | 290 | 1 | 1 | 1
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 46 | 56 | 40 |  | 2 | 3 | 0 | 17 | 21 | 12 | -15 | -1 | -23 |  | 3 | 7 | 8 |  |  |  | 267 | 334 | 180 |  | -8 | -1 | -6 | 0 | 0 | 0 |  |  | 104 | 104 | 104 | 2 | 2 | 2
47 | Westtirol (AT) - Vöhringen (DE) | TOOT | 91 | 91 | 90 |  | 18 | 22 | 15 | 46 | 48 | 44 | -125 | -99 | -152 | -8 | 24 | 60 | 65 | -1 | -4 | -4 | 712 | 729 | 695 |  | -58 | -18 | -3 | -1 | -1 | -6 | 83 | 0 | 34 | 34 | 34 | 0 | 0 | 0
81 | North South Interconnector | TOOT | 114 | 120 | 107 |  | 50 | 52 | 48 | 51 | 54 | 47 | -343 | -327 | -354 | 0 | 66 | 165 | 176 | 0 | 0 | 0 | 788 | 824 | 737 |  | -138 | -41 | -12 | -1 | -1 | -14 | 32 | 3 | 373 | 373 | 373 | 7 | 7 | 7
85 | Integration of RES in Alentejo | TOOT | 6 | 13 | 2 | 1 | 1 | 3 | 0 | 9 | 15 | 6 | -10 | -2 | -20 | 0 | 2 | 5 | 5 | 0 | 0 | 0 | 147 | 234 | 97 | 553 | -2 | -2 | -5 | 0 | 0 | -1 | -37 | -1 | 0 | 0 | 0 | 0 | 0 | 0
94 | GerPol Improvements | TOOT | 316 | 328 | 303 |  | 123 | 128 | 120 | 56 | 60 | 51 | -838 | -815 | -873 | 10 | 161 | 403 | 431 | 2 | 5 | 5 | 863 | 938 | 796 |  | -437 | -52 | -311 | -12 | -20 | -19 | 385 | 16 | 501 | 501 | 501 | 8 | 8 | 8
107 | Celtic Interconnector | TOOT | 269 | 276 | 266 |  | 27 | 28 | 27 | 198 | 209 | 185 | -185 | -184 | -188 | 14 | 36 | 89 | 95 | 3 | 6 | 7 | 3065 | 3262 | 2890 |  | -69 | -16 | -14 | -1 | -1 | -6 | 1096 | 45 | 1276 | 1276 | 1276 | 42 | 42 | 42
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 81 | 91 | 72 |  | 8 | 10 | 7 | 71 | 79 | 63 | -58 | -50 | -65 | 0 | 11 | 28 | 30 | 0 | 0 | 0 | 1101 | 1223 | 997 |  | -10 | -3 | -1 | 0 | 0 | -1 | 60 | 4 | 700 | 700 | 700 | 9 | 9 | 9
120 | Princess Elisabeth Island (MOG 2) | TOOT | 333 | 339 | 327 | 523 | 84 | 90 | 80 | 741 | 752 | 732 | -571 | -546 | -613 | 23 | 110 | 275 | 294 | 4 | 11 | 12 | 11480 | 11771 | 11261 | 3500 | -310 | -62 | -94 | -5 | -7 | -23 | 296 | 26 | 1936 | 1936 | 1936 | 22 | 22 | 22
121 | Nautilus: multi-purpose interconnector Belgium - UK | TOOT | 166 | 182 | 146 |  | 35 | 36 | 33 | -5 | 11 | -18 | -235 | -225 | -247 | 13 | 45 | 113 | 121 | 3 | 6 | 7 | -81 | 163 | -279 |  | -155 | -28 | -50 | -3 | -3 | -10 | 87 | 8 | 450 | 450 | 450 | 9 | 9 | 9
124 | Ekhyddan-Nybro-Hemsjö | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 55 | 57 | 53 |  | 1 | 3 | -1 | -6 | -2 | -10 | -10 | 4 | -22 | 12 | 2 | 5 | 5 | 2 | 6 | 6 | -89 | -23 | -150 |  | -39 | -5 | -26 | -1 | -1 | -2 | 154 | 13 | 345 | 345 | 345 | 0 | 0 | 0
127 | Central Southern Italy | TOOT | 16 | 26 | 11 |  | 7 | 9 | 5 | 2 | 6 | -1 | -45 | -36 | -60 | 12 | 9 | 21 | 23 | 2 | 6 | 6 | 33 | 86 | -22 |  | -21 | -7 | 0 | 0 | 0 | -3 | 146 | 7 | 94 | 94 | 94 | 1 | 1 | 1
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 519 | 655 | 413 |  | 30 | 38 | 23 | 192 | 238 | 158 | -204 | -159 | -259 | 3 | 39 | 98 | 105 | 1 | 2 | 2 | 2 | 2 | 2 |  | -71 | -22 | -2 | -1 | -1 | -8 | 241 | 10 | 0 | 0 | 0 | 0 | 0 | 0
132 | HVDC Line A-North | TOOT | 1640 | 1900 | 1431 |  | 99 | 121 | 81 | 620 | 749 | 519 | -676 | -549 | -826 | 46 | 130 | 325 | 348 | 9 | 22 | 23 | 6 | 7 | 5 |  | -234 | -74 | -7 | -2 | -2 | -26 | 988 | 55 | 0 | 0 | 0 | 0 | 0 | 0
138 | Black Sea Corridor | TOOT | 19 | 20 | 18 |  | 8 | 11 | 5 | 2 | 7 | -1 | -55 | -36 | -74 | 2 | 10 | 26 | 28 | 0 | 1 | 1 | 24 | 110 | -22 |  | -24 | -9 | -1 | 0 | 0 | -3 | -4 | -3 | 405 | 405 | 405 | 5 | 5 | 5
144 | Mid Continental East corridor | TOOT | 29 | 35 | 24 |  | 11 | 14 | 9 | 6 | 13 | -2 | -75 | -63 | -92 | 2 | 14 | 36 | 39 | 0 | 1 | 1 | 89 | 200 | -31 |  | -31 | -10 | -4 | 0 | 0 | -3 | -10 | -2 | 634 | 634 | 634 | 7 | 7 | 7
150 | Italy-Slovenia | TOOT | 32 | 42 | 21 |  | 23 | 24 | 21 | 7 | 11 | 1 | -155 | -140 | -163 | 5 | 30 | 75 | 80 | 1 | 2 | 3 | 102 | 167 | 21 |  | -62 | -20 | -1 | 0 | 0 | -7 | 142 | 10 | 205 | 205 | 205 | 3 | 3 | 3
153 | France-Alderney-Britain | TOOT | 113 | 120 | 103 |  | 35 | 36 | 34 | 21 | 32 | 12 | -238 | -233 | -246 | 20 | 46 | 115 | 123 | 4 | 9 | 10 | 329 | 492 | 177 |  | -90 | -27 | -9 | -1 | -1 | -9 | 997 | 51 | 2221 | 2221 | 2221 | 75 | 75 | 75
170 | Baltic States Synchronization with Continental Europe | TOOT | 424 | 427 | 418 |  | 222 | 222 | 221 | 174 | 180 | 165 | -1508 | -1505 | -1511 | 0 | 289 | 725 | 776 | 0 | 0 | 0 | 2700 | 2776 | 2581 |  | -536 | -104 | -394 | -14 | -28 | -35 | 155 | -6 | 770 | 770 | 770 | 14 | 14 | 14
174 | Greenconnector | TOOT | 135 | 158 | 111 |  | 83 | 90 | 75 | 12 | 16 | 9 | -568 | -509 | -609 | 7 | 109 | 273 | 292 | 1 | 3 | 3 | 189 | 244 | 132 |  | -245 | -66 | -30 | -3 | -3 | -23 | 540 | 35 | 469 | 469 | 469 | 6 | 6 | 6
176 | Hansa PowerBridge I | TOOT | 158 | 160 | 157 |  | 9 | 13 | 6 | 52 | 64 | 40 | -62 | -39 | -88 | -2 | 12 | 30 | 32 | 0 | -1 | -1 | 809 | 991 | 629 |  | -90 | -17 | -93 | -3 | -4 | -4 | -127 | -7 | 614 | 614 | 614 | 8 | 8 | 8
187 | St. Peter (AT) - Pleinting (DE) | TOOT | 449 | 468 | 433 |  | 91 | 106 | 75 | 214 | 224 | 208 | -617 | -511 | -722 | 15 | 119 | 297 | 318 | 3 | 7 | 8 | 3323 | 3501 | 3203 |  | -335 | -87 | -57 | -4 | -5 | -31 | 1577 | 77 | 305 | 305 | 305 | 3 | 3 | 3
200 | CZ Northwest-South corridor | TOOT | 144 | 157 | 129 |  | 88 | 92 | 83 | 57 | 62 | 54 | -601 | -567 | -624 | 1 | 115 | 289 | 309 | 0 | 0 | 0 | 880 | 968 | 816 |  | -252 | -77 | -19 | -2 | -3 | -27 | 273 | 7 | 287 | 287 | 287 | 0 | 0 | 0
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 31 | 34 | 28 |  | 11 | 12 | 8 | 3 | 5 | 0 | -73 | -54 | -85 | 2 | 14 | 35 | 37 | 0 | 1 | 1 | 46 | 86 | 2 |  | -23 | -6 | -4 | 0 | 0 | -2 | 33 | 2 | 167 | 167 | 167 | 1 | 1 | 1
219 | Great Sea Interconnector | TOOT | 571 | 590 | 552 |  | -27 | -26 | -28 | 195 | 199 | 188 | 184 | 189 | 179 | 36 | 0 | 0 | 0 | 7 | 17 | 19 | 3019 | 3107 | 2938 |  | -36 | -11 | -1 | 0 | 0 | -4 | -2356 | -193 | 549 | 549 | 549 | 5 | 5 | 5
225 | 2nd interconnector Belgium - Germany | light PINT | 157 | 162 | 151 |  | 12 | 14 | 10 | 74 | 81 | 63 | -80 | -67 | -93 | 37 | 15 | 39 | 41 | 7 | 18 | 19 | 1142 | 1267 | 962 |  | -59 | -5 | -38 | -1 | -2 | -2 | 901 | 39 | 366 | 366 | 366 | 4 | 4 | 4
227 | Transbalkan Corridor | TOOT | 29 | 40 | 18 |  | 14 | 19 | 11 | 2 | 17 | -12 | -97 | -75 | -130 | -1 | 19 | 47 | 50 | 0 | 0 | 0 | 33 | 254 | -192 |  | -60 | -18 | -9 | -1 | -1 | -6 | -98 | -7 | 501 | 501 | 501 | 0 | 0 | 0
228 | Muhlbach - Eichstetten | TOOT | 55 | 62 | 50 |  | 6 | 7 | 3 | 26 | 34 | 20 | -38 | -23 | -49 | 4 | 7 | 18 | 20 | 1 | 2 | 2 | 407 | 528 | 305 |  | -33 | -5 | -16 | -1 | -1 | -2 | 189 | 10 | 302 | 302 | 302 | 9 | 9 | 9
231 | Beznau - Tiengen | TOOT | 78 | 82 | 74 |  | 24 | 29 | 17 | 44 | 52 | 37 | -161 | -117 | -200 | -15 | 31 | 77 | 83 | -3 | -7 | -8 | 685 | 819 | 574 |  | -87 | -26 | -5 | -1 | -1 | -9 | 73 | -2 | 102 | 102 | 102 | 2 | 2 | 2
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 1511 | 1801 | 1327 |  | 89 | 112 | 73 | 589 | 721 | 505 | -608 | -493 | -764 | 58 | 117 | 292 | 313 | 11 | 28 | 30 | 6 | 7 | 5 |  | -832 | -263 | -25 | -7 | -7 | -92 | 1956 | 100 | 0 | 0 | 0 | 0 | 0 | 0
239 | Fenno-Skan 3 | Light PINT | 59 | 61 | 55 |  | 2 | 3 | 1 | 51 | 52 | 49 | -14 | -6 | -18 |  | 3 | 7 | 7 |  |  |  | 783 | 815 | 750 |  | -26 | 0 | -21 | -1 | -1 | 0 |  |  | 214 | 214 | 214 | 2 | 2 | 2
243 | New 400 kV interconnection line between Serbia and Croatia | Light PINT | 2 | 3 | 1 |  | 0 | 2 | -2 | 5 | 9 | -1 | 0 | 14 | -12 |  | 0 | 0 | 0 |  |  |  | 84 | 151 | -10 |  | 0 | -1 | -2 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
244 | Vigy - Uchtelfangen area | TOOT | 301 | 311 | 292 |  | 23 | 30 | 18 | 107 | 108 | 105 | -160 | -125 | -204 | 46 | 31 | 77 | 82 | 9 | 22 | 24 | 1762 | 1986 | 1604 |  | -137 | -19 | -68 | -3 | -4 | -7 | 1101 | 61 | 1688 | 1688 | 1688 | 45 | 45 | 45
247 | AQUIND Interconnector | TOOT | 191 | 200 | 183 |  | 63 | 64 | 62 | 40 | 43 | 36 | -427 | -423 | -434 | 21 | 82 | 206 | 220 | 4 | 10 | 11 | 621 | 665 | 542 |  | -190 | -47 | -38 | -2 | -3 | -17 | 801 | 45 | 3746 | 3746 | 3746 | 125 | 125 | 125
250 | Merchant line Castasegna (CH) - Mese (IT) | TOOT | 29 | 33 | 24 |  | 18 | 23 | 16 | 5 | 14 | -6 | -125 | -108 | -156 | 2 | 24 | 60 | 64 | 0 | 1 | 1 | 69 | 206 | -101 |  | -43 | -13 | -4 | 0 | -1 | -5 | 27 | 5 | 47 | 47 | 47 | 1 | 1 | 1
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 713 | 814 | 635 |  | 40 | 48 | 32 | 249 | 298 | 215 | -269 | -221 | -329 | 33 | 52 | 130 | 139 | 6 | 16 | 17 | 2 | 3 | 2 |  | -210 | -66 | -6 | -2 | -2 | -23 | 846 | 45 | 0 | 0 | 0 | 0 | 0 | 0
259 | HU-RO | TOOT | 28 | 29 | 26 |  | 9 | 11 | 4 | 3 | 5 | 0 | -58 | -29 | -75 | 4 | 11 | 28 | 30 | 1 | 2 | 2 | 52 | 81 | 1 |  | -33 | -10 | -5 | 0 | -1 | -3 | 201 | 15 | 713 | 713 | 713 | 9 | 9 | 9
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | TOOT | 177 | 187 | 171 |  | 28 | 30 | 24 | 21 | 22 | 21 | -188 | -164 | -206 | 30 | 36 | 90 | 97 | 6 | 14 | 15 | 329 | 336 | 322 |  | -78 | -24 | -11 | -1 | -1 | -8 | 305 | 22 | 859 | 859 | 859 | 33 | 33 | 33
267 | Hansa PowerBridge II | Light PINT | 158 | 160 | 157 |  | 9 | 13 | 6 | 52 | 64 | 40 | -62 | -39 | -88 | -2 | 12 | 30 | 32 | 0 | -1 | -1 | 809 | 991 | 629 |  | -90 | -17 | -93 | -3 | -4 | -4 | -127 | -7 | 614 | 614 | 614 | 8 | 8 | 8
270 | FR-ES project -Aragón-Atlantic Pyrenees | TOOT | 510 | 513 | 509 |  | 33 | 35 | 31 | 370 | 370 | 369 | -225 | -210 | -241 | 16 | 43 | 108 | 116 | 3 | 8 | 8 | 5758 | 5772 | 5744 |  | -124 | -28 | -33 | -2 | -3 | -10 | 1765 | 61 | 2606 | 2606 | 2606 | 86 | 86 | 86
276 | FR-ES project -Navarra-Landes | PINT | 466 | 481 | 446 |  | 28 | 32 | 26 | 340 | 363 | 318 | -191 | -176 | -218 | 26 | 37 | 92 | 98 | 5 | 12 | 13 | 5260 | 5676 | 4839 |  | -170 | -26 | -64 | -3 | -4 | -10 | 2571 | 85 | 1744 | 1744 | 1744 | 57 | 57 | 57
280 | FR-BE: Lonny-Achene-Gramme | TOOT | 125 | 134 | 111 |  | 9 | 12 | 5 | 45 | 54 | 35 | -65 | -37 | -84 | 15 | 12 | 31 | 33 | 3 | 7 | 8 | 696 | 840 | 538 |  | -74 | -4 | -42 | -2 | -2 | -2 | 475 | 25 | 1176 | 1176 | 1176 | 39 | 39 | 39
283 | TuNur Italy | PINT | 11 | 14 | 9 |  | 178 | 189 | 170 | -69 | -61 | -80 | -1212 | -1155 | -1285 | 0 | 233 | 583 | 624 | 0 | 0 | 0 | -1063 | -952 | -1226 | 5000 | -465 | -141 | -26 | -4 | -5 | -50 | -73 | 0 | 15 | 15 | 15 | 0 | 0 | 0
285 | GridLink | TOOT | 113 | 120 | 103 |  | 35 | 36 | 34 | 21 | 32 | 12 | -238 | -233 | -246 | 19 | 46 | 115 | 123 | 4 | 9 | 10 | 329 | 492 | 177 |  | -90 | -27 | -9 | -1 | -1 | -9 | 498 | 30 | 2220 | 2220 | 2220 | 75 | 75 | 75
297 | BRABO III | TOOT | 43 | 46 | 40 |  | 7 | 9 | 5 | 15 | 21 | 10 | -46 | -35 | -62 | 7 | 9 | 22 | 24 | 1 | 3 | 3 | 232 | 324 | 158 |  | -6 | -5 | -12 | 0 | 0 | -2 | 169 | 8 | 0 | 0 | 0 | 0 | 0 | 0
299 | SACOI 3 | TOOT | 167 | 181 | 147 |  | 90 | 94 | 82 | 12 | 18 | 4 | -610 | -556 | -637 | 2 | 117 | 293 | 314 | 0 | 1 | 1 | 182 | 284 | 58 |  | -2053 | -4 | -1379 | -53 | -74 | -18 | -70 | -7 | 354 | 354 | 354 | 9 | 9 | 9
309 | NeuConnect | TOOT | 186 | 189 | 184 |  | 47 | 53 | 42 | 45 | 65 | 23 | -319 | -285 | -364 | 28 | 61 | 154 | 164 | 5 | 14 | 15 | 695 | 1005 | 352 |  | -216 | -39 | -82 | -4 | -6 | -14 | 513 | 33 | 1820 | 1820 | 1820 | 21 | 21 | 21
312 | St. Peter (AT) - Tauern (AT) | TOOT | 342 | 352 | 333 |  | 69 | 82 | 56 | 162 | 162 | 162 | -472 | -383 | -556 | -32 | 91 | 227 | 243 | -6 | -15 | -16 | 2599 | 2793 | 2469 |  | -253 | -68 | -38 | -3 | -4 | -24 | -233 | -17 | 215 | 215 | 215 | 2 | 2 | 2
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 229 | 237 | 222 |  | 45 | 52 | 37 | 110 | 110 | 109 | -304 | -250 | -355 | 1 | 58 | 146 | 157 | 0 | 1 | 1 | 1697 | 1717 | 1677 |  | -162 | -44 | -24 | -2 | -2 | -15 | 364 | 9 | 125 | 125 | 125 | 1 | 1 | 1
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 4 | 5 | 3 |  | 2 | 3 | 1 | -3 | 2 | -9 | -12 | -4 | -21 | 1 | 2 | 6 | 6 | 0 | 1 | 1 | -54 | 32 | -136 |  | -3 | -1 | -5 | 0 | 0 | 0 | 275 | 20 | 7 | 7 | 7 | 0 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 13 | 19 | 6 |  | 5 | 6 | 4 | -2 | -2 | -3 | -31 | -24 | -42 | 2 | 6 | 15 | 16 | 0 | 1 | 1 | -37 | -28 | -47 |  | -3 | -5 | -9 | 0 | 0 | -2 | 285 | 20 | 22 | 22 | 22 | 0 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | TOOT | 183 | 195 | 168 |  | 82 | 88 | 72 | 16 | 19 | 15 | -558 | -490 | -600 | 9 | 107 | 268 | 287 | 2 | 4 | 5 | 254 | 298 | 227 |  | -227 | -56 | -41 | -3 | -3 | -20 | 191 | 11 | 920 | 920 | 920 | 9 | 9 | 9
328 | Interconnector DE-LUX | TOOT | 8 | 13 | 2 |  | 1 | 2 | 0 | 4 | 10 | -1 | -10 | 0 | -16 | -17 | 2 | 5 | 5 | -3 | -8 | -9 | 63 | 159 | -8 |  | -8 | -1 | -3 | 0 | 0 | 0 | -187 | -11 | 0 | 0 | 0 | 0 | 0 | 0
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 283 | 297 | 269 |  | 101 | 106 | 96 | 221 | 231 | 209 | -1692 | -1777 | -1595 | -11 | 574 | 1063 | 1120 | -2 | -5 | -6 | 4688 | 4435 | 4922 | 0 | -1536 | -177 | -74 | -122 | -79 | -53 | -336 | -34 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | TOOT | 81 | 86 | 74 |  | 0 | 2 | -3 | -1 | 2 | -6 | 1 | 21 | -16 | 8 | 0 | 0 | 0 | 2 | 4 | 4 | -15 | 28 | -99 |  | -29 | -2 | -27 | -1 | -2 | 0 | 72 | 7 | 641 | 641 | 641 | 1 | 1 | 1
335 | North Sea Wind Power Hub | Light PINT | 1514 | 1534 | 1498 | 1493 | 223 | 245 | 207 | 2942 | 2948 | 2934 | -1518 | -1409 | -1667 |  | 291 | 730 | 782 |  |  |  | 45890 | 45895 | 45886 | 14000 | -907 | -146 | -404 | -18 | -26 | -54 |  |  | 3397 | 3397 | 3397 | 42 | 42 | 42
338 | Adriatic HVDC link | TOOT | 105 | 117 | 98 |  | 32 | 34 | 29 | 34 | 36 | 32 | -216 | -197 | -232 | 28 | 42 | 104 | 111 | 5 | 13 | 14 | 524 | 561 | 488 |  | -89 | -32 | -4 | -1 | -1 | -11 | 338 | 13 | 669 | 669 | 669 | 9 | 9 | 9
339 | Tyrrhenian link | TOOT | 81 | 85 | 76 |  | 36 | 39 | 31 | 24 | 35 | 15 | -242 | -209 | -266 | 12 | 46 | 116 | 125 | 2 | 6 | 6 | 278 | 329 | 239 |  | -103 | -33 | -2 | -1 | -1 | -12 | 374 | 10 | 440 | 440 | 440 | 8 | 8 | 8
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 322 | 352 | 298 |  | 115 | 126 | 107 | 251 | 274 | 232 | -2907 | -3193 | -2680 | -11 | 986 | 1826 | 1925 | -2 | -5 | -6 | 4614 | 4282 | 5070 | 0 | -3069 | -252 | -2149 | -190 | -241 | -81 | -595 | -48 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | TOOT | 14 | 19 | 7 |  | 6 | 7 | 4 | 1 | 8 | -7 | -40 | -31 | -46 | 5 | 8 | 19 | 20 | 1 | 2 | 3 | 9 | 129 | -108 |  | -21 | -6 | -4 | 0 | 0 | -2 | 1211 | 89 | 428 | 428 | 428 | 0 | 0 | 0
342 | Central Balkan Corridor | TOOT | 7 | 11 | 3 |  | 6 | 7 | 6 | 0 | 2 | -4 | -44 | -41 | -48 | 2 | 8 | 21 | 23 | 0 | 1 | 1 | -5 | 26 | -59 |  | -26 | -6 | -5 | 0 | 0 | -2 | 18 | -1 | 322 | 322 | 322 | 4 | 4 | 4
343 | CSE1 New | TOOT | 15 | 23 | 9 |  | 4 | 5 | 3 | 0 | 1 | -2 | -25 | -17 | -32 | 1 | 5 | 12 | 13 | 0 | 1 | 1 | -6 | 18 | -31 |  | -5 | -3 | -4 | 0 | 0 | -1 | 99 | 7 | 36 | 36 | 36 | 0 | 0 | 0
346 | ZuidWest380 NL Oost | TOOT | 15 | 19 | 11 |  | 0 | 1 | -1 | -1 | 0 | -2 | -1 | 7 | -6 | -3 | 0 | 0 | 0 | -1 | -1 | -1 | -15 | 7 | -32 |  | -32 | -1 | -19 | -1 | -1 | -1 | -121 | -6 | 0 | 0 | 0 | 0 | 0 | 0
349 | MaresConnect | TOOT | 71 | 78 | 63 |  | 13 | 16 | 12 | 107 | 112 | 103 | -91 | -82 | -106 | 0 | 18 | 44 | 47 | 0 | 0 | 0 | 1651 | 1741 | 1604 |  | -21 | -3 | -7 | 0 | 0 | -1 | 76 | 1 | 522 | 522 | 522 | 9 | 9 | 9
350 | South Balkan Corridor | TOOT | 36 | 44 | 29 |  | 13 | 16 | 11 | -2 | 0 | -4 | -91 | -78 | -108 | 1 | 18 | 44 | 47 | 0 | 1 | 1 | -34 | 1 | -69 |  | -58 | -23 | -7 | 0 | 0 | -8 | 1216 | 88 | 130 | 130 | 130 | 2 | 2 | 2
375 | Lienz (AT) - Veneto region (IT) 220 kV | TOOT | 106 | 107 | 105 |  | 40 | 44 | 34 | 2 | 5 | -3 | -269 | -233 | -299 | 17 | 52 | 129 | 139 | 3 | 8 | 9 | 22 | 72 | -49 |  | -112 | -27 | -24 | -1 | -2 | -10 | 117 | 9 | 628 | 628 | 628 | 6 | 6 | 6
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | Light PINT | 9 | 14 | 5 |  | 1 | 5 | -4 | 8 | 13 | 3 | -9 | 24 | -33 |  | 2 | 4 | 5 |  |  |  | 126 | 208 | 50 |  | -44 | -8 | -12 | -1 | -1 | -3 |  |  | 2 | 2 | 2 | 0 | 0 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | TOOT | 42 | 46 | 34 |  | 7 | 9 | 6 | 14 | 21 | 11 | -47 | -40 | -62 | 7 | 9 | 23 | 24 | 1 | 3 | 4 | 222 | 324 | 165 |  | -11 | -5 | 0 | 0 | 0 | -2 | 193 | 9 | 0 | 0 | 0 | 0 | 0 | 0
378 | Transformer Gatica | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 339 | 352 | 331 |  | 22 | 23 | 21 | 139 | 146 | 130 | -148 | -142 | -159 | 39 | 28 | 71 | 76 | 8 | 19 | 20 | 1 | 1 | 1 |  | -51 | -16 | -2 | 0 | 0 | -6 | 896 | 51 | 0 | 0 | 0 | 0 | 0 | 0
1039 | SE North-south long-term reinforcements | PINT | 40 | 45 | 35 |  | 4 | 7 | 1 | 2 | 7 | -4 | -26 | -4 | -47 | 6 | 5 | 12 | 13 | 1 | 3 | 3 | 28 | 106 | -71 |  | -35 | -3 | -24 | -1 | -1 | -1 | 131 | 4 | 312 | 312 | 312 | 0 | 0 | 0
1040 | LirIC | TOOT | 84 | 88 | 77 |  | 14 | 18 | 9 | 103 | 111 | 94 | -95 | -62 | -122 | 0 | 18 | 46 | 49 | 0 | 0 | 0 | 1585 | 1713 | 1438 |  | -26 | -6 | -4 | 0 | 0 | -2 | 65 | 1 | 510 | 510 | 510 | 11 | 11 | 11
1041 | GREGY Green Energy Interconnector | TOOT | 322 | 330 | 313 |  | -424 | -421 | -427 | 52 | 60 | 47 | 2885 | 2904 | 2866 | -2 | 0 | 0 | 0 | 0 | -1 | -1 | 800 | 911 | 734 |  | -238 | -64 | -29 | -3 | -3 | -23 | 673 | 45 | 123 | 123 | 123 | 2 | 2 | 2
1046 | Finnish North-South reinforcement | PINT | 156 | 156 | 156 |  | 10 | 10 | 10 | 232 | 232 | 232 | 66 | 66 | 66 | 0 | 13 | 32 | 34 | 0 | 0 | 0 | 3634 | 3634 | 3634 |  | -1 | -1 | -1 | 0 | 0 | 0 | -138 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 61 | 70 | 55 |  | -54 | -53 | -55 | 9 | 9 | 8 | 365 | 371 | 358 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 370 | 127 |  | -38 | -17 | -8 | 0 | 0 | -6 | -4572 | -334 | 83 | 83 | 83 | 1 | 1 | 1
1049 | Cronos Energy Ltd | PINT | 146 | 147 | 146 |  | 40 | 42 | 39 | -18 | -13 | -26 | -274 | -267 | -284 | 9 | 53 | 132 | 141 | 2 | 4 | 5 | -286 | -196 | -410 |  | -151 | -33 | -39 | -2 | -3 | -12 | -100 | 1 | 511 | 511 | 511 | 6 | 6 | 6
1050 | Tarchon Energy Ltd | TOOT | 186 | 189 | 184 |  | 47 | 53 | 42 | 45 | 65 | 23 | -319 | -285 | -364 | 23 | 61 | 154 | 164 | 4 | 11 | 12 | 695 | 1005 | 352 |  | -216 | -39 | -82 | -4 | -6 | -14 | 335 | 21 | 1828 | 1828 | 1828 | 22 | 22 | 22
1052 | Lienz (AT) - Malta (AT) - Obersielach (AT) | TOOT | 475 | 510 | 441 | 164 | 142 | 147 | 137 | 218 | 243 | 192 | -968 | -932 | -1003 | 13 | 186 | 465 | 498 | 2 | 6 | 7 | 3402 | 3792 | 3012 | 2000 | -407 | -105 | -79 | -5 | -7 | -37 | -97 | -6 | 1736 | 1736 | 1736 | 17 | 17 | 17
1054 | 220-kV Westtirol (AT) - Zell/Ziller (AT) | TOOT | 91 | 91 | 90 |  | 18 | 22 | 15 | 45 | 46 | 44 | -126 | -99 | -152 | 15 | 24 | 60 | 65 | 3 | 7 | 8 | 697 | 698 | 695 |  | -58 | -18 | -3 | -1 | -1 | -6 | 391 | 24 | 34 | 34 | 34 | 0 | 0 | 0
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 177 | 184 | 170 |  | -1 | 3 | -6 | 134 | 139 | 124 | 9 | 37 | -22 | 45 | 0 | 0 | 0 | 9 | 22 | 23 | 2165 | 2167 | 2163 |  | -1 | -4 | -7 | 0 | 0 | -1 | 7116 | 532 | 222 | 222 | 222 | 1 | 1 | 1
1058 | HVDC Interconnector DE-CH | Light PINT | 204 | 219 | 184 |  | 24 | 32 | 15 | 69 | 73 | 65 | -166 | -105 | -220 |  | 32 | 80 | 86 |  |  |  | 1072 | 1113 | 1010 |  | -119 | -28 | -27 | -2 | -2 | -10 |  |  | 461 | 461 | 461 | 7 | 7 | 7
1059 | Southern Italy | TOOT | 7 | 8 | 6 |  | 3 | 4 | 1 | 0 | 5 | -5 | -17 | -6 | -24 | 5 | 3 | 8 | 9 | 1 | 2 | 2 | -6 | 75 | -73 |  | -4 | -3 | -3 | 0 | 0 | -1 | 121 | 1 | 96 | 96 | 96 | 1 | 1 | 1
1066 | Bulgaria - Turkey | Light PINT | 84 | 86 | 82 |  | -200 | -189 | -209 | 4 | 7 | -2 | 1358 | 1419 | 1284 |  | 0 | 0 | 0 |  |  |  | 58 | 109 | -38 |  | -545 | -170 | -25 | -5 | -5 | -60 |  |  | 184 | 184 | 184 | 2 | 2 | 2
1067 | New AC 400 kV interconnection line Greece - Turkey | Light PINT | 36 | 53 | 19 |  | -92 | -81 | -104 | 6 | 7 | 5 | 626 | 707 | 549 |  | 0 | 0 | 0 |  |  |  | 91 | 105 | 76 |  | -158 | -51 | -3 | -1 | -1 | -18 |  |  | 138 | 138 | 138 | 2 | 2 | 2
1068 | LaSGo Link | PINT | 74 | 81 | 65 |  | 8 | 10 | 7 | 75 | 80 | 71 | -57 | -46 | -71 | 2 | 11 | 28 | 29 | 0 | 1 | 1 | 1168 | 1218 | 1123 |  | -145 | -4 | -94 | -4 | -5 | -2 | 155 | 8 | 65 | 65 | 65 | 0 | 0 | 0
1074 | Pannonian Corridor | TOOT | 14 | 16 | 11 |  | 5 | 8 | 0 | -6 | -2 | -8 | -32 | 1 | -53 | 2 | 6 | 15 | 16 | 0 | 1 | 1 | -92 | -35 | -129 |  | -28 | -8 | -6 | 0 | -1 | -3 | 40 | 3 | 308 | 308 | 308 | 4 | 4 | 4
1085 | Malta-Italy Cable Link No.2 | TOOT | 0 | 1 | 0 |  | -24 | -21 | -28 | 15 | 22 | 11 | 166 | 189 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 336 | 167 |  | -62 | -19 | -4 | -1 | -1 | -7 | -45 | -5 | 87 | 87 | 87 | 1 | 1 | 1
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 0 | 6 | 0 | 35 | 5 | 6 | 4 | 47 | 61 | 35 | -35 | -29 | -39 | -1 | 7 | 17 | 18 | 0 | 0 | 0 | 731 | 955 | 544 | 700 | -143 | 0 | -96 | -4 | -5 | -1 | -371 | -5 | 6 | 6 | 6 | 0 | 0 | 0
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | TOOT | 21 | 23 | 19 | 44 | 10 | 14 | 7 | 74 | 75 | 73 | -71 | -45 | -97 | 0 | 14 | 34 | 36 | 0 | 0 | 0 | 1160 | 1173 | 1147 | 1000 | -103 | -1 | -68 | -3 | -4 | -1 | -214 | -5 | 0 | 0 | 0 | 0 | 0 | 0
1092 | TritonLink: offshore hybrid HVDC interconnector Belgium – Denmark | TOOT | 1060 | 1063 | 1057 | 202 | 103 | 106 | 101 | 1170 | 1171 | 1168 | -704 | -690 | -724 | 29 | 135 | 338 | 362 | 6 | 14 | 15 | 17844 | 17895 | 17792 | 10000 | -324 | -58 | -118 | -6 | -8 | -21 | 443 | 32 | 3467 | 3467 | 3467 | 37 | 37 | 37
1094 | Estlink 3 | TOOT | 114 | 119 | 111 |  | 29 | 31 | 26 | 120 | 130 | 113 | -195 | -177 | -214 | -5 | 37 | 94 | 101 | -1 | -2 | -2 | 1783 | 1793 | 1774 |  | -299 | -15 | -173 | -7 | -10 | -8 | 523 | 17 | 760 | 760 | 760 | 10 | 10 | 10
1095 | Aurora line 2 (4th AC Finland-Sweden north) | TOOT | 57 | 61 | 54 |  | 7 | 8 | 6 | 63 | 65 | 62 | -47 | -41 | -56 | 0 | 9 | 22 | 24 | 0 | 0 | 0 | 985 | 1008 | 966 |  | -15 | -3 | -4 | 0 | 0 | -1 | 43 | 3 | 699 | 699 | 699 | 9 | 9 | 9
1096 | Beznau - Mettlen | Light TOOT | 79 | 93 | 67 |  | 27 | 35 | 20 | 51 | 52 | 49 | -187 | -139 | -236 |  | 36 | 90 | 96 |  |  |  | 783 | 814 | 751 |  | -91 | -31 | -1 | -1 | -1 | -11 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1097 | Upgrade to Konti-Skan | PINT | 85 | 96 | 76 |  | 4 | 6 | 3 | 36 | 46 | 32 | -30 | -22 | -39 | 9 | 6 | 14 | 15 | 2 | 5 | 5 | 567 | 715 | 482 |  | -43 | -6 | -17 | -1 | -1 | -2 | 263 | 14 | 105 | 105 | 105 | 2 | 2 | 2
1098 | Offshore Wind LT 2 | TOOT | 7 | 8 | 5 | 46 | 9 | 10 | 9 | 55 | 58 | 52 | -63 | -59 | -65 | 0 | 12 | 30 | 33 | 0 | 0 | 0 | 845 | 904 | 804 | 700 | -65 | -1 | -42 | -2 | -2 | -1 | 104 | 3 | 147 | 147 | 147 | 1 | 1 | 1
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | TOOT | 138 | 150 | 126 |  | 87 | 89 | 84 | 48 | 51 | 43 | -589 | -572 | -608 | 17 | 113 | 283 | 303 | 3 | 8 | 9 | 751 | 793 | 679 |  | -248 | -76 | -18 | -2 | -3 | -27 | 559 | 28 | 289 | 289 | 289 | 0 | 0 | 0
1102 | Mettlen - Ulrichen | Light TOOT | 24 | 30 | 20 |  | 0 | 2 | -2 | 3 | 6 | 1 | -3 | 13 | -15 |  | 1 | 2 | 2 |  |  |  | 53 | 101 | 17 |  | -19 | -1 | -11 | 0 | -1 | -1 |  |  | 221 | 221 | 221 | 0 | 0 | 0
1103 | Bickigen - Chippis | Light TOOT | 58 | 74 | 47 |  | 20 | 24 | 14 | 43 | 50 | 34 | -134 | -97 | -163 |  | 26 | 65 | 69 |  |  |  | 661 | 774 | 519 |  | -55 | -21 | -5 | 0 | 0 | -7 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1104 | Bauler - Roost | TOOT | 3 | 5 | 2 |  | 1 | 2 | 0 | 2 | 6 | -3 | -7 | -2 | -11 | -17 | 1 | 4 | 4 | -3 | -8 | -9 | 29 | 97 | -43 |  | 0 | -1 | -2 | 0 | 0 | 0 | -196 | -12 | 0 | 0 | 0 | 0 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 128 | 129 | 128 |  | -22 | -18 | -26 | -2 | -2 | -2 | 149 | 177 | 119 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | -33 | -24 | -39 |  | -62 | -20 | -1 | 0 | -1 | -7 | -64 | -3 | 633 | 633 | 633 | 9 | 9 | 9
1106 | Bornholm Energy Island (BEI) | TOOT | 179 | 182 | 173 | 399 | 42 | 43 | 39 | 562 | 569 | 556 | -282 | -268 | -295 | -15 | 54 | 136 | 145 | -3 | -7 | -8 | 8699 | 8866 | 8539 | 3000 | -84 | -30 | -4 | -1 | -1 | -10 | -511 | -29 | 805 | 805 | 805 | 10 | 10 | 10
1109 | Basilicata - Campania reinforcements | TOOT | 12 | 18 | 9 |  | 6 | 7 | 5 | 0 | 6 | -8 | -40 | -33 | -45 | 4 | 8 | 19 | 21 | 1 | 2 | 2 | -4 | 86 | -134 |  | -15 | -6 | -1 | 0 | 0 | -2 | -32 | -6 | 94 | 94 | 94 | 1 | 1 | 1
1110 | Sicily - Calabria | TOOT | 6 | 11 | 2 |  | 6 | 14 | 1 | 1 | 5 | -4 | -38 | -5 | -97 | 1 | 7 | 18 | 20 | 0 | 0 | 0 | 15 | 72 | -61 |  | -10 | -2 | -11 | 0 | -1 | -1 | 7 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1112 | GRITA 2 | TOOT | 207 | 222 | 196 |  | 78 | 78 | 77 | 61 | 65 | 56 | -530 | -524 | -533 | 7 | 102 | 255 | 273 | 1 | 4 | 4 | 940 | 1007 | 863 |  | -155 | -50 | 0 | -1 | -1 | -18 | 519 | 36 | 889 | 889 | 889 | 12 | 12 | 12
1121 | 220-kV Hessenberg (AT) - Weißenbach (AT) | TOOT | 0 | 2 | 0 | 69 | 10 | 11 | 9 | 66 | 71 | 58 | -65 | -59 | -77 | 4 | 13 | 31 | 34 | 1 | 2 | 2 | 1015 | 1085 | 911 | 600 | -31 | -9 | -5 | 0 | 0 | -3 | -95 | -2 | 4 | 4 | 4 | 0 | 0 | 0
1122 | Offshore Wind farm connection Centre Manche 1 | TOOT | 44 | 53 | 31 | 243 | 23 | 24 | 20 | 334 | 335 | 333 | -154 | -138 | -164 | 10 | 30 | 74 | 79 | 2 | 5 | 5 | 5264 | 5473 | 5106 | 1050 | -48 | -14 | -4 | 0 | -1 | -5 | 911 | 42 | 261 | 261 | 261 | 9 | 9 | 9
1123 | Offshore Wind farm connection Centre Manche 2 | TOOT | 44 | 53 | 31 | 243 | 23 | 24 | 20 | 334 | 335 | 333 | -154 | -138 | -164 | 8 | 30 | 74 | 79 | 1 | 4 | 4 | 5264 | 5473 | 5106 | 1250 | -48 | -14 | -4 | 0 | -1 | -5 | 662 | 31 | 261 | 261 | 261 | 9 | 9 | 9
1124 | Offshore Wind Connection South Britanny | TOOT | 28 | 29 | 25 | 152 | 14 | 15 | 12 | 205 | 209 | 196 | -94 | -82 | -104 | 7 | 18 | 45 | 49 | 1 | 3 | 4 | 3170 | 3255 | 3074 | 250 | -26 | -7 | -4 | 0 | 0 | -3 | 663 | 27 | 157 | 157 | 157 | 5 | 5 | 5
1125 | Offshore Wind Connection Occitanie | TOOT | 33 | 38 | 25 | 162 | 17 | 18 | 17 | 206 | 211 | 202 | -119 | -114 | -121 | 3 | 23 | 57 | 61 | 1 | 2 | 2 | 3195 | 3286 | 3147 | 250 | -41 | -12 | -6 | 0 | -1 | -4 | 74 | 6 | 156 | 156 | 156 | 5 | 5 | 5
1126 | Offshore Wind Connection PACA | TOOT | 32 | 36 | 28 | 159 | 19 | 20 | 17 | 198 | 203 | 193 | -126 | -118 | -137 | 2 | 24 | 61 | 65 | 0 | 1 | 1 | 3071 | 3163 | 3022 | 250 | -59 | -13 | -15 | -1 | -1 | -5 | -223 | -7 | 157 | 157 | 157 | 5 | 5 | 5
1127 | Offshore Wind Connection South Atlantic Oléron 1 | TOOT | 35 | 37 | 33 | 232 | 22 | 24 | 21 | 298 | 302 | 295 | -152 | -145 | -165 | 6 | 29 | 73 | 78 | 1 | 3 | 3 | 4611 | 4703 | 4519 | 1250 | -53 | -15 | -7 | -1 | -1 | -5 | 622 | 29 | 261 | 261 | 261 | 9 | 9 | 9
1134 | GiLA | PINT | 329 | 329 | 329 |  | 27 | 27 | 27 | 231 | 231 | 231 | -184 | -184 | -184 | 12 | 0 | 0 | 0 | 2 | 6 | 6 | 4522 | 4522 | 4522 |  | -80 | -25 | -2 | -1 | -1 | -9 | 756 | 33 | 0 | 0 | 0 | 0 | 0 | 0
1138 | 400 kV OHL Suceava (RO) - Balti (MD) | TOOT | 28 | 37 | 20 |  | 18 | 24 | 14 | 6 | 16 | -3 | -123 | -94 | -162 | 3 | 24 | 59 | 64 | 0 | 1 | 1 | 84 | 239 | -45 |  | -42 | -16 | -3 | 0 | 0 | -6 | 1618 | 105 | 211 | 211 | 211 | 3 | 3 | 3
1139 | 380-kV Westtirol (AT) – Zell/Ziller (AT) | PINT | 67 | 68 | 66 | 153 | 21 | 24 | 19 | 169 | 175 | 160 | -143 | -129 | -166 | -20 | 28 | 69 | 74 | -4 | -10 | -10 | 2614 | 2678 | 2493 | 1600 | -106 | -18 | -40 | -2 | -3 | -7 | -681 | -39 | 12 | 12 | 12 | 0 | 0 | 0
1140 | 380-kV St. Peter (AT) - Dürnrohr (AT) | PINT | 84 | 85 | 83 | 135 | 31 | 35 | 27 | 189 | 197 | 185 | -209 | -185 | -238 | -8 | 40 | 101 | 108 | -2 | -4 | -4 | 2934 | 3087 | 2833 | 1500 | -118 | -31 | -17 | -1 | -2 | -11 | -293 | -17 | 14 | 14 | 14 | 1 | 1 | 1
1145 | 380-kV Obersielach (AT) - Hessenberg (AT) | TOOT | 82 | 84 | 81 | 154 | 32 | 36 | 28 | 225 | 227 | 222 | -218 | -192 | -245 | -16 | 42 | 105 | 112 | -3 | -8 | -8 | 3466 | 3472 | 3460 | 2000 | -111 | -27 | -23 | -1 | -2 | -10 | -225 | -15 | 12 | 12 | 12 | 0 | 0 | 0
1153 | PST romands | TOOT | 86 | 103 | 74 |  | 42 | 55 | 29 | 17 | 23 | 11 | -286 | -198 | -377 | 4 | 55 | 138 | 147 | 1 | 2 | 2 | 255 | 351 | 171 |  | -158 | -47 | -13 | -2 | -2 | -16 | 727 | 37 | 1338 | 1338 | 1338 | 45 | 45 | 45
1155 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT) | TOOT | 26 | 37 | 17 | 410 | 58 | 67 | 51 | 399 | 408 | 393 | -396 | -350 | -453 | 3 | 76 | 190 | 204 | 0 | 1 | 1 | 6177 | 6355 | 6027 | 2000 | -194 | -51 | -33 | -2 | -3 | -18 | -132 | -6 | 12 | 12 | 12 | 0 | 0 | 0
1156 | 380-kV Greater Vienna (AT) - Hessenberg (AT) | TOOT | 29 | 30 | 28 | 319 | 46 | 54 | 39 | 314 | 320 | 310 | -310 | -268 | -368 | -8 | 60 | 149 | 160 | -2 | -4 | -4 | 4863 | 4979 | 4718 | 2500 | -155 | -40 | -28 | -2 | -3 | -14 | -213 | -12 | 12 | 12 | 12 | 0 | 0 | 0
1157 | HG North Tyrrhenian Corridor | TOOT | 266 | 269 | 264 |  | 82 | 84 | 78 | 88 | 91 | 85 | -556 | -530 | -571 | 51 | 107 | 267 | 286 | 10 | 25 | 26 | 1326 | 1589 | 1075 |  | -316 | -91 | -34 | -3 | -4 | -32 | 734 | 48 | 2423 | 2423 | 2423 | 36 | 36 | 36
1158 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT) | PINT | 15 | 24 | 7 | 223 | 28 | 32 | 26 | 223 | 227 | 220 | -192 | -178 | -218 | -1 | 37 | 93 | 99 | 0 | -1 | -1 | 3458 | 3547 | 3396 | 2000 | -115 | -26 | -27 | -2 | -2 | -9 | -191 | -10 | 12 | 12 | 12 | 0 | 0 | 0
1159 | 220-kV Bisamberg (AT) – Wien Südost (AT) | TOOT | 0 | 0 | 0 | 24 | 3 | 3 | 2 | 24 | 30 | 17 | -18 | -16 | -21 | 2 | 3 | 9 | 9 | 0 | 1 | 1 | 371 | 457 | 265 | 500 | -5 | -2 | 0 | 0 | 0 | -1 | -3 | 2 | 6 | 6 | 6 | 0 | 0 | 0
1161 | Offshore Wind Connection South Atlantic Oléron 2 | TOOT | 24 | 25 | 23 | 207 | 19 | 20 | 18 | 262 | 267 | 253 | -132 | -121 | -138 | 11 | 25 | 64 | 68 | 2 | 5 | 5 | 4053 | 4163 | 3964 | 1200 | -60 | -12 | -17 | -1 | -1 | -4 | 900 | 44 | 251 | 251 | 251 | 8 | 8 | 8
1162 | Offshore Wind Connection Fécamp-Grand Large 1 | TOOT | 48 | 53 | 45 | 345 | 32 | 33 | 29 | 440 | 449 | 431 | -217 | -199 | -227 | 2 | 42 | 104 | 112 | 0 | 1 | 1 | 6725 | 6749 | 6701 | 2000 | -88 | -19 | -24 | -1 | -2 | -7 | 454 | 26 | 418 | 418 | 418 | 14 | 14 | 14
1163 | Offshore Wind Connection Fécamp-Grand Large 2 | TOOT | 48 | 53 | 45 | 345 | 32 | 33 | 29 | 440 | 449 | 431 | -217 | -199 | -227 | 2 | 42 | 104 | 112 | 0 | 1 | 1 | 6725 | 6749 | 6701 | 2000 | -88 | -19 | -24 | -1 | -2 | -7 | 454 | 26 | 418 | 418 | 418 | 14 | 14 | 14
1164 | Offshore Wind Connection Golfe de Lion Centre | TOOT | 48 | 53 | 45 | 345 | 32 | 33 | 29 | 440 | 449 | 431 | -217 | -199 | -227 | -3 | 42 | 104 | 112 | -1 | -1 | -2 | 6725 | 6749 | 6701 | 2000 | -88 | -19 | -24 | -1 | -2 | -7 | -649 | -25 | 418 | 418 | 418 | 14 | 14 | 14
1165 | Offshore Wind Connection Golfe de Gascogne Sud | TOOT | 24 | 25 | 23 | 207 | 19 | 20 | 18 | 262 | 267 | 253 | -132 | -121 | -138 | 6 | 25 | 64 | 68 | 1 | 3 | 3 | 4053 | 4163 | 3964 | 1200 | -60 | -12 | -17 | -1 | -1 | -4 | 464 | 23 | 250 | 250 | 250 | 8 | 8 | 8
1166 | HG Adriatic Corridor | PINT | 126 | 132 | 121 |  | 35 | 41 | 29 | 47 | 52 | 40 | -236 | -197 | -277 | 10 | 45 | 114 | 122 | 2 | 5 | 5 | 724 | 809 | 604 |  | -128 | -37 | -12 | -1 | -2 | -13 | 404 | 30 | 33 | 33 | 33 | 0 | 0 | 0
1167 | HG Central link | TOOT | 9 | 12 | 4 |  | 5 | 8 | 3 | 1 | 7 | -4 | -36 | -23 | -54 | 10 | 7 | 17 | 19 | 2 | 5 | 5 | 19 | 103 | -60 |  | -18 | -4 | -4 | 0 | 0 | -1 | 288 | 14 | 318 | 318 | 318 | 4 | 4 | 4
1168 | HG Ionian-Tyrrhenian Corridor | TOOT | 35 | 44 | 31 |  | 11 | 15 | 8 | 8 | 11 | 6 | -76 | -55 | -100 | 10 | 15 | 36 | 39 | 2 | 5 | 5 | 124 | 171 | 66 |  | -32 | -8 | -5 | 0 | 0 | -3 | 187 | 6 | 34 | 34 | 34 | 1 | 1 | 1
1169 | SAPEI 2 | PINT | 19 | 28 | 13 |  | 6 | 7 | 6 | 9 | 18 | 4 | -44 | -42 | -47 | -8 | 8 | 21 | 23 | -1 | -4 | -4 | 56 | 282 | -176 |  | -23 | -5 | -5 | 0 | 0 | -2 | 56 | 6 | 3 | 3 | 3 | 0 | 0 | 0
1171 | Interconnection IT-CH | PINT | 110 | 126 | 95 |  | 65 | 67 | 60 | 11 | 15 | 7 | -441 | -406 | -458 | 3 | 85 | 212 | 227 | 1 | 2 | 2 | 175 | 227 | 108 |  | -156 | -54 | -4 | -1 | -1 | -19 | 342 | 21 | 65 | 65 | 65 | 1 | 1 | 1
1182 | EHV S/S Thesprotias and its connection to the 400 kV System | Light PINT | 9 | 14 | 1 |  | -1 | 1 | -3 | 1 | 5 | -1 | 4 | 19 | -8 |  | 0 | 0 | 0 |  |  |  | 24 | 72 | -14 |  | -17 | -1 | -9 | 0 | 0 | -1 |  |  | 4 | 4 | 4 | 0 | 0 | 0
1183 | New interconnection line 400 kV Greece - Albania | Light PINT | 9 | 14 | 6 |  | 0 | 1 | -2 | 5 | 8 | 2 | 0 | 14 | -8 |  | 0 | 0 | 0 |  |  |  | 74 | 126 | 23 |  | -10 | -1 | -4 | 0 | 0 | -1 |  |  | 1 | 1 | 1 | 0 | 0 | 0
1185 | South Coast Offshore Transmission Project | TOOT | 0 | 0 | 0 | 56 | 7 | 8 | 6 | 66 | 76 | 55 | -44 | -38 | -53 | 0 | 9 | 21 | 23 | 0 | 0 | 0 | 1014 | 1154 | 861 | 800 | -24 | -2 | -14 | -1 | -1 | -1 | 17 | 1 | 55 | 55 | 55 | 1 | 1 | 1
1192 | HansaLink - Phase 1 | PINT | 301 | 319 | 277 |  | 65 | 80 | 45 | 20 | 27 | 14 | -440 | -305 | -547 | -14 | 85 | 212 | 227 | -3 | -7 | -7 | 313 | 415 | 212 | 2000 | -320 | -53 | -134 | -6 | -9 | -20 | -256 | -22 | 2249 | 2249 | 2249 | 28 | 28 | 28
1193 | HansaLink - Phase 2 | PINT | 62 | 66 | 57 |  | 9 | 9 | 8 | -37 | -31 | -45 | -58 | -51 | -63 | 1 | 11 | 28 | 30 | 0 | 1 | 1 | -573 | -482 | -686 | 2000 | -46 | -5 | -22 | -1 | -1 | -2 | -235 | -9 | 193 | 193 | 193 | 23 | 23 | 23
1197 | NU-Link Interconnector | PINT | 102 | 115 | 84 |  | 25 | 28 | 20 | -13 | -5 | -20 | -168 | -136 | -188 | 9 | 32 | 81 | 86 | 2 | 4 | 4 | -206 | -80 | -313 |  | -90 | -20 | -22 | -1 | -2 | -7 | -71 | -3 | 193 | 193 | 193 | 5 | 5 | 5
1200 | Hybrid interconnector Norway-Sørvest F Windfarm-Continent (DK, DE or BE) | PINT | 752 | 755 | 750 |  | 65 | 68 | 62 | 472 | 474 | 470 | -442 | -425 | -460 | 21 | 85 | 213 | 228 | 4 | 10 | 11 | 7411 | 7431 | 7390 |  | -227 | -51 | -63 | -3 | -4 | -18 | 249 | 14 | 868 | 868 | 868 | 11 | 11 | 11
1201 | Reinvestment of Skagerrak 1 and 2 | PINT | 206 | 234 | 180 |  | 17 | 19 | 14 | 131 | 153 | 113 | -113 | -94 | -133 | 1 | 22 | 54 | 58 | 0 | 0 | 0 | 2048 | 2406 | 1718 |  | -90 | -8 | -51 | -2 | -3 | -3 | 208 | 4 | 228 | 228 | 228 | 4 | 4 | 4
1202 | Increased capacity Norway-Finland, Back-to-Back | PINT | 34 | 35 | 32 |  | 3 | 4 | 2 | 24 | 27 | 18 | -20 | -13 | -25 | 0 | 4 | 10 | 10 | 0 | 0 | 0 | 366 | 417 | 274 |  | -17 | -1 | -15 | -1 | -1 | 0 | 156 | 6 | 54 | 54 | 54 | 1 | 1 | 1
1203 | Offshore Wind Connection Bretagne Nord-Ouest | PINT | 38 | 41 | 31 | 215 | 19 | 23 | 16 | 281 | 284 | 276 | -130 | -112 | -157 | 5 | 25 | 63 | 67 | 1 | 2 | 2 | 4351 | 4435 | 4304 | 1200 | -63 | -12 | -19 | -1 | -1 | -4 | 905 | 43 | 251 | 251 | 251 | 8 | 8 | 8
1207 | 380kV Niederstedem-Bertrange/Bofferdange | PINT | 3 | 6 | 1 |  | -1 | 0 | -2 | 1 | 3 | 0 | 8 | 12 | -1 | 14 | 0 | 0 | 0 | 3 | 7 | 7 | 18 | 44 | 3 |  | -13 | -1 | -11 | 0 | -1 | 0 | 191 | 11 | 0 | 0 | 0 | 0 | 0 | 0
1208 | Medlink | PINT | 250 | 253 | 247 |  | 321 | 326 | 316 | -112 | -110 | -114 | -2182 | -2150 | -2215 | 17 | 419 | 1050 | 1124 | 3 | 8 | 9 | -1745 | -1718 | -1773 | 9016 | -901 | -265 | -72 | -9 | -10 | -93 | 511 | 48 | 18 | 18 | 18 | 0 | 0 | 0
1209 | Latvia and Lithuania cross-border strengthening project | PINT | 50 | 51 | 50 |  | 11 | 12 | 11 | 29 | 30 | 28 | -78 | -75 | -81 | 1 | 15 | 38 | 40 | 0 | 0 | 0 | 446 | 471 | 421 |  | -53 | -1 | -38 | -1 | -2 | -1 | -70 | 0 | 265 | 265 | 265 | 3 | 3 | 3
1210 | APOLLO-LINK | Light PINT | 873 | 891 | 846 |  | 228 | 230 | 225 | 469 | 471 | 467 | -1552 | -1530 | -1563 |  | 298 | 746 | 799 |  |  |  | 7224 | 7270 | 7178 |  | -732 | -225 | -35 | -7 | -7 | -79 |  |  | 270 | 270 | 270 | 3 | 3 | 3
1211 | Baltic WindConnector (BWC) | PINT | 572 | 579 | 564 | 142 | 49 | 52 | 46 | 476 | 480 | 472 | -334 | -315 | -352 | 21 | 64 | 160 | 172 | 4 | 10 | 11 | 7353 | 7518 | 7189 | 2000 | -77 | -40 | -11 | 0 | 0 | -13 | 332 | 23 | 1594 | 1594 | 1594 | 21 | 21 | 21
1213 | Offshore hybrid Interconnector (DE-NL) | Light PINT | 153 | 161 | 147 |  | 17 | 19 | 16 | 53 | 53 | 53 | -115 | -106 | -131 |  | 22 | 55 | 59 |  |  |  | 817 | 831 | 803 |  | -95 | -15 | -42 | -2 | -3 | -6 |  |  | 418 | 418 | 418 | 7 | 7 | 7
1214 | Hybrid Interconnector Denmark-Germany | TOOT | 582 | 599 | 557 | 86 | 51 | 53 | 49 | 572 | 572 | 571 | -344 | -334 | -359 | 103 | 66 | 165 | 177 | 20 | 50 | 53 | 8962 | 8982 | 8941 | 2000 | -229 | -34 | -99 | -4 | -6 | -13 | 2353 | 145 | 0 | 0 | 0 | 0 | 0 | 0
1215 | Xlinks Morocco - Germany | PINT | 921 | 923 | 919 |  | 157 | 166 | 147 | -87 | -63 | -116 | -1065 | -998 | -1131 | 228 | 204 | 512 | 549 | 44 | 110 | 118 | -1340 | -991 | -1766 | 15200 | -720 | -101 | -342 | -15 | -21 | -38 | 4054 | 260 | 130 | 130 | 130 | 3 | 3 | 3
1216 | High-Voltage Direct Current Interconnector Project Romania-Hungary | PINT | 32 | 36 | 28 |  | 9 | 12 | 4 | 6 | 12 | 1 | -59 | -26 | -80 | 7 | 11 | 28 | 30 | 1 | 3 | 3 | 98 | 190 | 13 |  | -40 | -10 | -11 | -1 | -1 | -4 | -26 | -2 | 36 | 36 | 36 | 0 | 0 | 0
1217 | Further Development of Offshore Renewables (MOG 3) | Light PINT | 44 | 52 | 38 | 360 | 29 | 30 | 27 | 452 | 456 | 448 | -194 | -181 | -208 |  | 37 | 94 | 100 |  |  |  | 7003 | 7081 | 6937 |  | -83 | -18 | -23 | -1 | -2 | -6 |  |  | 454 | 454 | 454 | 5 | 5 | 5
1218 | Hybrid HVDC Interconnector BE-NL | Light PINT | 53 | 59 | 47 |  | 6 | 7 | 5 | 21 | 26 | 11 | -40 | -34 | -49 |  | 8 | 19 | 21 |  |  |  | 324 | 400 | 172 |  | -48 | -12 | -9 | -1 | -1 | -4 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1219 | Bofferdange- Bertrange | Light PINT | 29 | 31 | 26 |  | 2 | 2 | 1 | 9 | 15 | 5 | -13 | -6 | -16 |  | 2 | 6 | 7 |  |  |  | 133 | 234 | 78 |  | -12 | -2 | -6 | 0 | 0 | -1 |  |  | 81 | 81 | 81 | 1 | 1 | 1
1220 | Offshore Wind Connection Viana do Castelo | TOOT | 6 | 13 | 0 | 45 | 5 | 8 | 4 | 146 | 161 | 124 | -36 | -27 | -51 | 3 | 7 | 18 | 19 | 1 | 1 | 1 | 2257 | 2507 | 1943 | 2000 | 0 | -2 | -5 | 0 | 0 | -1 | 140 | 6 | 243 | 243 | 243 | 2 | 2 | 2
1221 | Offshore Wind Connection Leixões | TOOT | 3 | 8 | 0 | 36 | 5 | 9 | 2 | 107 | 123 | 86 | -33 | -16 | -58 | 0 | 6 | 16 | 17 | 0 | 0 | 0 | 1665 | 1912 | 1347 | 1500 | -4 | -1 | 0 | 0 | 0 | 0 | 134 | 5 | 184 | 184 | 184 | 2 | 2 | 2
1222 | Offshore Wind Connection Figueira da Foz (North) | TOOT | 18 | 25 | 10 | 33 | 5 | 8 | 4 | 146 | 161 | 124 | -36 | -27 | -51 | 1 | 7 | 18 | 19 | 0 | 0 | 1 | 2257 | 2507 | 1943 | 2000 | 0 | -2 | -5 | 0 | 0 | -1 | 121 | 6 | 245 | 245 | 245 | 2 | 2 | 2
1223 | Offshore Wind Connection Figueira da Foz (South) | TOOT | 18 | 25 | 10 | 33 | 5 | 8 | 4 | 146 | 161 | 124 | -36 | -27 | -51 | 1 | 7 | 18 | 19 | 0 | 0 | 1 | 2257 | 2507 | 1943 | 2000 | 0 | -2 | -5 | 0 | 0 | -1 | 133 | 6 | 244 | 244 | 244 | 2 | 2 | 2
1224 | Offshore Wind Connection Ericeira | TOOT | 3 | 4 | 1 | 24 | 4 | 6 | 2 | 76 | 78 | 74 | -26 | -17 | -39 | 1 | 5 | 13 | 14 | 0 | 0 | 0 | 1077 | 1213 | 894 | 1000 | -6 | -4 | -12 | 0 | -1 | -1 | 15 | 3 | 118 | 118 | 118 | 1 | 1 | 1
1225 | Offshore Wind Connection Sines | TOOT | 15 | 20 | 7 | 24 | 5 | 9 | 2 | 107 | 123 | 86 | -33 | -16 | -58 | -1 | 6 | 16 | 17 | 0 | 0 | 0 | 1665 | 1912 | 1347 | 1500 | -4 | -1 | 0 | 0 | 0 | 0 | -63 | 3 | 179 | 179 | 179 | 2 | 2 | 2
1226 | North-South Electricity Corridor in Eastern Europe | Light PINT | 223 | 315 | 160 |  | 65 | 70 | 59 | 35 | 37 | 32 | -439 | -402 | -477 |  | 84 | 211 | 226 |  |  |  | 536 | 570 | 501 |  | -465 | -149 | -13 | -4 | -4 | -52 |  |  | 149 | 149 | 149 | 2 | 2 | 2
1229 | Rhine-Main-Link | PINT | 1653 | 1994 | 1409 |  | 99 | 125 | 79 | 650 | 795 | 547 | -676 | -536 | -852 | 48 | 130 | 325 | 348 | 9 | 23 | 24 | 5 | 8 | 1 |  | -234 | -74 | -7 | -2 | -2 | -26 | 1452 | 69 | 0 | 0 | 0 | 0 | 0 | 0
1230 | TuNur Malta | PINT | 1 | 2 | 0 |  | 36 | 39 | 34 | -9 | 2 | -20 | -244 | -231 | -268 | 1 | 47 | 117 | 125 | 0 | 1 | 1 | -142 | 38 | -306 | 1400 | -97 | -29 | -5 | -1 | -1 | -10 | -8 | 6 | 0 | 0 | 0 | 0 | 0 | 0
1231 | Green Aegean Interconnector | Light PINT | 1124 | 1160 | 1094 |  | 347 | 352 | 343 | 289 | 290 | 288 | -2363 | -2331 | -2394 |  | 454 | 1136 | 1217 |  |  |  | 4483 | 4542 | 4399 |  | -640 | -156 | -141 | -9 | -11 | -56 |  |  | 2687 | 2687 | 2687 | 35 | 35 | 35
1233 | Laufenburg - Beznau - Breite | Light PINT | 132 | 142 | 122 |  | 44 | 53 | 32 | 106 | 113 | 102 | -296 | -217 | -360 |  | 57 | 142 | 153 |  |  |  | 1648 | 1770 | 1550 |  | -134 | -50 | -14 | -1 | 0 | -17 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1234 | 220-kV Reitdorf (AT) - Weißenbach (AT) | TOOT | 3 | 6 | 0 | 51 | 7 | 8 | 6 | 52 | 54 | 50 | -51 | -44 | -56 | 1 | 10 | 24 | 26 | 0 | 1 | 1 | 800 | 850 | 761 | 500 | -22 | -6 | -4 | 0 | 0 | -2 | -59 | -1 | 4 | 4 | 4 | 0 | 0 | 0
1235 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | PINT | 6 | 8 | 3 |  | 2 | 4 | 1 | 0 | 0 | -1 | -16 | -7 | -27 | -1 | 3 | 8 | 8 | 0 | -1 | -1 | -1 | 7 | -10 |  | -25 | -3 | -12 | -1 | -1 | -1 | -442 | -28 | 13 | 13 | 13 | 0 | 0 | 0
1236 | Power-to-Gas for Austria (P2G4A) | PINT | 1 | 2 | 0 |  | 0 | 2 | -1 | 2 | 8 | -4 | -3 | 6 | -13 | 3 | 0 | 1 | 1 | 1 | 1 | 2 | 32 | 125 | -65 |  | -1 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0
1239 | Interconnection Ukraine-Slovak Republic | Light PINT | 54 | 86 | 9 |  | 26 | 49 | -1 | 3 | 7 | 0 | -176 | 8 | -333 |  | 34 | 85 | 91 |  |  |  | 47 | 114 | -5 |  | -232 | -16 | -195 | -7 | -13 | -6
1240 | Interconnection Ukraine-Romania | Light PINT | 115 | 139 | 98 |  | 49 | 50 | 48 | 9 | 17 | -1 | -331 | -323 | -339 |  | 64 | 159 | 170 |  |  |  | 141 | 263 | -15 |  | -435 | -29 | -378 | -14 | -25 | -11

## 2040DE-ENTSO-E
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 61 | 91 | 21 | 130.4 | 35 | 39 | 27 | 238 | 282 | 179 | -236 | -187 | -266 | 1 | 45 | 113 | 121 | 0 | 1 | 1 | 3379 | 3956 | 2554 | 1154 | -65 | -6 | -30 | -1 | -2 | -3 | 346 | 15 | 2259 | 2259 | 2259 | 18 | 18 | 18
4 | Interconnection Portugal-Spain | TOOT | 142 | 146 | 136 |  | 23 | 25 | 21 | 141 | 150 | 130 | -155 | -142 | -170 | 2 | 30 | 74 | 80 | 0 | 1 | 1 | 2008 | 2152 | 1851 |  | -46 | -8 | -17 | -1 | -1 | -3 | 56 | 9 | 606 | 606 | 606 | 4 | 4 | 4
16 | Biscay Gulf | TOOT | 332 | 339 | 324 |  | 74 | 78 | 67 | 212 | 212 | 212 | -502 | -457 | -530 | 36 | 96 | 241 | 258 | 7 | 17 | 18 | 3009 | 3044 | 2975 |  | -167 | -37 | -37 | -2 | -3 | -13 | 3409 | 128 | 3664 | 3664 | 3664 | 55 | 55 | 55
28 | Italy-Montenegro | TOOT | 92 | 96 | 87 |  | 32 | 33 | 30 | 32 | 34 | 30 | -214 | -207 | -228 | 104 | 41 | 103 | 110 | 20 | 50 | 54 | 462 | 479 | 434 |  | -69 | -24 | 0 | 0 | 0 | -8 | 525 | 45 | 319 | 319 | 319 | 0 | 0 | 0
29 | Italy-Tunisia | TOOT | 119 | 147 | 95 |  | -7 | 30 | -33 | 25 | 33 | 20 | 184 | 227 | 122 | -8 | 0 | 0 | 0 | -2 | -4 | -4 | 355 | 466 | 282 |  | -66 | -16 | -15 | -1 | -1 | -6 | -168 | -12 | 99 | 99 | 99 | 2 | 2 | 2
33 | Central Northern Italy | TOOT | 41 | 46 | 35 |  | 10 | 11 | 8 | 18 | 25 | 15 | -57 | -33 | -76 | -3 | 13 | 31 | 34 | -1 | -2 | -2 | 244 | 346 | 183 |  | -45 | -13 | -3 | 0 | -1 | -5 | 63 | -4 | 230 | 230 | 230 | 3 | 3 | 3
35 | CZ Southwest-east corridor | TOOT | 194 | 198 | 192 |  | 54 | 56 | 51 | 63 | 65 | 60 | -364 | -347 | -381 | 24 | 70 | 175 | 188 | 5 | 12 | 13 | 895 | 922 | 854 |  | -226 | -63 | -43 | -3 | -3 | -22 | 424 | 21 | 487 | 487 | 487 | 6 | 6 | 6
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 53 | 57 | 50 |  | 4 | 5 | 3 | 30 | 33 | 26 | -29 | -22 | -37 |  | 5 | 14 | 15 |  |  |  | 423 | 476 | 365 |  | -14 | 0 | -12 | 0 | -1 | 0 |  |  | 727 | 727 | 727 | 9 | 9 | 9
47 | Westtirol (AT) - Vöhringen (DE) | TOOT | 102 | 103 | 101 |  | 8 | 10 | 7 | 41 | 42 | 39 | -52 | -45 | -65 | 6 | 10 | 25 | 27 | 1 | 3 | 3 | 579 | 593 | 561 |  | -32 | -4 | -13 | -1 | -1 | -2 | 83 | -8 | 796 | 796 | 796 | 10 | 10 | 10
81 | North South Interconnector | TOOT | 364 | 373 | 352 |  | 59 | 60 | 56 | 122 | 122 | 122 | -399 | -384 | -408 | 3 | 77 | 192 | 206 | 1 | 2 | 2 | 1736 | 1755 | 1717 |  | -416 | -64 | -152 | -7 | -10 | -24 | 32 | 4 | 330 | 330 | 330 | 3 | 3 | 3
85 | Integration of RES in Alentejo | TOOT | 0 | 1 | 0 | 8 | 0 | 1 | 0 | 8 | 10 | 7 | -2 | 1 | -8 | -1 | 0 | 1 | 1 | 0 | -1 | -1 | 116 | 137 | 98 | 700 | 3 | 0 | 1 | 0 | 0 | 0 | -37 | -2 | 0 | 0 | 0 | 0 | 0 | 0
94 | GerPol Improvements | TOOT | 308 | 310 | 306 |  | 41 | 42 | 40 | 106 | 107 | 103 | -279 | -271 | -288 | 15 | 54 | 134 | 144 | 3 | 7 | 8 | 1505 | 1538 | 1450 |  | -202 | -37 | -96 | -4 | -7 | -13 | 385 | 20 | 1994 | 1994 | 1994 | 26 | 26 | 26
107 | Celtic Interconnector | TOOT | 254 | 256 | 251 |  | 33 | 35 | 32 | 159 | 163 | 155 | -227 | -214 | -239 | 26 | 44 | 109 | 117 | 5 | 12 | 13 | 2266 | 2343 | 2219 |  | -88 | -28 | -6 | -1 | -1 | -10 | 1096 | 54 | 1438 | 1438 | 1438 | 14 | 14 | 14
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 63 | 66 | 59 |  | 4 | 5 | 3 | 44 | 47 | 43 | -30 | -19 | -37 | 2 | 6 | 14 | 15 | 0 | 1 | 1 | 629 | 660 | 610 |  | -49 | -4 | -33 | -1 | -2 | -1 | 60 | 2 | 1169 | 1169 | 1169 | 9 | 9 | 9
120 | Princess Elisabeth Island (MOG 2) | TOOT | 304 | 314 | 295 | 594 | 75 | 76 | 73 | 804 | 833 | 775 | -508 | -498 | -518 | 25 | 98 | 245 | 262 | 5 | 12 | 13 | 11407 | 11700 | 11113 | 3500 | -424 | -51 | -230 | -10 | -15 | -19 | 296 | 28 | 4176 | 4176 | 4176 | 190 | 190 | 190
121 | Nautilus: multi-purpose interconnector Belgium - UK | TOOT | 151 | 159 | 144 |  | 21 | 22 | 20 | 27 | 30 | 24 | -143 | -133 | -150 | 12 | 28 | 69 | 74 | 2 | 6 | 6 | 384 | 419 | 348 |  | -80 | -20 | -10 | -1 | -1 | -7 | 87 | 7 | 837 | 837 | 837 | 54 | 54 | 54
124 | Ekhyddan-Nybro-Hemsjö | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 65 | 82 | 52 |  | 7 | 12 | 4 | 16 | 17 | 15 | -49 | -29 | -80 | 21 | 9 | 24 | 25 | 4 | 10 | 11 | 230 | 251 | 209 |  | -36 | -6 | -19 | -1 | -1 | -2 | 154 | 14 | 81 | 81 | 81 | 0 | 0 | 0
127 | Central Southern Italy | TOOT | 17 | 20 | 15 |  | 3 | 7 | -4 | 3 | 5 | 0 | -37 | -29 | -45 | 18 | 4 | 11 | 11 | 3 | 9 | 9 | 41 | 68 | -5 |  | -29 | -8 | -6 | 0 | 0 | -3 | 146 | 6 | 453 | 453 | 453 | 0 | 0 | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 606 | 699 | 541 |  | 15 | 19 | 13 | 225 | 270 | 195 | -105 | -90 | -128 | 8 | 20 | 50 | 54 | 2 | 4 | 4 | 2 | 3 | 2 |  | -79 | -25 | -2 | -1 | -1 | -9 | 241 | 8 | 0 | 0 | 0 | 0 | 0 | 0
132 | HVDC Line A-North | TOOT | 970 | 1172 | 841 |  | 25 | 32 | 20 | 357 | 452 | 294 | -168 | -139 | -216 | 47 | 32 | 81 | 87 | 9 | 23 | 24 | 4 | 5 | 3 |  | -127 | -40 | -4 | -1 | -1 | -14 | 988 | 57 | 0 | 0 | 0 | 0 | 0 | 0
138 | Black Sea Corridor | TOOT | 9 | 13 | 4 |  | 6 | 9 | 3 | 3 | 8 | -2 | -40 | -24 | -59 | -11 | 8 | 19 | 20 | -2 | -5 | -6 | 35 | 107 | -35 |  | -17 | -6 | -1 | 0 | 0 | -2 | -4 | -3 | 523 | 523 | 523 | 0 | 0 | 0
144 | Mid Continental East corridor | TOOT | 40 | 48 | 31 |  | 16 | 24 | 10 | 4 | 6 | 2 | -111 | -68 | -162 | 4 | 21 | 53 | 57 | 1 | 2 | 2 | 56 | 90 | 32 |  | -71 | -5 | -85 | -3 | -4 | -2 | -10 | -1 | 950 | 950 | 950 | 8 | 8 | 8
150 | Italy-Slovenia | TOOT | 55 | 60 | 52 |  | 27 | 31 | 23 | 10 | 12 | 6 | -184 | -157 | -209 | 12 | 35 | 89 | 95 | 2 | 6 | 6 | 136 | 170 | 87 |  | -72 | -16 | -48 | -2 | -2 | -6 | 142 | 10 | 252 | 252 | 252 | 3 | 3 | 3
153 | France-Alderney-Britain | TOOT | 106 | 122 | 93 |  | 21 | 23 | 20 | 48 | 49 | 47 | -145 | -139 | -155 | 15 | 28 | 70 | 75 | 3 | 7 | 7 | 680 | 704 | 656 |  | -62 | -13 | -14 | -1 | -1 | -5 | 997 | 55 | 549 | 549 | 549 | 22 | 22 | 22
170 | Baltic States Synchronization with Continental Europe | TOOT | 176 | 177 | 175 |  | 84 | 88 | 82 | 76 | 79 | 74 | -573 | -555 | -601 | 2 | 110 | 275 | 295 | 0 | 1 | 1 | 1085 | 1109 | 1059 |  | -299 | -50 | -194 | -7 | -13 | -18 | 155 | 10 | 1379 | 1379 | 1379 | 23 | 23 | 23
174 | Greenconnector | TOOT | 104 | 123 | 87 |  | 49 | 54 | 40 | 21 | 23 | 18 | -331 | -271 | -364 | 35 | 64 | 159 | 170 | 7 | 17 | 18 | 295 | 318 | 254 |  | -149 | -46 | -6 | -1 | -1 | -16 | 540 | 35 | 793 | 793 | 793 | 24 | 24 | 24
176 | Hansa PowerBridge I | TOOT | 167 | 172 | 159 |  | 9 | 9 | 7 | 86 | 89 | 84 | -58 | -49 | -63 | -2 | 11 | 28 | 30 | 0 | -1 | -1 | 1218 | 1280 | 1180 |  | -36 | -11 | 2 | 0 | 0 | -4 | 21 | 0 | 1470 | 1470 | 1470 | 18 | 18 | 18
187 | St. Peter (AT) - Pleinting (DE) | TOOT | 489 | 508 | 471 |  | 41 | 45 | 36 | 194 | 202 | 186 | -280 | -248 | -307 | 39 | 54 | 135 | 144 | 8 | 19 | 20 | 2762 | 2840 | 2662 |  | -193 | -30 | -77 | -4 | -5 | -11 | 1577 | 72 | 4670 | 4670 | 4670 | 57 | 57 | 57
200 | CZ Northwest-South corridor | TOOT | 194 | 198 | 192 |  | 54 | 56 | 51 | 63 | 65 | 60 | -364 | -347 | -381 | -10 | 70 | 175 | 188 | -2 | -5 | -5 | 895 | 922 | 854 |  | -226 | -63 | -43 | -3 | -3 | -22 | 273 | 8 | 493 | 493 | 493 | 6 | 6 | 6
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 35 | 41 | 32 |  | 11 | 12 | 11 | 9 | 13 | 5 | -75 | -72 | -81 | 2 | 14 | 36 | 39 | 0 | 1 | 1 | 135 | 179 | 73 |  | -37 | -10 | -5 | 0 | 0 | -4 | 33 | 2 | 94 | 94 | 94 | 1 | 1 | 1
219 | Great Sea Interconnector | TOOT | 358 | 385 | 330 |  | -9 | 31 | -38 | 88 | 93 | 78 | 201 | 259 | 132 | 59 | 0 | 0 | 0 | 11 | 28 | 30 | 1251 | 1337 | 1117 |  | -96 | -31 | -4 | -1 | -1 | -11 | -2356 | -172 | 19 | 19 | 19 | 0 | 0 | 0
225 | 2nd interconnector Belgium - Germany | light PINT | 190 | 192 | 188 |  | 12 | 14 | 11 | 116 | 120 | 110 | -82 | -72 | -94 | 14 | 16 | 39 | 42 | 3 | 7 | 7 | 1644 | 1684 | 1588 |  | -67 | -4 | -61 | -2 | -4 | -2 | 901 | 47 | 2040 | 2040 | 2040 | 25 | 25 | 25
227 | Transbalkan Corridor | TOOT | 101 | 104 | 99 |  | 46 | 57 | 31 | 15 | 24 | 8 | -316 | -212 | -388 | -12 | 61 | 152 | 163 | -2 | -6 | -6 | 218 | 345 | 116 |  | -299 | -82 | -79 | -4 | -5 | -29 | -98 | -7 | 1873 | 1873 | 1873 | 20 | 20 | 20
228 | Muhlbach - Eichstetten | TOOT | 72 | 76 | 67 |  | 4 | 5 | 3 | 33 | 36 | 30 | -26 | -19 | -31 | 7 | 5 | 12 | 13 | 1 | 3 | 3 | 471 | 515 | 419 |  | -16 | -5 | -2 | 0 | 0 | -2 | 189 | 9 | 630 | 630 | 630 | 8 | 8 | 8
231 | Beznau - Tiengen | TOOT | 79 | 83 | 75 |  | 17 | 21 | 13 | 61 | 64 | 56 | -117 | -87 | -145 | 7 | 23 | 56 | 60 | 1 | 3 | 4 | 870 | 916 | 805 |  | -82 | -24 | -5 | -1 | -1 | -8 | 73 | -10 | 128 | 128 | 128 | 2 | 2 | 2
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 1438 | 1656 | 1233 |  | 34 | 43 | 29 | 508 | 619 | 423 | -232 | -198 | -290 | 74 | 45 | 112 | 120 | 14 | 36 | 38 | 5 | 6 | 4 |  | -176 | -55 | -5 | -1 | -1 | -19 | 1956 | 101 | 0 | 0 | 0 | 0 | 0 | 0
239 | Fenno-Skan 3 | Light PINT | 64 | 64 | 64 |  | 5 | 7 | 4 | 47 | 53 | 43 | -36 | -28 | -51 |  | 7 | 17 | 19 |  |  |  | 677 | 752 | 603 |  | -57 | -3 | -31 | -1 | -2 | -2 |  |  | 171 | 171 | 171 | 2 | 2 | 2
243 | New 400 kV interconnection line between Serbia and Croatia | Light PINT | 12 | 22 | 6 |  | 8 | 11 | 6 | 1 | 7 | -4 | -53 | -39 | -72 |  | 10 | 25 | 27 |  |  |  | 19 | 107 | -54 |  | -40 | -14 | 3 | 0 | 0 | -5 |  |  | 6 | 6 | 6 | 0 | 0 | 0
244 | Vigy - Uchtelfangen area | TOOT | 367 | 377 | 356 |  | 23 | 25 | 22 | 159 | 168 | 151 | -159 | -149 | -168 | 57 | 31 | 77 | 82 | 11 | 27 | 29 | 2266 | 2400 | 2172 |  | -134 | -23 | -58 | -3 | -4 | -8 | 1101 | 62 | 3208 | 3208 | 3208 | 39 | 39 | 39
247 | AQUIND Interconnector | TOOT | 164 | 168 | 161 |  | 39 | 40 | 38 | 83 | 84 | 83 | -265 | -259 | -271 | 19 | 51 | 128 | 137 | 4 | 9 | 10 | 1180 | 1199 | 1161 |  | -107 | -23 | -25 | -2 | -2 | -8 | 801 | 48 | 1091 | 1091 | 1091 | 39 | 39 | 39
250 | Merchant line Castasegna (CH) - Mese (IT) | TOOT | 20 | 27 | 13 |  | 8 | 10 | 6 | 4 | 6 | 3 | -57 | -40 | -67 | 5 | 11 | 27 | 29 | 1 | 2 | 3 | 62 | 86 | 47 |  | -25 | -9 | 3 | 0 | 0 | -3 | 27 | 4 | 88 | 88 | 88 | 4 | 4 | 4
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 276 | 313 | 236 |  | 5 | 5 | 5 | 80 | 88 | 74 | -33 | -31 | -35 | 37 | 6 | 16 | 17 | 7 | 18 | 19 | 1 | 1 | 1 |  | -25 | -8 | -1 | 0 | 0 | -3 | 846 | 46 | 0 | 0 | 0 | 0 | 0 | 0
259 | HU-RO | TOOT | 48 | 49 | 48 |  | 10 | 11 | 9 | 2 | 4 | 0 | -67 | -60 | -72 | 47 | 13 | 32 | 35 | 9 | 23 | 24 | 29 | 56 | 3 |  | -58 | -7 | -27 | -1 | -2 | -3 | 201 | 18 | 1087 | 1087 | 1087 | 10 | 10 | 10
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | TOOT | 172 | 185 | 162 |  | 20 | 22 | 19 | 77 | 83 | 71 | -137 | -130 | -146 | 35 | 26 | 66 | 71 | 7 | 17 | 18 | 1100 | 1189 | 1010 |  | -103 | -24 | -26 | -1 | -2 | -8 | 305 | 24 | 992 | 992 | 992 | 45 | 45 | 45
267 | Hansa PowerBridge II | Light PINT | 167 | 172 | 159 |  | 9 | 9 | 7 | 86 | 89 | 84 | -58 | -49 | -63 | -2 | 11 | 28 | 30 | 0 | -1 | -1 | 1218 | 1280 | 1180 |  | -36 | -11 | 2 | 0 | 0 | -4 | 21 | 0 | 1470 | 1470 | 1470 | 18 | 18 | 18
270 | FR-ES project -Aragón-Atlantic Pyrenees | TOOT | 217 | 221 | 214 |  | 49 | 49 | 48 | 132 | 154 | 102 | -333 | -327 | -337 | 19 | 64 | 160 | 171 | 4 | 9 | 10 | 1875 | 2159 | 1451 |  | -126 | -25 | -35 | -2 | -2 | -9 | 1765 | 68 | 2215 | 2215 | 2215 | 31 | 31 | 31
276 | FR-ES project -Navarra-Landes | PINT | 184 | 186 | 180 |  | 42 | 47 | 35 | 128 | 129 | 127 | -284 | -238 | -318 | 31 | 55 | 137 | 146 | 6 | 15 | 16 | 1813 | 1815 | 1812 |  | -41 | -16 | 8 | 0 | 0 | -6 | 2571 | 103 | 729 | 729 | 729 | 9 | 9 | 9
280 | FR-BE: Lonny-Achene-Gramme | TOOT | 170 | 173 | 167 |  | 6 | 8 | 5 | 55 | 62 | 51 | -43 | -37 | -54 | 20 | 8 | 21 | 22 | 4 | 10 | 10 | 783 | 886 | 727 |  | -33 | -11 | 5 | 0 | 0 | -4 | 475 | 26 | 832 | 832 | 832 | 30 | 30 | 30
283 | TuNur Italy | PINT | 8 | 15 | 2 |  | 111 | 111 | 110 | -84 | -78 | -90 | -752 | -749 | -754 | 13 | 144 | 362 | 387 | 2 | 6 | 6 | -1191 | -1111 | -1272 | 5000 | -371 | -96 | -69 | -5 | -6 | -34 | -73 | -3 | 0 | 0 | 0 | 0 | 0 | 0
285 | GridLink | TOOT | 106 | 122 | 93 |  | 21 | 23 | 20 | 48 | 49 | 47 | -145 | -139 | -155 | 16 | 28 | 70 | 75 | 3 | 8 | 8 | 680 | 704 | 656 |  | -62 | -13 | -14 | -1 | -1 | -5 | 498 | 30 | 566 | 566 | 566 | 22 | 22 | 22
297 | BRABO III | TOOT | 72 | 72 | 71 |  | 5 | 5 | 4 | 50 | 52 | 47 | -34 | -29 | -36 | 7 | 7 | 16 | 17 | 1 | 3 | 4 | 709 | 738 | 667 |  | -37 | -4 | -27 | -1 | -2 | -1 | 169 | 8 | 522 | 522 | 522 | 30 | 30 | 30
299 | SACOI 3 | TOOT | 179 | 183 | 176 |  | 98 | 99 | 97 | 21 | 23 | 19 | -667 | -659 | -675 | -3 | 128 | 321 | 344 | -1 | -1 | -2 | 298 | 318 | 278 |  | -2063 | -3 | -1369 | -53 | -74 | -21 | -70 | -6 | 944 | 944 | 944 | 17 | 17 | 17
309 | NeuConnect | TOOT | 170 | 182 | 158 |  | 36 | 39 | 33 | 86 | 88 | 83 | -245 | -222 | -266 | 38 | 47 | 118 | 126 | 7 | 18 | 20 | 1225 | 1254 | 1183 |  | -170 | -29 | -66 | -3 | -4 | -11 | 513 | 34 | 3012 | 3012 | 3012 | 37 | 37 | 37
312 | St. Peter (AT) - Tauern (AT) | TOOT | 375 | 389 | 363 |  | 31 | 32 | 28 | 150 | 155 | 144 | -210 | -193 | -218 | -35 | 40 | 101 | 108 | -7 | -17 | -18 | 2137 | 2176 | 2062 |  | -143 | -23 | -54 | -3 | -4 | -9 | -233 | -16 | 3588 | 3588 | 3588 | 44 | 44 | 44
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 254 | 256 | 251 |  | 23 | 29 | 19 | 99 | 103 | 97 | -153 | -129 | -196 | -23 | 29 | 74 | 79 | -4 | -11 | -12 | 1410 | 1445 | 1391 |  | -89 | -13 | -33 | -2 | -2 | -5 | 364 | 5 | 2307 | 2307 | 2307 | 28 | 28 | 28
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 9 | 13 | 6 |  | 2 | 4 | 0 | 3 | 6 | 0 | -16 | 0 | -27 | 27 | 3 | 8 | 8 | 5 | 13 | 14 | 35 | 83 | 5 |  | -14 | -1 | -15 | 0 | -1 | -1 | 275 | 18 | 9 | 9 | 9 | 0 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 11 | 18 | 7 |  | 3 | 5 | 0 | 1 | 3 | -1 | -19 | -3 | -35 | 28 | 4 | 9 | 10 | 5 | 14 | 14 | 21 | 48 | -9 |  | -12 | -3 | -9 | 0 | 0 | -1 | 285 | 18 | 24 | 24 | 24 | 0 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | TOOT | 214 | 218 | 211 |  | 87 | 91 | 82 | 57 | 61 | 52 | -590 | -557 | -617 | 6 | 113 | 284 | 304 | 1 | 3 | 3 | 814 | 882 | 735 |  | -266 | -86 | -13 | -2 | -2 | -30 | 191 | 10 | 740 | 740 | 740 | 9 | 9 | 9
328 | Interconnector DE-LUX | TOOT | 49 | 50 | 48 |  | -1 | 1 | -3 | 5 | 7 | 2 | 13 | 21 | 7 | 5 | 0 | 0 | 0 | 1 | 2 | 2 | 69 | 95 | 32 |  | -3 | 1 | -6 | 0 | 0 | 0 | -187 | -19 | 46 | 46 | 46 | 1 | 1 | 1
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 232 | 269 | 219 |  | 83 | 96 | 78 | 180 | 209 | 170 | -1816 | -2843 | -1503 | -9 | 615 | 1140 | 1202 | -2 | -4 | -5 | 3630 | 3568 | 3690 |  | -2080 | -138 | -2107 | -111 | -190 | -47 | -336 | -31 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | TOOT | 131 | 137 | 123 |  | 0 | 6 | -4 | 4 | 6 | 2 | 27 | 42 | 13 | 20 | 0 | 0 | 0 | 4 | 9 | 10 | 54 | 93 | 22 |  | -9 | 4 | -27 | -1 | -1 | 1 | 72 | 8 | 256 | 256 | 256 | 2 | 2 | 2
335 | North Sea Wind Power Hub | Light PINT | 1735 | 1744 | 1727 | 1326 | 232 | 239 | 225 | 2846 | 2851 | 2841 | -1578 | -1528 | -1628 |  | 303 | 759 | 813 |  |  |  | 40350 | 40709 | 39991 | 14000 | -1103 | -146 | -544 | -23 | -33 | -56 |  |  | 4973 | 4973 | 4973 | 61 | 61 | 61
338 | Adriatic HVDC link | TOOT | 116 | 120 | 110 |  | 31 | 33 | 29 | 50 | 59 | 43 | -210 | -200 | -225 | 27 | 40 | 101 | 108 | 5 | 13 | 14 | 691 | 833 | 510 |  | -146 | -39 | -25 | -2 | -2 | -14 | 338 | 13 | 1354 | 1354 | 1354 | 11 | 11 | 11
339 | Tyrrhenian link | TOOT | 95 | 101 | 89 |  | 3 | 33 | -31 | 51 | 61 | 47 | -189 | -128 | -226 | 11 | 4 | 10 | 10 | 2 | 5 | 6 | 692 | 721 | 670 |  | -106 | -31 | -8 | -1 | -1 | -11 | 374 | 9 | 1437 | 1437 | 1437 | 0 | 0 | 0
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 258 | 294 | 189 |  | 92 | 105 | 68 | 201 | 229 | 147 | -2563 | -3132 | -1285 | -6 | 869 | 1610 | 1697 | -1 | -3 | -3 | 3659 | 3094 | 4045 |  | -3036 | -182 | -3444 | -152 | -293 | -63 | -595 | -46 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | TOOT | 13 | 14 | 11 |  | 9 | 13 | 5 | 3 | 12 | -2 | -59 | -32 | -88 | 129 | 11 | 29 | 31 | 25 | 62 | 66 | 49 | 172 | -26 |  | -26 | -2 | -42 | -1 | -2 | -1 | 1211 | 80 | 105 | 105 | 105 | 0 | 0 | 0
342 | Central Balkan Corridor | TOOT | 10 | 12 | 7 |  | 10 | 15 | 7 | 1 | 4 | -1 | -65 | -45 | -99 | 2 | 13 | 31 | 34 | 0 | 1 | 1 | 16 | 61 | -10 |  | -43 | -4 | -49 | -1 | -2 | -1 | 18 | 0 | 337 | 337 | 337 | 3 | 3 | 3
343 | CSE1 New | TOOT | 10 | 12 | 8 |  | 4 | 6 | 2 | -1 | 1 | -5 | -30 | -16 | -41 | 14 | 6 | 14 | 15 | 3 | 7 | 7 | -20 | 8 | -71 |  | -39 | -8 | -19 | -1 | -1 | -3 | 99 | 8 | 94 | 94 | 94 | 0 | 0 | 0
346 | ZuidWest380 NL Oost | TOOT | 20 | 26 | 15 |  | 0 | 1 | 0 | 6 | 7 | 4 | -3 | 1 | -5 | -4 | 1 | 2 | 2 | -1 | -2 | -2 | 82 | 102 | 61 |  | 10 | 1 | 6 | 0 | 0 | 0 | -121 | -6 | 332 | 332 | 332 | 28 | 28 | 28
349 | MaresConnect | TOOT | 58 | 61 | 55 |  | 27 | 30 | 25 | 90 | 98 | 83 | -184 | -173 | -203 | -1 | 35 | 89 | 95 | 0 | 0 | 0 | 1283 | 1375 | 1185 |  | -82 | -23 | -15 | -1 | -1 | -8 | 76 | 2 | 1540 | 1540 | 1540 | 15 | 15 | 15
350 | South Balkan Corridor | TOOT | 55 | 56 | 54 |  | 29 | 38 | 23 | 17 | 23 | 8 | -198 | -154 | -259 | 109 | 38 | 95 | 102 | 21 | 52 | 56 | 247 | 323 | 118 |  | -163 | -53 | -4 | -1 | -1 | -19 | 1216 | 79 | 472 | 472 | 472 | 0 | 0 | 0
375 | Lienz (AT) - Veneto region (IT) 220 kV | TOOT | 116 | 124 | 105 |  | 36 | 40 | 31 | 31 | 33 | 30 | -245 | -213 | -272 | 14 | 47 | 118 | 126 | 3 | 7 | 7 | 446 | 476 | 419 |  | -113 | -31 | -18 | -1 | -1 | -11 | 117 | 8 | 389 | 389 | 389 | 5 | 5 | 5
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | Light PINT | 21 | 25 | 18 |  | 11 | 13 | 9 | 7 | 9 | 5 | -77 | -59 | -86 |  | 15 | 37 | 39 |  |  |  | 103 | 130 | 75 |  | -68 | -22 | 2 | 0 | 0 | -8 |  |  | 14 | 14 | 14 | 0 | 0 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | TOOT | 71 | 72 | 71 |  | 5 | 5 | 4 | 49 | 51 | 47 | -33 | -29 | -36 | 9 | 6 | 16 | 17 | 2 | 4 | 5 | 704 | 724 | 667 |  | -37 | -4 | -27 | -1 | -2 | -1 | 193 | 9 | 514 | 514 | 514 | 30 | 30 | 30
378 | Transformer Gatica | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 226 | 292 | 184 |  | 7 | 10 | 5 | 106 | 151 | 78 | -48 | -32 | -70 | 41 | 9 | 23 | 25 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | -36 | -11 | -1 | 0 | 0 | -4 | 886 | 51 | 0 | 0 | 0 | 0 | 0 | 0
1039 | SE North-south long-term reinforcements | PINT | 46 | 49 | 41 |  | 6 | 8 | 4 | 8 | 9 | 8 | -40 | -25 | -51 | 6 | 8 | 19 | 21 | 1 | 3 | 3 | 120 | 129 | 109 |  | -23 | -4 | -11 | 0 | -1 | -1 | 131 | 4 | 82 | 82 | 82 | 0 | 0 | 0
1040 | LirIC | TOOT | 125 | 130 | 120 |  | 41 | 44 | 38 | 35 | 47 | 24 | -278 | -260 | -301 | 1 | 53 | 134 | 143 | 0 | 1 | 1 | 498 | 658 | 346 |  | -248 | -41 | -87 | -4 | -6 | -15 | 65 | 3 | 550 | 550 | 550 | 6 | 6 | 6
1041 | GREGY Green Energy Interconnector | TOOT | 458 | 462 | 454 |  | -223 | -177 | -269 | 233 | 233 | 233 | 1830 | 1830 | 1830 | -4 | 0 | 0 | 0 | -1 | -2 | -2 | 3279 | 3279 | 3279 |  | -176 | -48 | -27 | -2 | -2 | -17 | 673 | 41 | 135 | 135 | 135 | 1 | 1 | 1
1046 | Finnish North-South reinforcement | PINT | 287 | 287 | 287 |  | 14 | 14 | 14 | 413 | 413 | 413 | 95.093 | 95.093 | 95.093 | -1 | 18 | 46 | 49 | 0 | 0 | 0 | 6463 | 6463 | 6463 |  | -15 | -4 | -14 | 0 | -1 | -1 | -138 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 63 | 65 | 60 |  | -36 | -29 | -42 | 40 | 43 | 36 | 261 | 296 | 200 | -66 | 0 | 0 | 0 | -13 | -32 | -34 | 574 | 620 | 510 |  | -26 | -8 | -2 | 0 | 0 | -3 | -4572 | -290 | 2 | 2 | 2 | 0 | 0 | 0
1049 | Cronos Energy Ltd | PINT | 125 | 127 | 123 |  | 30 | 30 | 29 | 2 | 13 | -5 | -203 | -197 | -206 | 8 | 39 | 98 | 105 | 2 | 4 | 4 | 31 | 186 | -74 |  | -146 | -24 | -61 | -3 | -4 | -9 | -100 | 0 | 542 | 542 | 542 | 14 | 14 | 14
1050 | Tarchon Energy Ltd | TOOT | 170 | 182 | 158 |  | 36 | 39 | 33 | 86 | 88 | 83 | -245 | -222 | -266 | 24 | 47 | 118 | 126 | 5 | 12 | 12 | 1225 | 1254 | 1183 |  | -170 | -29 | -66 | -3 | -4 | -11 | 335 | 21 | 3004 | 3004 | 3004 | 37 | 37 | 37
1052 | Lienz (AT) - Malta (AT) - Obersielach (AT) | TOOT | 499 | 506 | 493 | 124 | 142 | 145 | 139 | 325 | 357 | 294 | -964 | -943 | -985 | 4 | 185 | 464 | 497 | 1 | 2 | 2 | 4615 | 5113 | 4117 | 2000 | -464 | -139 | -54 | -5 | -5 | -49 | -97 | -7 | 1024 | 1024 | 1024 | 13 | 13 | 13
1054 | 220-kV Westtirol (AT) - Zell/Ziller (AT) | TOOT | 103 | 106 | 102 |  | 8 | 10 | 7 | 41 | 42 | 40 | -53 | -45 | -65 | 14 | 10 | 26 | 27 | 3 | 7 | 7 | 581 | 593 | 568 |  | -32 | -4 | -13 | -1 | -1 | -2 | 391 | 20 | 778 | 778 | 778 | 10 | 10 | 10
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 80 | 84 | 76 |  | -1 | 4 | -5 | 56 | 62 | 48 | 23 | 32 | 16 | 233 | 0 | 0 | 0 | 45 | 112 | 120 | 796 | 875 | 683 |  | -8 | -2 | -5 | 0 | 0 | -1 | 7116 | 457 | 43 | 43 | 43 | 0 | 0 | 0
1058 | HVDC Interconnector DE-CH | Light PINT | 226 | 228 | 224 |  | 18 | 22 | 13 | 100 | 101 | 99 | -125 | -88 | -148 |  | 24 | 60 | 64 |  |  |  | 1424 | 1441 | 1407 |  | -96 | -20 | -37 | -2 | -2 | -7 |  |  | 331 | 331 | 331 | 4 | 4 | 4
1059 | Southern Italy | TOOT | 10 | 13 | 7 |  | 1 | 3 | -3 | 1 | 2 | -1 | -16 | -8 | -20 | 4 | 1 | 3 | 3 | 1 | 2 | 2 | 7 | 25 | -12 |  | -19 | -4 | -6 | 0 | 0 | -1 | 121 | 1 | 690 | 690 | 690 | 0 | 0 | 0
1066 | Bulgaria - Turkey | Light PINT | 74 | 91 | 54 |  | -145 | -143 | -148 | 11 | 17 | 7 | 934 | 1009 | 823 |  | 0 | 0 | 0 |  |  |  | 160 | 236 | 103 |  | -495 | -158 | -1 | -4 | -4 | -55 |  |  | 272 | 272 | 272 | 1 | 1 | 1
1067 | New AC 400 kV interconnection line Greece - Turkey | Light PINT | 76 | 80 | 71 |  | -59 | -55 | -63 | 27 | 29 | 23 | 421 | 456 | 376 |  | 0 | 0 | 0 |  |  |  | 385 | 418 | 324 |  | -90 | -22 | -22 | -1 | -2 | -8 |  |  | 10 | 10 | 10 | 0 | 0 | 0
1068 | LaSGo Link | PINT | 58 | 59 | 57 |  | 8 | 12 | 6 | 41 | 45 | 36 | -57 | -41 | -81 | 1 | 11 | 28 | 30 | 0 | 1 | 1 | 583 | 649 | 508 |  | -151 | -3 | -96 | -4 | -5 | -2 | 53 | 3 | 129 | 129 | 129 | 0 | 0 | 0
1074 | Pannonian Corridor | TOOT | 19 | 29 | 10 |  | 2 | 3 | 2 | 0 | 4 | -5 | -8 | 9 | -22 | 10 | 3 | 8 | 9 | 2 | 5 | 5 | 6 | 59 | -78 |  | -16 | -4 | 10 | 0 | 0 | -1 | 40 | 3 | 632 | 632 | 632 | 6 | 6 | 6
1085 | Malta-Italy Cable Link No.2 | TOOT | 34 | 36 | 31 |  | -2 | 16 | -17 | 20 | 22 | 19 | 15 | 116 | -107 | -8 | 0 | 0 | 0 | -1 | -4 | -4 | 286 | 310 | 268 |  | -42 | -11 | -9 | -1 | -1 | -4 | -45 | -4 | 70 | 70 | 70 | 1 | 1 | 1
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 8 | 14 | 2 | 75 | 8 | 10 | 7 | 91 | 96 | 87 | -56 | -50 | -65 | -2 | 11 | 27 | 29 | 0 | -1 | -1 | 1296 | 1374 | 1252 | 700 | -126 | -2 | -85 | -3 | -5 | -2 | -371 | -13 | 0 | 0 | 0 | 0 | 0 | 0
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | TOOT | 54 | 54 | 54 | 114 | 16 | 17 | 15 | 175 | 175 | 174 | -109 | -104 | -114 | 0 | 21 | 52 | 56 | 0 | 0 | 0 | 2482 | 2505 | 2460 | 1000 | -84 | -6 | -51 | -2 | -3 | -3 | -214 | -10 | 0 | 0 | 0 | 0 | 0 | 0
1092 | TritonLink: offshore hybrid HVDC interconnector Belgium – Denmark | TOOT | 1112 | 1144 | 1083 | 151 | 102 | 107 | 97 | 1135 | 1189 | 1082 | -692 | -662 | -728 | 29 | 133 | 333 | 356 | 6 | 14 | 15 | 16115 | 16670 | 15457 | 10000 | -529 | -65 | -294 | -12 | -19 | -24 | 443 | 31 | 6504 | 6504 | 6504 | 219 | 219 | 219
1094 | Estlink 3 | TOOT | 73 | 74 | 71 |  | 9 | 11 | 6 | 55 | 57 | 54 | -58 | -44 | -73 | 6 | 11 | 28 | 30 | 1 | 3 | 3 | 787 | 800 | 774 |  | -58 | -10 | -17 | -1 | -1 | -4 | 63 | 4 | 763 | 763 | 763 | 6 | 6 | 6
1095 | Aurora line 2 (4th AC Finland-Sweden north) | TOOT | 63 | 63 | 63 |  | 4 | 5 | 3 | 38 | 46 | 29 | -25 | -21 | -32 | 2 | 5 | 12 | 13 | 0 | 1 | 1 | 545 | 641 | 410 |  | -52 | -5 | -29 | -1 | -2 | -2 | 43 | 2 | 1174 | 1174 | 1174 | 9 | 9 | 9
1096 | Beznau - Mettlen | Light TOOT | 79 | 84 | 74 |  | 22 | 25 | 16 | 69 | 70 | 68 | -148 | -108 | -173 |  | 28 | 71 | 76 |  |  |  | 984 | 1009 | 962 |  | -102 | -31 | -5 | -1 | -1 | -11 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1097 | Upgrade to Konti-Skan | PINT | 143 | 144 | 141 |  | 11 | 11 | 10 | 120 | 124 | 113 | -74 | -71 | -76 | 10 | 14 | 36 | 38 | 2 | 5 | 5 | 1707 | 1781 | 1613 |  | -21 | -4 | -3 | 0 | 0 | -2 | 263 | 14 | 177 | 177 | 177 | 0 | 0 | 0
1098 | Offshore Wind LT 2 | TOOT | 6 | 11 | 4 | 96 | 8 | 10 | 7 | 112 | 117 | 110 | -56 | -48 | -65 | 0 | 11 | 27 | 29 | 0 | 0 | 0 | 1593 | 1636 | 1571 | 700 | -63 | -3 | -37 | -1 | -2 | -2 | 104 | 5 | 121 | 121 | 121 | 1 | 1 | 1
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | TOOT | 194 | 202 | 186 |  | 54 | 56 | 50 | 65 | 68 | 61 | -366 | -343 | -379 | 21 | 70 | 176 | 188 | 4 | 10 | 11 | 928 | 957 | 878 |  | -228 | -63 | -46 | -3 | -4 | -22 | 559 | 24 | 0 | 0 | 0 | 0 | 0 | 0
1102 | Mettlen - Ulrichen | Light TOOT | 26 | 27 | 25 |  | 0 | 2 | -2 | 1 | 3 | -2 | 9 | 14 | 6 |  | 0 | 0 | 0 |  |  |  | 12 | 41 | -26 |  | 0 | -2 | 2 | 0 | 0 | -1 |  |  | 282 | 282 | 282 | 0 | 0 | 0
1103 | Bickigen - Chippis | Light TOOT | 53 | 58 | 50 |  | 14 | 17 | 11 | 50 | 52 | 48 | -97 | -75 | -113 |  | 19 | 47 | 50 |  |  |  | 710 | 752 | 689 |  | -66 | -21 | -2 | -1 | 0 | -7 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1104 | Bauler - Roost | TOOT | 3 | 4 | 1 |  | -1 | 1 | -3 | 3 | 5 | 1 | 6 | 18 | -2 | 4 | 0 | 0 | 0 | 1 | 2 | 2 | 37 | 69 | 10 |  | -1 | 0 | -3 | 0 | 0 | 0 | -196 | -19 | 0 | 0 | 0 | 0 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 121 | 124 | 118 |  | -7 | -4 | -11 | -3 | -2 | -4 | 50 | 73 | 27 | -23 | 0 | 0 | 0 | -4 | -11 | -12 | -46 | -32 | -60 |  | -27 | -15 | 45 | 1 | 1 | -5 | -64 | -5 | 521 | 521 | 521 | 4 | 4 | 4
1106 | Bornholm Energy Island (BEI) | TOOT | 324 | 324 | 324 | 299 | 50 | 53 | 46 | 544 | 555 | 531 | -340 | -312 | -364 | -7 | 65 | 164 | 175 | -1 | -3 | -4 | 7735 | 7835 | 7588 | 3000 | -108 | -29 | -18 | -1 | -2 | -10 | -434 | -20 | 3410 | 3410 | 3410 | 42 | 42 | 42
1109 | Basilicata - Campania reinforcements | TOOT | 16 | 20 | 13 |  | 3 | 7 | -4 | 3 | 5 | -2 | -34 | -29 | -45 | -7 | 4 | 10 | 10 | -1 | -3 | -3 | 36 | 68 | -24 |  | -29 | -8 | -6 | 0 | 0 | -3 | -32 | -7 | 449 | 449 | 449 | 0 | 0 | 0
1110 | Sicily - Calabria | TOOT | 5 | 8 | 2 |  | 0 | 1 | -2 | 3 | 6 | 1 | -3 | 4 | -13 | -5 | 0 | 0 | 0 | -1 | -3 | -3 | 35 | 81 | 17 |  | 8 | 1 | 5 | 0 | 0 | 0 | 7 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1112 | GRITA 2 | TOOT | 212 | 215 | 208 |  | 61 | 63 | 58 | 80 | 80 | 79 | -413 | -396 | -429 | 38 | 79 | 199 | 213 | 7 | 18 | 19 | 1128 | 1139 | 1118 |  | -99 | -37 | 13 | 0 | 0 | -13 | 519 | 38 | 1226 | 1226 | 1226 | 0 | 0 | 0
1121 | 220-kV Hessenberg (AT) - Weißenbach (AT) | TOOT | 1 | 3 | 0 | 51 | 3 | 4 | 3 | 59 | 63 | 57 | -22 | -18 | -28 | -1 | 4 | 11 | 11 | 0 | -1 | -1 | 838 | 884 | 809 | 600 | -14 | -3 | -3 | 0 | 0 | -1 | -95 | -3 | 0 | 0 | 0 | 0 | 0 | 0
1122 | Offshore Wind farm connection Centre Manche 1 | TOOT | 29 | 33 | 27 | 249 | 26 | 28 | 24 | 342 | 353 | 329 | -178 | -162 | -192 | 105 | 34 | 86 | 92 | 20 | 50 | 54 | 4951 | 4962 | 4940 | 1050 | -97 | -10 | -52 | -2 | -3 | -4 | 911 | 45 | 165 | 165 | 165 | 3 | 3 | 3
1123 | Offshore Wind farm connection Centre Manche 2 | TOOT | 98 | 102 | 96 | 180 | 26 | 28 | 24 | 342 | 353 | 329 | -178 | -162 | -192 | 79 | 34 | 86 | 92 | 15 | 38 | 41 | 4951 | 4962 | 4940 | 1250 | -97 | -10 | -52 | -2 | -3 | -4 | 662 | 34 | 167 | 167 | 167 | 3 | 3 | 3
1124 | Offshore Wind Connection South Britanny | TOOT | 20 | 21 | 18 | 155 | 17 | 18 | 15 | 210 | 218 | 201 | -114 | -104 | -123 | 63 | 22 | 55 | 59 | 12 | 30 | 32 | 2982 | 3060 | 2873 | 250 | -55 | -7 | -28 | -1 | -2 | -3 | 663 | 28 | 99 | 99 | 99 | 2 | 2 | 2
1125 | Offshore Wind Connection Occitanie | TOOT | 65 | 66 | 64 | 125 | 18 | 20 | 17 | 211 | 219 | 203 | -126 | -119 | -135 | 11 | 24 | 60 | 65 | 2 | 5 | 6 | 3004 | 3080 | 2902 | 250 | -71 | -10 | -29 | -1 | -2 | -4 | 74 | 4 | 99 | 99 | 99 | 2 | 2 | 2
1126 | Offshore Wind Connection PACA | TOOT | 61 | 67 | 55 | 120 | 18 | 19 | 18 | 202 | 210 | 195 | -124 | -119 | -131 | -18 | 24 | 59 | 64 | -3 | -8 | -9 | 2878 | 2949 | 2782 | 250 | -77 | -10 | -35 | -2 | -2 | -4 | -223 | -9 | 99 | 99 | 99 | 2 | 2 | 2
1127 | Offshore Wind Connection South Atlantic Oléron 1 | TOOT | 22 | 25 | 20 | 234 | 24 | 27 | 21 | 302 | 311 | 291 | -162 | -143 | -182 | 70 | 31 | 78 | 84 | 13 | 33 | 36 | 4294 | 4366 | 4159 | 1250 | -90 | -11 | -47 | -2 | -3 | -4 | 622 | 30 | 165 | 165 | 165 | 3 | 3 | 3
1134 | GiLA | PINT | 455 | 455 | 455 |  | 39 | 39 | 39 | 287 | 287 | 287 | -264 | -264 | -264 | 13 | 0 | 0 | 0 | 2 | 6 | 7 | 5647 | 5647 | 5647 |  | -115 | -36 | -5 | -1 | -1 | -13 | 756 | 31 | 0 | 0 | 0 | 0 | 0 | 0
1138 | 400 kV OHL Suceava (RO) - Balti (MD) | TOOT | 60 | 64 | 56 |  | 21 | 26 | 17 | 8 | 12 | 7 | -141 | -118 | -175 | 56 | 27 | 68 | 72 | 11 | 27 | 29 | 119 | 164 | 95 |  | -67 | -34 | 42 | 1 | 2 | -12 | 1618 | 89 | 252 | 252 | 252 | 2 | 2 | 2
1139 | 380-kV Westtirol (AT) – Zell/Ziller (AT) | PINT | 72 | 105 | 36 | 77 | 5 | 17 | -10 | 158 | 179 | 130 | -82 | -61 | -115 | -22 | 7 | 17 | 18 | -4 | -11 | -11 | 2245 | 2512 | 1864 | 1600 | -63 | -9 | -33 | -1 | -2 | -4 | -681 | -35 | 0 | 0 | 0 | 0 | 0 | 0
1140 | 380-kV St. Peter (AT) - Dürnrohr (AT) | PINT | 118 | 122 | 113 | 68 | 16 | 17 | 14 | 161 | 166 | 156 | -106 | -99 | -114 | -12 | 20 | 51 | 55 | -2 | -6 | -6 | 2285 | 2330 | 2241 | 1500 | -72 | -10 | -37 | -2 | -2 | -4 | -293 | -17 | 287 | 287 | 287 | 4 | 4 | 4
1145 | 380-kV Obersielach (AT) - Hessenberg (AT) | TOOT | 3 | 6 | 0 | 170 | 14 | 15 | 14 | 194 | 201 | 188 | -97 | -93 | -100 | -17 | 19 | 47 | 50 | -3 | -8 | -9 | 2761 | 2816 | 2701 | 2000 | -59 | -12 | -23 | -1 | -2 | -4 | -225 | -13 | 0 | 0 | 0 | 0 | 0 | 0
1153 | PST romands | TOOT | 104 | 113 | 100 |  | 34 | 37 | 28 | 32 | 39 | 27 | -231 | -191 | -255 | 93 | 44 | 111 | 119 | 18 | 45 | 48 | 458 | 562 | 382 |  | -168 | -54 | -5 | -1 | -1 | -19 | 727 | 38 | 382 | 382 | 382 | 9 | 9 | 9
1155 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT) | TOOT | 13 | 21 | 5 | 298 | 25 | 27 | 23 | 344 | 356 | 334 | -172 | -154 | -185 | -1 | 33 | 83 | 89 | 0 | 0 | 0 | 4895 | 5005 | 4772 | 2000 | -90 | -20 | -28 | -1 | -2 | -7 | -132 | -5 | 0 | 0 | 0 | 0 | 0 | 0
1156 | 380-kV Greater Vienna (AT) - Hessenberg (AT) | TOOT | 7 | 12 | 0 | 233 | 19 | 20 | 17 | 263 | 263 | 262 | -127 | -114 | -137 | -12 | 24 | 61 | 65 | -2 | -6 | -6 | 3810 | 3912 | 3748 | 2500 | -70 | -15 | -23 | -1 | -2 | -5 | -213 | -12 | 0 | 0 | 0 | 0 | 0 | 0
1157 | HG North Tyrrhenian Corridor | TOOT | 301 | 309 | 295 |  | 87 | 91 | 85 | 123 | 135 | 110 | -594 | -579 | -619 | 96 | 114 | 285 | 306 | 19 | 46 | 50 | 1680 | 1936 | 1291 |  | -388 | -107 | -57 | -4 | -6 | -38 | 734 | 48 | 4244 | 4244 | 4244 | 45 | 45 | 45
1158 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT) | PINT | 6 | 8 | 5 | 163 | 13 | 16 | 10 | 190 | 198 | 185 | -91 | -71 | -106 | -2 | 17 | 44 | 47 | 0 | -1 | -1 | 2707 | 2777 | 2658 | 2000 | -49 | -10 | -18 | -1 | -1 | -4 | -191 | -7 | 0 | 0 | 0 | 0 | 0 | 0
1159 | 220-kV Bisamberg (AT) – Wien Südost (AT) | TOOT | 1 | 3 | 0 | 19 | 0 | 1 | -1 | 25 | 27 | 22 | 2 | 8 | -7 | -1 | 0 | 0 | 0 | 0 | -1 | -1 | 352 | 385 | 308 | 500 | -3 | -1 | 2 | 0 | 0 | -1 | -3 | 1 | 0 | 0 | 0 | 0 | 0 | 0
1161 | Offshore Wind Connection South Atlantic Oléron 2 | TOOT | 12 | 12 | 12 | 210 | 21 | 22 | 20 | 269 | 279 | 258 | -140 | -134 | -152 | 106 | 27 | 68 | 72 | 20 | 51 | 55 | 3825 | 3913 | 3691 | 1200 | -83 | -10 | -41 | -2 | -3 | -4 | 900 | 46 | 157 | 157 | 157 | 3 | 3 | 3
1162 | Offshore Wind Connection Fécamp-Grand Large 1 | TOOT | 18 | 19 | 17 | 351 | 35 | 37 | 33 | 448 | 464 | 429 | -236 | -223 | -252 | 71 | 45 | 114 | 122 | 14 | 34 | 37 | 6495 | 6521 | 6470 | 2000 | -111 | -15 | -50 | -2 | -3 | -6 | 454 | 28 | 263 | 263 | 263 | 5 | 5 | 5
1163 | Offshore Wind Connection Fécamp-Grand Large 2 | TOOT | 128 | 129 | 127 | 241 | 35 | 37 | 33 | 448 | 464 | 429 | -236 | -223 | -252 | 71 | 45 | 114 | 122 | 14 | 34 | 37 | 6495 | 6521 | 6470 | 2000 | -111 | -15 | -50 | -2 | -3 | -6 | 454 | 28 | 262 | 262 | 262 | 4 | 4 | 4
1164 | Offshore Wind Connection Golfe de Lion Centre | TOOT | 128 | 129 | 127 | 241 | 35 | 37 | 33 | 448 | 464 | 429 | -236 | -223 | -252 | -63 | 45 | 114 | 122 | -12 | -30 | -32 | 6495 | 6521 | 6470 | 2000 | -111 | -15 | -50 | -2 | -3 | -6 | -649 | -29 | 265 | 265 | 265 | 4 | 4 | 4
1165 | Offshore Wind Connection Golfe de Gascogne Sud | TOOT | 77 | 77 | 77 | 145 | 21 | 22 | 20 | 269 | 279 | 258 | -140 | -134 | -152 | 56 | 27 | 68 | 72 | 11 | 27 | 29 | 3825 | 3913 | 3691 | 1200 | -83 | -10 | -41 | -2 | -3 | -4 | 464 | 24 | 158 | 158 | 158 | 3 | 3 | 3
1166 | HG Adriatic Corridor | PINT | 140 | 145 | 135 |  | 37 | 38 | 35 | 65 | 67 | 62 | -250 | -237 | -261 | 41 | 48 | 120 | 129 | 8 | 20 | 21 | 925 | 949 | 891 |  | -140 | -38 | -21 | -2 | -2 | -14 | 404 | 32 | 118 | 118 | 118 | 1 | 1 | 1
1167 | HG Central link | TOOT | 8 | 13 | 1 |  | 1 | 3 | -4 | 3 | 5 | 0 | -8 | 19 | -25 | 16 | 1 | 2 | 2 | 3 | 8 | 8 | 42 | 69 | 2 |  | -18 | -6 | 2 | 0 | 0 | -2 | 288 | 13 | 715 | 715 | 715 | 5 | 5 | 5
1168 | HG Ionian-Tyrrhenian Corridor | TOOT | 31 | 34 | 27 |  | 4 | 11 | -7 | 12 | 19 | 4 | -52 | -12 | -74 | 8 | 5 | 13 | 14 | 2 | 4 | 4 | 153 | 219 | 56 |  | -36 | -10 | -6 | 0 | -1 | -3 | 187 | 6 | 0 | 0 | 0 | 0 | 0 | 0
1169 | SAPEI 2 | PINT | 20 | 23 | 15 |  | 6 | 11 | -3 | 9 | 10 | 7 | -52 | -18 | -74 | -2 | 8 | 21 | 22 | 0 | -1 | -1 | 122 | 141 | 100 |  | -20 | -7 | 0 | 0 | 0 | -2 | 56 | 6 | 14 | 14 | 14 | 0 | 0 | 0
1171 | Interconnection IT-CH | PINT | 66 | 67 | 66 |  | 35 | 40 | 27 | 16 | 18 | 13 | -238 | -184 | -275 | 17 | 46 | 114 | 123 | 3 | 8 | 9 | 223 | 246 | 191 |  | -93 | -27 | -14 | -1 | -1 | -9 | 342 | 22 | 85 | 85 | 85 | 1 | 1 | 1
1182 | EHV S/S Thesprotias and its connection to the 400 kV System | Light PINT | 36 | 45 | 25 |  | 7 | 11 | 6 | 12 | 16 | 10 | -50 | -39 | -72 |  | 10 | 24 | 26 |  |  |  | 176 | 224 | 141 |  | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 1 | 1 | 1 | 0 | 0 | 0
1183 | New interconnection line 400 kV Greece - Albania | Light PINT | 6 | 7 | 5 |  | 2 | 5 | -2 | -3 | 2 | -12 | -13 | 12 | -35 |  | 3 | 6 | 7 |  |  |  | -49 | 36 | -171 |  | 2 | 1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1185 | South Coast Offshore Transmission Project | TOOT | 3 | 4 | 3 | 117 | 9 | 10 | 8 | 132 | 138 | 126 | -61 | -55 | -68 | 0 | 12 | 30 | 32 | 0 | 0 | 0 | 1880 | 1939 | 1801 | 800 | -33 | -8 | -11 | -1 | -1 | -3 | 17 | 1 | 177 | 177 | 177 | 2 | 2 | 2
1192 | HansaLink - Phase 1 | PINT | 209 | 211 | 208 |  | 66 | 70 | 62 | 26 | 28 | 25 | -452 | -424 | -479 | -46 | 87 | 217 | 233 | -9 | -22 | -24 | 372 | 386 | 358 | 2000 | -280 | -46 | -130 | -6 | -8 | -17 | -256 | -23 | 3869 | 3869 | 3869 | 47 | 47 | 47
1193 | HansaLink - Phase 2 | PINT | 50 | 56 | 44 |  | 21 | 24 | 17 | -57 | -57 | -58 | -142 | -118 | -166 | 2 | 27 | 68 | 73 | 0 | 1 | 1 | -817 | -812 | -823 | 2000 | -50 | -8 | -24 | -1 | -2 | -3 | -235 | -9 | 23 | 23 | 23 | 57 | 57 | 57
1197 | NU-Link Interconnector | PINT | 102 | 104 | 100 |  | 22 | 23 | 21 | 40 | 46 | 38 | -152 | -143 | -159 | -15 | 29 | 73 | 79 | -3 | -7 | -8 | 576 | 657 | 526 |  | -109 | -16 | -45 | -2 | -3 | -6 | -71 | -4 | 198 | 198 | 198 | 9 | 9 | 9
1200 | Hybrid interconnector Norway-Sørvest F Windfarm-Continent (DK, DE or BE) | PINT | 834 | 836 | 832 |  | 61 | 69 | 53 | 570 | 570 | 569 | -416 | -363 | -468 | 8 | 80 | 200 | 214 | 1 | 4 | 4 | 8123 | 8216 | 8029 |  | -188 | -46 | -35 | -2 | -2 | -17 | 249 | 10 | 3108 | 3108 | 3108 | 38 | 38 | 38
1201 | Reinvestment of Skagerrak 1 and 2 | PINT | 191 | 191 | 190 |  | 16 | 19 | 14 | 150 | 151 | 149 | -112 | -95 | -129 | 1 | 21 | 54 | 58 | 0 | 0 | 0 | 2129 | 2169 | 2089 |  | -94 | -6 | -70 | -3 | -5 | -3 | 208 | 4 | 296 | 296 | 296 | 0 | 0 | 0
1202 | Increased capacity Norway-Finland, Back-to-Back | PINT | 40 | 42 | 36 |  | 5 | 7 | 3 | 31 | 33 | 30 | -32 | -23 | -49 | 1 | 6 | 16 | 17 | 0 | 0 | 0 | 441 | 472 | 425 |  | -42 | -1 | -31 | -1 | -2 | -1 | 156 | 7 | 68 | 68 | 68 | 0 | 0 | 0
1203 | Offshore Wind Connection Bretagne Nord-Ouest | PINT | 6 | 10 | 2 | 236 | 23 | 25 | 22 | 290 | 300 | 277 | -155 | -147 | -167 | 99 | 30 | 75 | 80 | 19 | 47 | 51 | 4211 | 4215 | 4207 | 1200 | -45 | -7 | -22 | -1 | -1 | -3 | 905 | 45 | 157 | 157 | 157 | 2 | 2 | 2
1207 | 380kV Niederstedem-Bertrange/Bofferdange | PINT | 0 | 0 | 0 |  | 1 | 2 | 0 | 1 | 3 | -2 | -5 | -1 | -12 | -7 | 1 | 3 | 3 | -1 | -3 | -4 | 8 | 37 | -22 |  | -2 | 0 | -5 | 0 | 0 | 0 | 191 | 18 | 0 | 0 | 0 | 0 | 0 | 0
1208 | Medlink | PINT | 260 | 261 | 259 |  | 235 | 239 | 233 | -156 | -150 | -165 | -1602 | -1585 | -1629 |  | 308 | 770 | 825 |  |  |  | -2217 | -2105 | -2358 | 9016 | -771 | -214 | -105 | -9 | -11 | -75 | 511 | 47 | 0 | 0 | 0 | 0 | 0 | 0
1209 | Latvia and Lithuania cross-border strengthening project | PINT | 33 | 37 | 30 |  | 4 | 6 | 3 | 32 | 32 | 31 | -28 | -21 | -38 | 0 | 5 | 13 | 14 | 0 | 0 | 0 | 457 | 464 | 443 |  | -161 | -2 | -107 | -4 | -6 | -2 | -70 | -2 | 11 | 11 | 11 | 0 | 0 | 0
1210 | APOLLO-LINK | Light PINT | 382 | 382 | 382 |  | 129 | 133 | 123 | 200 | 215 | 186 | -880 | -837 | -905 |  | 169 | 423 | 453 |  |  |  | 2850 | 3087 | 2656 |  | -547 | -178 | -10 | -4 | -4 | -62 |  |  | 446 | 446 | 446 | 4 | 4 | 4
1211 | Baltic WindConnector (BWC) | PINT | 499 | 503 | 495 | 248 | 44 | 44 | 44 | 518 | 522 | 514 | -298 | -297 | -298 | 13 | 57 | 143 | 153 | 3 | 6 | 7 | 7363 | 7391 | 7335 | 2000 | -194 | -33 | -89 | -4 | -6 | -12 | 332 | 20 | 2808 | 2808 | 2808 | 34 | 34 | 34
1213 | Offshore hybrid Interconnector (DE-NL) | Light PINT | 162 | 168 | 158 |  | 12 | 16 | 9 | 79 | 85 | 71 | -80 | -61 | -109 |  | 15 | 38 | 41 |  |  |  | 1126 | 1190 | 1024 |  | -49 | -5 | -35 | -1 | -2 | -2 |  |  | 1368 | 1368 | 1368 | 17 | 17 | 17
1214 | Hybrid Interconnector Denmark-Germany | TOOT | 718 | 728 | 705 | 51 | 57 | 62 | 53 | 635 | 645 | 624 | -437 | -361 | -532 | 108 | 75 | 188 | 201 | 21 | 52 | 56 | 9046 | 9177 | 8909 | 2000 | -234 | -39 | -105 | -5 | -7 | -14 | 2353 | 139 | 0 | 0 | 0 | 0 | 0 | 0
1215 | Xlinks Morocco - Germany | PINT | 937 | 948 | 925 |  | 172 | 196 | 149 | -125 | -105 | -154 | -1168 | -1012 | -1332 | 282 | 224 | 562 | 601 | 54 | 136 | 145 | -1564 | -1497 | -1630 | 15200 | -655 | -99 | -319 | -13 | -20 | -37 | 4054 | 273 | 0 | 0 | 0 | 0 | 0 | 0
1216 | High-Voltage Direct Current Interconnector Project Romania-Hungary | PINT | 51 | 56 | 43 |  | 12 | 14 | 9 | -2 | 2 | -10 | -80 | -65 | -94 | 14 | 15 | 38 | 41 | 3 | 7 | 7 | -32 | 30 | -147 |  | -57 | -6 | -51 | -2 | -3 | -2 | -26 | -1 | 110 | 110 | 110 | 1 | 1 | 1
1217 | Further Development of Offshore Renewables (MOG 3) | Light PINT | 31 | 36 | 22 | 409 | 32 | 37 | 29 | 471 | 481 | 459 | -218 | -201 | -250 |  | 42 | 105 | 112 |  |  |  | 6771 | 6789 | 6752 |  | -187 | -20 | -111 | -4 | -7 | -8 |  |  | 323 | 323 | 323 | 19 | 19 | 19
1218 | Hybrid HVDC Interconnector BE-NL | Light PINT | 109 | 114 | 106 |  | 8 | 11 | 4 | 84 | 93 | 72 | -54 | -30 | -77 |  | 10 | 26 | 28 |  |  |  | 1283 | 1302 | 1264 |  | -82 | -8 | -63 | -2 | -4 | -3 |  |  | 1 | 1 | 1 | 7 | 7 | 7
1219 | Bofferdange- Bertrange | Light PINT | 23 | 27 | 15 |  | 3 | 4 | 2 | 12 | 16 | 10 | -21 | -15 | -28 |  | 4 | 10 | 11 |  |  |  | 171 | 225 | 140 |  | -2 | 0 | -5 | 0 | 0 | 0 |  |  | 467 | 467 | 467 | 6 | 6 | 6
1220 | Offshore Wind Connection Viana do Castelo | TOOT | 25 | 31 | 21 | 161 | 29 | 30 | 27 | 204 | 217 | 190 | -196 | -184 | -202 | 1 | 38 | 94 | 101 | 0 | 1 | 1 | 2897 | 3047 | 2720 | 2000 | -62 | -5 | -33 | -1 | -2 | -2 | 140 | 14 | 183 | 183 | 183 | 1 | 1 | 1
1221 | Offshore Wind Connection Leixões | TOOT | 16 | 21 | 10 | 116 | 20 | 21 | 19 | 148 | 157 | 136 | -139 | -127 | -146 | 6 | 27 | 67 | 72 | 1 | 3 | 3 | 2102 | 2206 | 1951 | 1500 | -39 | -4 | -20 | -1 | -1 | -2 | 134 | 13 | 136 | 136 | 136 | 1 | 1 | 1
1222 | Offshore Wind Connection Figueira da Foz (North) | TOOT | 27 | 33 | 23 | 159 | 29 | 30 | 27 | 204 | 217 | 190 | -196 | -184 | -202 | 4 | 38 | 94 | 101 | 1 | 2 | 2 | 2897 | 3047 | 2720 | 2000 | -62 | -5 | -33 | -1 | -2 | -2 | 121 | 13 | 183 | 183 | 183 | 1 | 1 | 1
1223 | Offshore Wind Connection Figueira da Foz (South) | TOOT | 27 | 33 | 23 | 159 | 29 | 30 | 27 | 204 | 217 | 190 | -196 | -184 | -202 | 4 | 38 | 94 | 101 | 1 | 2 | 2 | 2897 | 3047 | 2720 | 2000 | -62 | -5 | -33 | -1 | -2 | -2 | 133 | 13 | 183 | 183 | 183 | 1 | 1 | 1
1224 | Offshore Wind Connection Ericeira | TOOT | 10 | 13 | 7 | 77 | 12 | 14 | 11 | 95 | 101 | 86 | -84 | -73 | -92 | 4 | 16 | 41 | 44 | 1 | 2 | 2 | 1346 | 1422 | 1238 | 1000 | -35 | -3 | -18 | -1 | -1 | -1 | 15 | 3 | 91 | 91 | 91 | 1 | 1 | 1
1225 | Offshore Wind Connection Sines | TOOT | 13 | 18 | 7 | 119 | 20 | 21 | 19 | 148 | 157 | 136 | -139 | -127 | -146 | 3 | 27 | 67 | 72 | 1 | 2 | 2 | 2102 | 2206 | 1951 | 1500 | -39 | -4 | -20 | -1 | -1 | -2 | -63 | 0 | 137 | 137 | 137 | 1 | 1 | 1
1226 | North-South Electricity Corridor in Eastern Europe | Light PINT | 586 | 606 | 566 |  | 196 | 215 | 176 | 157 | 158 | 156 | -1331 | -1197 | -1466 |  | 256 | 640 | 686 |  |  |  | 2237 | 2247 | 2227 |  | -1104 | -307 | -240 | -14 | -17 | -108 |  |  | 667 | 667 | 667 | 8 | 8 | 8
1229 | Rhine-Main-Link | PINT | 1887 | 2170 | 1705 |  | 46 | 56 | 40 | 683 | 813 | 602 | -315 | -271 | -382 | 52 | 61 | 152 | 162 | 10 | 25 | 27 | 7 | 8 | 6 |  | -238 | -75 | -7 | -2 | -2 | -26 | 1452 | 69 | 0 | 0 | 0 | 0 | 0 | 20
1230 | TuNur Malta | PINT | 13 | 28 | 0 |  | 59 | 60 | 59 | 3 | 5 | 1 | -403 | -398 | -407 | 4 | 77 | 194 | 207 | 1 | 2 | 2 | 49 | 73 | 11 | 1400 | -51 | -15 | -5 | -1 | -1 | -5 | -8 | 4 | 0 | 0 | 0 | 0 | 0 | 0
1231 | Green Aegean Interconnector | Light PINT | 1058 | 1059 | 1057 |  | 219 | 221 | 217 | 363 | 366 | 357 | -1488 | -1475 | -1501 |  | 286 | 716 | 767 |  |  |  | 5161 | 5225 | 5122 |  | -281 | -92 | -21 | -2 | -2 | -32 |  |  | 1675 | 1675 | 1675 | 21 | 21 | 21
1233 | Laufenburg - Beznau - Breite | Light PINT | 145 | 148 | 139 |  | 33 | 38 | 24 | 142 | 146 | 139 | -222 | -160 | -257 |  | 43 | 107 | 114 |  |  |  | 2030 | 2096 | 1988 |  | -130 | -44 | 0 | -1 | -1 | -15 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1234 | 220-kV Reitdorf (AT) - Weißenbach (AT) | TOOT | 4 | 4 | 2 | 37 | 2 | 3 | 2 | 43 | 48 | 40 | -17 | -14 | -21 | -3 | 3 | 8 | 9 | -1 | -1 | -1 | 617 | 667 | 570 | 500 | -17 | -2 | -7 | 0 | 0 | -1 | -59 | -2 | 0 | 0 | 0 | 0 | 0 | 0
1235 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | PINT | 13 | 13 | 13 |  | 6 | 7 | 5 | 2 | 3 | 0 | -42 | -32 | -50 | -51 | 8 | 20 | 22 | -10 | -25 | -26 | 24 | 48 | 7 |  | 7 | -6 | 40 | 1 | 2 | -2 | -442 | -30 | 32 | 32 | 32 | 0 | 0 | 0
1236 | Power-to-Gas for Austria (P2G4A) | PINT | 1 | 2 | 0 |  | 0 | 2 | -1 | 0 | 8 | -8 | -2 | 3 | -10 | -1 | 0 | 1 | 1 | 0 | 0 | 0 | 3 | 120 | -114 |  | -2 | 1 | -5 | 0 | 0 | 0 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0
1239 | Interconnection Ukraine-Slovak Republic | Light PINT | 159 | 165 | 150 |  | 67 | 75 | 60 | 6 | 10 | 3 | -457 | -407 | -508 |  | 88 | 220 | 235 |  |  |  | 80 | 146 | 45 |  | -346 | -47 | -203 | -8 | -15 | -17
1240 | Interconnection Ukraine-Romania | Light PINT | 254 | 258 | 250 |  | 106 | 108 | 104 | 14 | 15 | 14 | -723 | -709 | -737 |  | 139 | 348 | 373 |  |  |  | 203 | 213 | 193 |  | -619 | -91 | -302 | -14 | -26 | -32

## 2030NT-EU27
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 67 | 67 | 66 | 62 | 53 | 55 | 52 | 132 | 137 | 127 | -470 | -458 | -483 | 52 | 6 | 59 | 95 | 1 | 7 | 11 | 2035 | 2129 | 1942 | 1154 | -65 | -20 | -3 | -1 | -1 | -7 | 156 | 12 | 1953 | 1953 | 1953 | 14 | 14 | 14
4 | Interconnection Portugal-Spain | TOOT | 26 | 28 | 25 |  | 13 | 17 | 10 | 21 | 23 | 19 | -116 | -90 | -146 | 23 | 1 | 15 | 23 | 0 | 3 | 5 | 327 | 366 | 284 |  | -23 | -8 | -4 | 0 | 0 | -3 | 41 | 5 | 246 | 246 | 246 | 3 | 3 | 3
16 | Biscay Gulf | TOOT | 418 | 446 | 392 |  | 130 | 134 | 125 | 225 | 257 | 201 | -1149 | -1103 | -1178 | 351 | 14 | 143 | 232 | 4 | 44 | 71 | 3453 | 3989 | 3067 |  | -539 | -160 | -59 | -6 | -6 | -56 | 2577 | 121 | 2304 | 2304 | 2304 | 76 | 76 | 76
28 | Italy-Montenegro | TOOT | 6 | 10 | 0 |  | 13 | 20 | 8 | 16 | 18 | 14 | -118 | -71 | -175 | 7 | 1 | 15 | 24 | 0 | 1 | 1 | 241 | 271 | 220 |  | -53 | -17 | -2 | 0 | 0 | -6 | 31 | 2 | 21 | 21 | 21 | 0 | 0 | 0
29 | Italy-Tunisia | TOOT | 50 | 52 | 48 |  | -112 | -103 | -121 | 22 | 24 | 21 | 1063 | 1063 | 1063 | -19 | 0 | 0 | 0 | 0 | -2 | -4 | 344 | 373 | 315 |  | -324 | -101 | -14 | -3 | -3 | -36 | -76 | -5 | 110 | 110 | 110 | 2 | 2 | 2
33 | Central Northern Italy | TOOT | 6 | 12 | 1 |  | 2 | 4 | 1 | 5 | 8 | 2 | -19 | -8 | -36 | -6 | 0 | 2 | 4 | 0 | -1 | -1 | 71 | 118 | 34 |  | -30 | -3 | -13 | -1 | -1 | -1 | 86 | 0 | 17 | 17 | 17 | 0 | 0 | 0
35 | CZ Southwest-east corridor | TOOT | 78 | 79 | 78 |  | 56 | 58 | 54 | 26 | 27 | 25 | -498 | -479 | -511 | 29 | 6 | 62 | 100 | 0 | 4 | 6 | 394 | 414 | 378 |  | -207 | -62 | -14 | -2 | -2 | -22 | 274 | 13 | 178 | 178 | 178 | 3 | 3 | 3
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 22 | 25 | 18 |  | 8 | 10 | 5 | 15 | 17 | 13 | -68 | -42 | -87 |  | 1 | 8 | 14 |  |  |  | 236 | 260 | 202 |  | -39 | -9 | -13 | -1 | -1 | -3 |  |  | 11 | 11 | 11 | 0 | 0 | 0
47 | Westtirol (AT) - Vöhringen (DE) | TOOT | 35 | 40 | 32 |  | 17 | 21 | 15 | 26 | 28 | 24 | -153 | -130 | -184 | 27 | 2 | 19 | 31 | 0 | 3 | 5 | 405 | 422 | 375 |  | -65 | -19 | -6 | -1 | -1 | -7 | 147 | 9 | 192 | 192 | 192 | 3 | 3 | 3
81 | North South Interconnector | TOOT | 4 | 7 | 1 |  | -1 | 1 | -4 | 0 | 8 | -9 | 19 | 32 | 11 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 129 | -140 |  | -8 | -1 | -7 | 0 | 0 | -1 | -40 | 0 | 153 | 153 | 153 | 3 | 3 | 3
85 | Integration of RES in Alentejo | TOOT | 0 | 1 | 0 | 12 | 1 | 3 | -2 | 20 | 20 | 19 | -9 | 18 | -26 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 302 | 311 | 293 | 442 | -4 | -2 | -1 | 0 | 0 | -1 | 19 | 1 | 0 | 0 | 0 | 0 | 0 | 0
94 | GerPol Improvements | TOOT | 140 | 143 | 137 |  | 76 | 82 | 66 | 36 | 37 | 35 | -668 | -585 | -726 | 76 | 8 | 83 | 135 | 1 | 9 | 15 | 555 | 565 | 538 |  | -385 | -51 | -259 | -10 | -17 | -18 | 464 | 26 | 477 | 477 | 477 | 8 | 8 | 8
107 | Celtic Interconnector | TOOT | 243 | 246 | 241 |  | 53 | 57 | 49 | 194 | 197 | 190 | -464 | -436 | -506 | 90 | 6 | 58 | 94 | 1 | 11 | 18 | 2981 | 3011 | 2954 |  | -110 | -39 | -36 | 0 | 0 | -14 | 866 | 32 | 829 | 829 | 829 | 27 | 27 | 27
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 46 | 51 | 42 |  | 10 | 16 | 4 | 44 | 46 | 43 | -86 | -33 | -137 | 6 | 1 | 11 | 17 | 0 | 1 | 1 | 678 | 698 | 657 |  | -107 | -1 | -79 | -3 | -5 | -1 | -1 | 2 | 602 | 602 | 602 | 8 | 8 | 8
120 | Princess Elisabeth Island (MOG 2) | TOOT | 309 | 336 | 291 | 559 | 239 | 245 | 236 | 853 | 855 | 851 | -2109 | -2077 | -2161 | 129 | 27 | 263 | 425 | 2 | 16 | 26 | 13254 | 13500 | 12957 | 3600 | -740 | -207 | -113 | -9 | -11 | -73 | 619 | 40 | 1103 | 1103 | 1103 | 15 | 15 | 15
121 | Nautilus: multi-purpose interconnector Belgium - UK | TOOT | 100 | 104 | 97 |  | 70 | 71 | 69 | 11 | 15 | 9 | -615 | -608 | -625 | 35 | 8 | 77 | 124 | 0 | 4 | 7 | 171 | 236 | 132 |  | -221 | -60 | -38 | -3 | -4 | -21 | 150 | 10 | 621 | 621 | 621 | 8 | 8 | 8
124 | Ekhyddan-Nybro-Hemsjö | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 35 | 38 | 33 |  | 20 | 24 | 16 | 2 | 4 | 1 | -175 | -139 | -209 | 20 | 2 | 22 | 35 | 0 | 3 | 4 | 32 | 66 | 11 |  | -210 | -20 | -109 | -5 | -6 | -8 | 162 | 10 | 102 | 102 | 102 | 0 | 0 | 0
127 | Central Southern Italy | TOOT | 29 | 34 | 25 |  | 13 | 14 | 12 | 12 | 14 | 11 | -111 | -102 | -124 | 36 | 1 | 14 | 22 | 0 | 5 | 7 | 190 | 216 | 161 |  | -35 | -12 | -3 | 0 | 0 | -4 | 160 | 10 | 349 | 349 | 349 | 0 | 0 | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 233 | 299 | 176 |  | 90 | 151 | 41 | 96 | 124 | 71 | -793 | -365 | -1330 | 27 | 10 | 99 | 160 | 0 | 3 | 5 | 1 | 1 | 1 |  | -379 | -98 | -55 | -4 | -5 | -35 | 0 | -9
132 | HVDC Line A-North | TOOT | 812 | 932 | 721 |  | 121 | 196 | 27 | 413 | 476 | 363 | -1071 | -239 | -1461 | 52 | 13 | 133 | 216 | 1 | 6 | 10 | 4 | 5 | 4 |  | -466 | -135 | -38 | -5 | -5 | -48 | 0 | -18
138 | Black Sea Corridor | TOOT | 14 | 23 | 6 |  | -6 | 12 | -20 | -2 | 0 | -3 | 123 | 175 | 83 | 15 | 0 | 0 | 0 | 0 | 2 | 3 | -29 | 6 | -52 |  | -22 | -7 | -5 | 0 | 0 | -2 | 55 | 4 | 275 | 275 | 275 | 0 | 0 | 0
144 | Mid Continental East corridor | TOOT | 13 | 21 | 8 |  | 7 | 10 | 2 | -1 | 2 | -3 | -61 | -16 | -88 | 32 | 1 | 8 | 12 | 0 | 4 | 6 | -11 | 27 | -44 |  | -18 | -3 | -3 | 0 | 0 | -1 | 115 | 9 | 459 | 459 | 459 | 7 | 7 | 7
150 | Italy-Slovenia | TOOT | 6 | 10 | 4 |  | 9 | 10 | 8 | 1 | 7 | -4 | -79 | -68 | -91 | 29 | 1 | 10 | 16 | 0 | 4 | 6 | 16 | 108 | -54 |  | -25 | -6 | -7 | 0 | -1 | -2 | 107 | 8 | 86 | 86 | 86 | 1 | 1 | 1
153 | France-Alderney-Britain | TOOT | 86 | 89 | 83 |  | 78 | 79 | 77 | 23 | 25 | 21 | -690 | -680 | -699 | 119 | 9 | 86 | 139 | 1 | 15 | 24 | 361 | 383 | 321 |  | -197 | -62 | -10 | -2 | -2 | -22 | 685 | 39 | 1419 | 1419 | 1419 | 29 | 29 | 29
170 | Baltic States Synchronization with Continental Europe | TOOT | 269 | 277 | 261 |  | 188 | 195 | 178 | 130 | 132 | 128 | -1661 | -1573 | -1723 | -198 | 21 | 207 | 335 | -3 | -25 | -40 | 2000 | 2032 | 1962 |  | -60 | -110 | -113 | -3 | -15 | -31 | -1125 | -65 | 596 | 596 | 596 | 10 | 10 | 10
174 | Greenconnector | TOOT | 83 | 88 | 78 |  | 85 | 91 | 81 | 0 | 4 | -2 | -749 | -714 | -802 | 73 | 9 | 93 | 151 | 1 | 9 | 15 | -2 | 61 | -38 |  | -353 | -101 | -49 | -4 | -5 | -36 | 433 | 25 | 66 | 66 | 66 | 1 | 1 | 1
176 | Hansa PowerBridge I | TOOT | 145 | 151 | 141 |  | 69 | 75 | 60 | 23 | 27 | 21 | -607 | -533 | -661 | 51 | 8 | 76 | 122 | 1 | 6 | 10 | 358 | 414 | 329 |  | -142 | -68 | -26 | 0 | 0 | -23 | 225 | 17 | 265 | 265 | 265 | 4 | 4 | 4
187 | St. Peter (AT) - Pleinting (DE) | TOOT | 244 | 248 | 239 |  | 99 | 114 | 83 | 124 | 131 | 120 | -876 | -729 | -1004 | 18 | 11 | 109 | 177 | 0 | 2 | 4 | 1905 | 1997 | 1840 |  | -367 | -95 | -92 | -5 | -7 | -34 | 73 | 4 | 1643 | 1643 | 1643 | 25 | 25 | 25
200 | CZ Northwest-South corridor | TOOT | 78 | 79 | 78 |  | 56 | 58 | 54 | 26 | 27 | 25 | -498 | -479 | -511 | 3 | 6 | 62 | 100 | 0 | 0 | 1 | 394 | 414 | 378 |  | -207 | -62 | -14 | -2 | -2 | -22 | 184 | 6 | 183 | 183 | 183 | 3 | 3 | 3
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 25 | 34 | 19 |  | 12 | 13 | 10 | 0 | 2 | -1 | -102 | -89 | -113 | 3 | 1 | 13 | 21 | 0 | 0 | 1 | 0 | 23 | -13 |  | -54 | -12 | -14 | -1 | -1 | -4 | 35 | 2 | 28 | 28 | 28 | 0 | 0 | 0
219 | Great Sea Interconnector | TOOT | 157 | 165 | 148 |  | -130 | -121 | -140 | 2 | 4 | 0 | 1219 | 1235 | 1204 | 242 | 0 | 0 | 0 | 3 | 30 | 49 | 27 | 59 | -3 |  | -429 | -143 | -1 | -3 | -3 | -50 | 592 | 60 | 150 | 150 | 150 | 1 | 1 | 1
225 | 2nd interconnector Belgium - Germany | light PINT | 60 | 68 | 52 |  | 24 | 26 | 21 | 50 | 57 | 41 | -213 | -188 | -231 | 125 | 3 | 27 | 43 | 2 | 16 | 25 | 767 | 872 | 625 |  | -83 | -22 | -21 | -1 | -2 | -8 | 617 | 38 | 46 | 46 | 46 | 1 | 1 | 1
227 | Transbalkan Corridor | TOOT | 4 | 7 | 0 |  | 3 | 5 | 1 | -2 | -1 | -4 | -24 | -10 | -41 | 0 | 0 | 3 | 5 | 0 | 0 | 0 | -36 | -22 | -58 |  | -10 | -2 | -4 | 0 | 0 | -1 | -1 | 0 | 102 | 102 | 102 | 1 | 1 | 1
228 | Muhlbach - Eichstetten | TOOT | 26 | 32 | 19 |  | 9 | 10 | 8 | 16 | 20 | 12 | -82 | -74 | -92 | 24 | 1 | 10 | 16 | 0 | 3 | 5 | 250 | 310 | 182 |  | -32 | -8 | -7 | 0 | -1 | -3 | 166 | 8 | 268 | 268 | 268 | 9 | 9 | 9
231 | Beznau - Tiengen | TOOT | 16 | 19 | 13 |  | 18 | 24 | 14 | 35 | 39 | 32 | -160 | -121 | -215 | 56 | 2 | 20 | 32 | 1 | 7 | 11 | 542 | 600 | 482 |  | -81 | -23 | -13 | -1 | -1 | -8 | 102 | 14 | 24 | 24 | 24 | 0 | 0 | 0
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 845 | 1049 | 715 |  | 163 | 206 | 135 | 385 | 488 | 316 | -1441 | -1192 | -1278 | 80 | 18 | 180 | 291 | 1 | 10 | 16 | 4 | 5 | 3 |  | -657 | -180 | -74 | -7 | -8 | -64 | -1 | -32
239 | Fenno-Skan 3 | Light PINT | 27 | 31 | 23 |  | 9 | 11 | 5 | 20 | 22 | 18 | -80 | -47 | -99 |  | 1 | 10 | 16 |  |  |  | 304 | 334 | 274 |  | -75 | -8 | -37 | -2 | -2 | -3 |  |  | 102 | 102 | 102 | 1 | 1 | 1
243 | New 400 kV interconnection line between Serbia and Croatia | Light PINT | 7 | 11 | 4 |  | 2 | 3 | 1 | 4 | 6 | 2 | -20 | -6 | -29 |  | 0 | 3 | 4 |  |  |  | 56 | 91 | 23 |  | -7 | -2 | -1 | 0 | 0 | -1 |  |  | 4 | 4 | 4 | 0 | 0 | 0
244 | Vigy - Uchtelfangen area | TOOT | 143 | 144 | 142 |  | 58 | 58 | 57 | 92 | 93 | 91 | -510 | -506 | -514 | 154 | 6 | 64 | 103 | 2 | 19 | 31 | 1415 | 1443 | 1386 |  | -254 | -54 | -101 | -5 | -7 | -19 | 968 | 50 | 1462 | 1462 | 1462 | 51 | 51 | 51
247 | AQUIND Interconnector | TOOT | 130 | 134 | 126 |  | 123 | 126 | 122 | 35 | 38 | 31 | -1084 | -1072 | -1107 | 125 | 14 | 135 | 219 | 2 | 16 | 25 | 533 | 574 | 477 |  | -302 | -96 | -3 | -2 | -3 | -34 | 611 | 38 | 2231 | 2231 | 2231 | 40 | 40 | 40
250 | Merchant line Castasegna (CH) - Mese (IT) | TOOT | 15 | 24 | 8 |  | 14 | 15 | 13 | -2 | 0 | -3 | -122 | -114 | -130 | 23 | 2 | 15 | 25 | 0 | 3 | 5 | -26 | -2 | -48 |  | -47 | -16 | -2 | 0 | 0 | -5 | 114 | 7 | 5 | 5 | 5 | 0 | 0 | 0
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 168 | 196 | 151 |  | 32 | 35 | 29 | 70 | 81 | 62 | -284 | -254 | -278 | 49 | 4 | 35 | 57 | 1 | 6 | 10 | 1 | 1 | 1 |  | -140 | -35 | -23 | -2 | -2 | -13 | 0 | -18 | 0 | 0 | 0 | 0 | 0
259 | HU-RO | TOOT | 10 | 11 | 7 |  | 8 | 11 | 4 | 3 | 3 | 2 | -67 | -34 | -96 | 28 | 1 | 8 | 13 | 0 | 4 | 6 | 44 | 52 | 35 |  | -25 | -7 | -2 | 0 | 0 | -3 | 96 | 8 | 41 | 41 | 41 | 1 | 1 | 1
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | TOOT | 102 | 104 | 100 |  | 89 | 91 | 85 | 55 | 61 | 46 | -784 | -752 | -804 | -167 | 10 | 98 | 158 | -2 | -21 | -34 | 842 | 950 | 708 |  | -304 | -79 | -68 | -4 | -6 | -28 | -904 | -58 | 950 | 950 | 950 | 30 | 30 | 30
267 | Hansa PowerBridge II | Light PINT | 123 | 129 | 117 |  | 59 | 67 | 52 | 22 | 26 | 20 | -522 | -462 | -587 |  | 7 | 65 | 105 |  |  |  | 344 | 396 | 303 |  | -77 | -61 | -164 | -5 | -7 | -19 |  |  | 55 | 55 | 55 | 1 | 1 | 1
270 | FR-ES project -Aragón-Atlantic Pyrenees | TOOT | 214 | 222 | 207 |  | 72 | 84 | 57 | 132 | 150 | 115 | -638 | -504 | -744 | 228 | 8 | 79 | 129 | 3 | 28 | 46 | 2031 | 2322 | 1749 |  | -303 | -90 | -34 | -3 | -4 | -32 | 1534 | 78 | 584 | 584 | 584 | 19 | 19 | 19
276 | FR-ES project -Navarra-Landes | PINT | 214 | 222 | 207 |  | 72 | 84 | 57 | 132 | 150 | 115 | -638 | -504 | -744 | 226 | 8 | 79 | 129 | 3 | 28 | 46 | 2031 | 2322 | 1749 |  | -303 | -90 | -34 | -3 | -4 | -32 | 1546 | 78 | 581 | 581 | 581 | 19 | 19 | 19
280 | FR-BE: Lonny-Achene-Gramme | TOOT | 52 | 55 | 48 |  | 21 | 23 | 20 | 27 | 29 | 24 | -185 | -176 | -199 | 62 | 2 | 23 | 37 | 1 | 8 | 13 | 415 | 439 | 368 |  | -79 | -19 | -25 | -1 | -2 | -7 | 382 | 21 | 0 | 0 | 0 | 0 | 0 | 0
283 | TuNur Italy | PINT | 51 | 63 | 39 | 0 | 342 | 354 | 332 | -24 | -23 | -25 | -3019 | -2932 | -3120 | 103 | 38 | 376 | 609 | 1 | 13 | 21 | -368 | -353 | -383 | 5000 | -1076 | -340 | -36 | -9 | -9 | -119 | 382 | 27 | 11 | 11 | 11 | 0 | 0 | 0
285 | GridLink | TOOT | 86 | 89 | 83 |  | 78 | 79 | 77 | 23 | 25 | 21 | -690 | -680 | -699 | 100 | 9 | 86 | 139 | 1 | 12 | 20 | 361 | 383 | 321 |  | -197 | -62 | -10 | -2 | -2 | -22 | 555 | 33 | 1425 | 1425 | 1425 | 29 | 29 | 29
297 | BRABO III | TOOT | 33 | 37 | 30 |  | 8 | 11 | 6 | 48 | 53 | 40 | -71 | -49 | -96 | 16 | 1 | 9 | 14 | 0 | 2 | 3 | 740 | 817 | 602 |  | -10 | -4 | -1 | 0 | 0 | -1 | 77 | 4 | 86 | 86 | 86 | 1 | 1 | 1
299 | SACOI 3 | TOOT | 119 | 132 | 102 |  | 55 | 58 | 49 | 6 | 9 | 2 | -483 | -428 | -514 | 23 | 6 | 60 | 97 | 0 | 3 | 5 | 95 | 132 | 30 |  | -1924 | -15 | -1309 | -50 | -70 | -14 | 78 | 6 | 297 | 297 | 297 | 7 | 7 | 7
309 | NeuConnect | TOOT | 98 | 102 | 94 |  | 131 | 136 | 125 | 39 | 44 | 35 | -1159 | -1101 | -1203 | 137 | 15 | 144 | 234 | 2 | 17 | 28 | 607 | 677 | 535 |  | -440 | -116 | -95 | -6 | -8 | -41 | 671 | 42 | 744 | 744 | 744 | 11 | 11 | 11
312 | St. Peter (AT) - Tauern (AT) | TOOT | 155 | 159 | 150 |  | 73 | 82 | 61 | 94 | 98 | 92 | -644 | -542 | -725 | -102 | 8 | 80 | 130 | -1 | -13 | -20 | 1445 | 1493 | 1407 |  | -281 | -73 | -68 | -4 | -5 | -26 | -545 | -32 | 1179 | 1179 | 1179 | 19 | 19 | 19
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 95 | 97 | 92 |  | 47 | 53 | 40 | 63 | 65 | 62 | -415 | -349 | -470 | 102 | 5 | 52 | 84 | 1 | 13 | 21 | 969 | 985 | 945 |  | -176 | -47 | -34 | -2 | -3 | -17 | 106 | 31 | 686 | 686 | 686 | 11 | 11 | 11
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 3 | 6 | 0 |  | -1 | 1 | -4 | -2 | -1 | -3 | 8 | 32 | -13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | -32 | -21 | -48 |  | -4 | 0 | -2 | 0 | 0 | 0 | 6 | 1 | 6 | 6 | 6 | 0 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 1 | 2 | 0 |  | 0 | 2 | -2 | -2 | -1 | -4 | -4 | 14 | -17 | 5 | 0 | 0 | 1 | 0 | 1 | 1 | -30 | -8 | -55 |  | -7 | -2 | -3 | 0 | 0 | -1 | 15 | 1 | 9 | 9 | 9 | 0 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | TOOT | 112 | 123 | 101 |  | 63 | 67 | 60 | 21 | 24 | 15 | -553 | -526 | -595 | 64 | 7 | 69 | 111 | 1 | 8 | 13 | 316 | 360 | 235 |  | -226 | -64 | -36 | -3 | -3 | -23 | 352 | 21 | 29 | 29 | 29 | 0 | 0 | 0
328 | Interconnector DE-LUX | TOOT | 0 | 0 | 0 |  | -2 | 0 | -4 | -1 | 2 | -3 | 15 | 33 | -2 | -86 | 0 | 0 | 0 | -1 | -11 | -17 | -13 | 28 | -41 |  | -2 | -2 | -2 | 0 | 0 | -1 | -217 | -23 | 0 | 0 | 0 | 0 | 0 | 0
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 352 | 370 | 325 |  | 126 | 132 | 117 | 274 | 288 | 253 | -2831 | -2978 | -2613 | -20 | 357 | 674 | 892 | 0 | -2 | -4 | 5776 | 5371 | 6046 | 0 | -3728 | -156 | -5563 | -151 | -414 | -61 | 692 | 15 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | TOOT | 27 | 32 | 20 |  | 8 | 11 | 6 | 10 | 13 | 8 | -67 | -49 | -100 | 27 | 1 | 8 | 14 | 0 | 3 | 5 | 154 | 199 | 128 |  | -19 | -2 | -19 | -1 | -1 | -1 | 104 | 7 | 18 | 18 | 18 | 0 | 0 | 0
335 | North Sea Wind Power Hub | Light PINT | 1545 | 1600 | 1490 | 1656 | 730 | 739 | 720 | 3498 | 3554 | 3441 | -6434 | -6349 | -6520 |  | 81 | 802 | 1297 |  |  |  | 53953 | 54390 | 53516 | 14000 | -2275 | -620 | -423 | -28 | -37 | -218 |  |  | 473 | 473 | 473 | 8 | 8 | 8
338 | Adriatic HVDC link | TOOT | 17 | 27 | 9 |  | 6 | 8 | 5 | 13 | 19 | 9 | -55 | -47 | -70 | 22 | 1 | 7 | 11 | 0 | 3 | 4 | 199 | 298 | 131 |  | -21 | -7 | -2 | 0 | 0 | -2 | 214 | 8 | 463 | 463 | 463 | 0 | 0 | 0
339 | Tyrrhenian link | TOOT | 102 | 105 | 98 |  | 47 | 50 | 43 | 41 | 42 | 40 | -416 | -376 | -437 | 86 | 5 | 52 | 84 | 1 | 11 | 17 | 638 | 661 | 607 |  | -153 | -48 | -4 | -1 | -1 | -17 | 375 | 24 | 1473 | 1473 | 1473 | 0 | 0 | 0
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 112 | 140 | 67 |  | 40 | 50 | 24 | 87 | 109 | 52 | -1213 | -1429 | -745 | -73 | 153 | 289 | 382 | -1 | -9 | -15 | 2030 | 1235 | 2599 | 0 | -2007 | -17 | -4309 | -45 | -277 | -16 | 368 | -4 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | TOOT | 3 | 6 | 0 |  | 0 | 3 | -2 | -2 | 1 | -5 | -3 | 21 | -22 | 24 | 0 | 0 | 1 | 0 | 3 | 5 | -26 | 16 | -77 |  | -10 | -3 | -1 | 0 | 0 | -1 | 3 | 5 | 278 | 278 | 278 | 4 | 4 | 4
342 | Central Balkan Corridor | TOOT | 10 | 12 | 6 |  | 3 | 6 | 0 | 3 | 4 | 3 | -19 | -2 | -49 | 20 | 0 | 3 | 5 | 0 | 2 | 4 | 51 | 57 | 42 |  | -8 | -3 | -1 | 0 | 0 | -1 | 67 | 6 | 17 | 17 | 17 | 0 | 0 | 0
343 | CSE1 New | TOOT | 5 | 8 | 3 |  | 3 | 5 | 2 | 2 | 4 | 0 | -26 | -15 | -42 | -11 | 0 | 3 | 5 | 0 | -1 | -2 | 30 | 70 | 5 |  | -8 | -2 | -4 | 0 | 0 | -1 | -35 | -2 | 2 | 2 | 2 | 0 | 0 | 0
346 | ZuidWest380 NL Oost | TOOT | 3 | 4 | 3 |  | 2 | 3 | 1 | 2 | 2 | 2 | -15 | -5 | -24 | -16 | 0 | 2 | 3 | 0 | -2 | -3 | 36 | 36 | 34 |  | -7 | -2 | -2 | 0 | 0 | -1 | -89 | -5 | 0 | 0 | 0 | 0 | 0 | 0
349 | MaresConnect | TOOT | 59 | 63 | 56 |  | 12 | 16 | 8 | 92 | 96 | 90 | -106 | -71 | -141 | 3 | 1 | 13 | 21 | 0 | 0 | 1 | 1412 | 1461 | 1377 |  | 0 | -5 | -35 | -1 | -1 | -2 | 61 | 1 | 412 | 412 | 412 | 7 | 7 | 7
350 | South Balkan Corridor | TOOT | 0 | 0 | 0 |  | 8 | 9 | 8 | 2 | 9 | -2 | 41 | 126 | -76 | 26 | 1 | 9 | 15 | 0 | 3 | 5 | 28 | 142 | -33 |  | -40 | -8 | -6 | -1 | -1 | -3 | 2 | 6 | 10 | 10 | 10 | 0 | 0 | 0
375 | Lienz (AT) - Veneto region (IT) 220 kV | TOOT | 84 | 101 | 71 |  | 40 | 42 | 37 | 11 | 11 | 10 | -353 | -323 | -370 | 25 | 4 | 44 | 71 | 0 | 3 | 5 | 164 | 177 | 152 |  | -148 | -42 | -24 | -2 | -2 | -15 | 135 | 8 | 32 | 32 | 32 | 0 | 0 | 0
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | Light PINT | 4 | 5 | 3 |  | 1 | 2 | 1 | 2 | 4 | 1 | -8 | 5 | -15 |  | 0 | 1 | 2 |  |  |  | 32 | 64 | 15 |  | -9 | -1 | -8 | 0 | 0 | -1 |  |  | 1 | 1 | 1 | 0 | 0 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | TOOT | 27 | 31 | 22 |  | 5 | 6 | 4 | 38 | 43 | 30 | -47 | -38 | -57 | 5 | 1 | 6 | 9 | 0 | 1 | 1 | 582 | 655 | 457 |  | -19 | -5 | -5 | 0 | 0 | -2 | 37 | 1 | 19 | 19 | 19 | 0 | 0 | 0
378 | Transformer Gatica | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 356 | 457 | 290 |  | 44 | 95 | -64 | 179 | 229 | 147 | -655 | -538 | -568 | -8 | 5 | 49 | 79 | 0 | -1 | -2 | 2 | 2 | 1 |  | -291 | -82 | -28 | -3 | -3 | -29 | -128 | -4 | 0 | 0 | 0 | 0 | 0
1039 | SE North-south long-term reinforcements | PINT | 27 | 29 | 25 |  | 14 | 16 | 12 | 2 | 3 | 1 | -124 | -105 | -143 |  | 2 | 15 | 25 |  |  |  | 35 | 49 | 19 |  | -142 | -15 | -70 | -3 | -4 | -6 |  |  | 95 | 95 | 95 | 0 | 0 | 0
1040 | LirIC | TOOT | 62 | 64 | 60 |  | 10 | 12 | 9 | 28 | 30 | 26 | -89 | -76 | -106 | 4 | 1 | 11 | 18 | 0 | 0 | 1 | 433 | 458 | 407 |  | -10 | -10 | -34 | -1 | -1 | -3 | 163 | 1 | 32 | 32 | 32 | 1 | 1 | 1
1041 | GREGY Green Energy Interconnector | TOOT | 117 | 166 | 68 |  | -34 | 293 | -295 | 0 | 3 | -2 | 2596 | 2605 | 2588 | 323 | 0 | 0 | 0 | 4 | 40 | 65 | 0 | 50 | -34 |  | -317 | -98 | -21 | -3 | -3 | -34 | 1056 | 85 | 118 | 118 | 118 | 2 | 2 | 2
1046 | Finnish North-South reinforcement | PINT | 391 | 391 | 391 |  | 49 | 49 | 49 | 480 | 480 | 480 | 436 | 436 | 436 | -7 | 5 | 54 | 88 | 0 | -1 | -1 | 7505 | 7505 | 7505 |  | -2 | 0 | -2 | 0 | 0 | 0 | -495 | -25 | 0 | 0 | 0 | 0 | 0 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 16 | 22 | 11 |  | 0 | 8 | -5 | 2 | 3 | 1 | 17 | 48 | -20 | -5 | 0 | 0 | 0 | 0 | -1 | -1 | 35 | 45 | 23 |  | -16 | -6 | -3 | 0 | 0 | -2 | -33 | -2 | 3 | 3 | 3 | 0 | 0 | 0
1049 | Cronos Energy Ltd | PINT | 91 | 108 | 72 |  | 108 | 110 | 106 | -2 | -1 | -3 | -949 | -933 | -972 | -10 | 12 | 118 | 191 | 0 | -1 | -2 | -27 | -13 | -47 |  | -314 | -91 | -37 | -3 | -4 | -32 | -963 | -29 | 162 | 162 | 162 | 2 | 2 | 2
1050 | Tarchon Energy Ltd | TOOT | 95 | 110 | 78 |  | 126 | 128 | 125 | 42 | 44 | 38 | -1113 | -1102 | -1130 | 104 | 14 | 139 | 224 | 1 | 13 | 21 | 642 | 687 | 572 |  | -390 | -106 | -72 | -5 | -7 | -37 | 529 | 33 | 226 | 226 | 226 | 2 | 2 | 2
1052 | Lienz (AT) - Malta (AT) - Obersielach (AT) | TOOT | 304 | 339 | 270 | 165 | 189 | 203 | 175 | 234 | 241 | 227 | -1668 | -1545 | -1792 | 56 | 21 | 208 | 336 | 1 | 7 | 11 | 3611 | 3688 | 3534 | 2000 | -683 | -189 | -125 | -8 | -11 | -66 | 330 | 20 | 45 | 45 | 45 | 1 | 1 | 1
1054 | 220-kV Westtirol (AT) - Zell/Ziller (AT) | TOOT | 32 | 34 | 30 |  | 17 | 18 | 16 | 24 | 27 | 22 | -148 | -138 | -161 | 40 | 2 | 18 | 30 | 1 | 5 | 8 | 374 | 417 | 331 |  | -66 | -18 | -10 | -1 | -1 | -6 | 189 | 13 | 194 | 194 | 194 | 3 | 3 | 3
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 100 | 103 | 98 |  | -116 | -105 | -127 | 0 | 1 | -2 | 924 | 929 | 919 | 555 | 0 | 0 | 0 | 7 | 69 | 112 | 3 | 22 | -34 |  | -388 | -126 | -8 | -3 | -3 | -44 | 1653 | 143 | 89 | 89 | 89 | 0 | 0 | 0
1058 | HVDC Interconnector DE-CH | Light PINT | 31 | 32 | 29 |  | 40 | 45 | 35 | 55 | 59 | 51 | -350 | -308 | -393 |  | 4 | 44 | 70 |  |  |  | 849 | 913 | 777 |  | -132 | -39 | -22 | -2 | -2 | -13 |  |  | 100 | 100 | 100 | 2 | 2 | 2
1059 | Southern Italy | TOOT | 7 | 10 | 4 |  | 5 | 6 | 4 | 7 | 11 | 5 | -47 | -33 | -55 | 13 | 1 | 6 | 9 | 0 | 2 | 3 | 112 | 172 | 71 |  | -19 | -6 | -1 | 0 | 0 | -2 | 125 | 5 | 210 | 210 | 210 | 0 | 0 | 0
1066 | Bulgaria - Turkey | Light PINT | 76 | 82 | 71 |  | -236 | -227 | -244 | 2 | 3 | 0 | 2005 | 2151 | 1859 |  | 0 | 0 | 0 |  |  |  | 30 | 47 | 5 |  | -754 | -237 | -26 | -6 | -7 | -83 |  |  | 135 | 135 | 135 | 2 | 2 | 2
1067 | New AC 400 kV interconnection line Greece - Turkey | Light PINT | 44 | 48 | 39 |  | -111 | -107 | -115 | 1 | 2 | 1 | 958 | 1015 | 915 |  | 0 | 0 | 0 |  |  |  | 15 | 28 | 8 |  | -365 | -114 | -12 | -3 | -3 | -40 |  |  | 61 | 61 | 61 | 1 | 1 | 1
1068 | LaSGo Link | PINT | 40 | 46 | 37 |  | 24 | 26 | 20 | 21 | 22 | 20 | -209 | -175 | -229 | 8 | 3 | 26 | 42 | 0 | 1 | 2 | 328 | 341 | 310 |  | -670 | -15 | -420 | -17 | -23 | -11 | 117 | 5 | 11 | 11 | 11 | 0 | 0 | 0
1074 | Pannonian Corridor | TOOT | 8 | 10 | 6 |  | 5 | 6 | 3 | 2 | 2 | 1 | -40 | -28 | -52 | 10 | 1 | 5 | 8 | 0 | 1 | 2 | 26 | 37 | 15 |  | -7 | -4 | -1 | 0 | 0 | -1 | 31 | 3 | 21 | 21 | 21 | 0 | 0 | 0
1085 | Malta-Italy Cable Link No.2 | TOOT | 27 | 33 | 18 |  | 17 | 18 | 16 | 4 | 6 | 2 | -146 | -140 | -159 | 10 | 2 | 18 | 29 | 0 | 1 | 2 | 67 | 92 | 25 |  | -52 | -17 | -3 | 0 | 0 | -6 | 30 | 3 | 10 | 10 | 10 | 0 | 0 | 0
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 8 | 14 | 3 | 84 | 14 | 16 | 12 | 134 | 136 | 129 | -126 | -110 | -140 | 0 | 2 | 16 | 25 | 0 | 0 | 0 | 2055 | 2121 | 1964 | 700 | -379 | -7 | -247 | -10 | -13 | -6 | 76 | 3 | 2 | 2 | 2 | 0 | 0 | 0
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | TOOT | 27 | 38 | 17 | 70 | 14 | 17 | 11 | 134 | 136 | 132 | -124 | -96 | -152 | 2 | 2 | 15 | 25 | 0 | 0 | 0 | 2059 | 2075 | 2045 | 1000 | -194 | -6 | -119 | -5 | -6 | -4 | 41 | 3 | 68 | 68 | 68 | 1 | 1 | 1
1092 | TritonLink: offshore hybrid HVDC interconnector Belgium – Denmark | TOOT | 584 | 588 | 580 | 412 | 210 | 216 | 206 | 1079 | 1107 | 1055 | -1854 | -1814 | -1901 | 48 | 23 | 231 | 374 | 1 | 6 | 10 | 16576 | 16940 | 16072 | 4000 | -624 | -174 | -104 | -8 | -10 | -61 | 131 | 14 | 360 | 360 | 360 | 6 | 6 | 6
1094 | Estlink 3 | TOOT | 40 | 46 | 36 |  | 36 | 39 | 34 | 4 | 5 | 2 | -320 | -300 | -342 | 17 | 4 | 40 | 65 | 0 | 2 | 3 | 62 | 79 | 30 |  | -1591 | -14 | -1024 | -40 | -55 | -20 | 132 | 6 | 7 | 7 | 7 | 0 | 0 | 0
1095 | Aurora line 2 (4th AC Finland-Sweden north) | TOOT | 34 | 37 | 31 |  | 6 | 8 | 5 | 31 | 33 | 29 | -55 | -41 | -72 | 3 | 1 | 7 | 11 | 0 | 0 | 1 | 476 | 520 | 439 |  | -71 | -3 | -48 | -2 | -3 | -2 | 0 | 1 | 37 | 37 | 37 | 0 | 0 | 0
1096 | Beznau - Mettlen | Light TOOT | 17 | 19 | 12 |  | 29 | 35 | 21 | 41 | 42 | 40 | -257 | -184 | -310 |  | 3 | 32 | 52 |  |  |  | 631 | 642 | 625 |  | -111 | -37 | -4 | -1 | -1 | -13 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1097 | Upgrade to Konti-Skan | PINT | 124 | 126 | 120 |  | 44 | 51 | 36 | 34 | 38 | 30 | -388 | -319 | -447 | 64 | 5 | 48 | 78 | 1 | 8 | 13 | 523 | 585 | 452 |  | -119 | -45 | -6 | -1 | -1 | -15 | 271 | 12 | 75 | 75 | 75 | 1 | 1 | 1
1098 | Offshore Wind LT 2 | TOOT | 9 | 11 | 7 | 45 | 11 | 12 | 10 | 72 | 74 | 71 | -99 | -91 | -104 | 19 | 1 | 12 | 20 | 0 | 2 | 4 | 1113 | 1148 | 1080 | 700 | -213 | -7 | -132 | -5 | -7 | -4 | 132 | 7 | 45 | 45 | 45 | 1 | 1 | 1
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | TOOT | 80 | 90 | 71 |  | 56 | 59 | 51 | 26 | 31 | 22 | -493 | -452 | -516 | 50 | 6 | 61 | 99 | 1 | 6 | 10 | 395 | 470 | 340 |  | -199 | -61 | -13 | -2 | -2 | -21 | 371 | 19 | 29 | 29 | 29 | 0 | 0 | 0
1102 | Mettlen - Ulrichen | Light TOOT | 5 | 9 | 2 |  | 2 | 4 | 0 | 3 | 5 | 1 | -17 | 4 | -35 |  | 0 | 2 | 3 |  |  |  | 49 | 74 | 18 |  | -16 | -3 | -10 | 0 | -1 | -1 |  |  | 42 | 42 | 42 | 1 | 1 | 1
1103 | Bickigen - Chippis | Light TOOT | 7 | 9 | 5 |  | 17 | 20 | 14 | 28 | 28 | 27 | -149 | -125 | -175 |  | 2 | 19 | 30 |  |  |  | 426 | 435 | 414 |  | -56 | -17 | -1 | 0 | -1 | -6 |  |  | 1 | 1 | 1 | 0 | 0 | 0
1104 | Bauler - Roost | TOOT | 0 | 1 | 0 |  | -2 | 0 | -4 | -1 | 1 | -3 | 20 | 34 | -2 | -41 | 0 | 0 | 0 | -1 | -5 | -8 | -15 | 12 | -41 |  | -9 | -3 | -3 | 0 | 0 | -1 | 14 | -9 | 0 | 0 | 0 | 0 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 36 | 49 | 23 |  | -80 | -71 | -89 | 1 | 2 | -1 | 634 | 638 | 630 | -99 | 0 | 0 | 0 | -1 | -12 | -20 | 12 | 27 | -13 |  | -234 | -73 | -10 | -2 | -2 | -25 | 24 | -43 | 218 | 218 | 218 | 3 | 3 | 3
1106 | Bornholm Energy Island (BEI) | TOOT | 142 | 145 | 138 | 466 | 156 | 157 | 155 | 663 | 670 | 656 | -1376 | -1371 | -1382 | -20 | 17 | 172 | 277 | 0 | -2 | -4 | 10232 | 10262 | 10202 | 3000 | -435 | -135 | -29 | -4 | -5 | -47 | -92 | -6 | 234 | 234 | 234 | 3 | 3 | 3
1109 | Basilicata - Campania reinforcements | TOOT | 25 | 28 | 21 |  | 13 | 15 | 11 | 10 | 14 | 4 | -111 | -96 | -134 | 4 | 1 | 14 | 22 | 0 | 0 | 1 | 154 | 215 | 62 |  | -44 | -14 | -4 | 0 | 0 | -5 | -39 | -1 | 41 | 41 | 41 | 0 | 0 | 0
1110 | Sicily - Calabria | TOOT | 5 | 14 | 0 |  | 0 | 2 | -1 | 7 | 12 | 3 | -1 | 11 | -15 | -10 | 0 | 0 | 1 | 0 | -1 | -2 | 104 | 184 | 51 |  | -27 | -1 | -15 | -1 | -1 | 0 | 50 | -1 | 51 | 51 | 51 | 0 | 0 | 0
1112 | GRITA 2 | TOOT | 97 | 98 | 97 |  | 11 | 40 | -11 | 39 | 41 | 38 | 64 | 99 | 29 | 78 | 1 | 12 | 19 | 1 | 10 | 16 | 606 | 636 | 572 |  | -121 | -38 | -3 | -1 | -1 | -13 | 284 | 22 | 30 | 30 | 30 | 0 | 0 | 0
1121 | 220-kV Hessenberg (AT) - Weißenbach (AT) | TOOT | 0 | 0 | 0 | 63 | 17 | 19 | 15 | 61 | 62 | 60 | -152 | -135 | -169 | -11 | 2 | 19 | 31 | 0 | -1 | -2 | 940 | 963 | 917 | 600 | -49 | -13 | -9 | -1 | -1 | -5 | -78 | -4 | 2 | 2 | 2 | 0 | 0 | 0
1122 | Offshore Wind farm connection Centre Manche 1 | TOOT | 11 | 15 | 8 | 237 | 54 | 56 | 52 | 294 | 301 | 289 | -473 | -460 | -492 | 87 | 6 | 59 | 95 | 1 | 11 | 18 | 4510 | 4608 | 4403 | 1050 | -133 | -41 | -7 | -1 | -1 | -14 | 585 | 32 | 137 | 137 | 137 | 4 | 4 | 4
1123 | Offshore Wind farm connection Centre Manche 2 | TOOT | 20 | 23 | 17 | 277 | 63 | 66 | 61 | 356 | 366 | 346 | -558 | -539 | -583 | 76 | 7 | 70 | 113 | 1 | 9 | 15 | 5469 | 5606 | 5270 | 1250 | -163 | -51 | -10 | -1 | -2 | -18 | 499 | 28 | 163 | 163 | 163 | 5 | 5 | 5
1124 | Offshore Wind Connection South Britanny | TOOT | 0 | 1 | 0 | 58 | 12 | 12 | 12 | 69 | 72 | 68 | -107 | -105 | -109 | 13 | 1 | 13 | 22 | 0 | 2 | 3 | 1064 | 1099 | 1031 | 250 | -31 | -10 | -2 | 0 | 0 | -4 | 87 | 5 | 33 | 33 | 33 | 1 | 1 | 1
1125 | Offshore Wind Connection Occitanie | TOOT | 0 | 0 | 0 | 60 | 12 | 12 | 12 | 67 | 68 | 65 | -108 | -105 | -110 | 12 | 1 | 13 | 22 | 0 | 1 | 2 | 1032 | 1064 | 1000 | 250 | -33 | -11 | 0 | 0 | 0 | -4 | 9 | 2 | 33 | 33 | 33 | 1 | 1 | 1
1126 | Offshore Wind Connection PACA | TOOT | 0 | 0 | 0 | 59 | 12 | 12 | 12 | 67 | 68 | 65 | -108 | -105 | -109 | 1 | 1 | 13 | 22 | 0 | 0 | 0 | 1028 | 1064 | 990 | 250 | -28 | -10 | -2 | 0 | 0 | -3 | -69 | -2 | 33 | 33 | 33 | 1 | 1 | 1
1127 | Offshore Wind Connection South Atlantic Oléron 1 | TOOT | 11 | 12 | 10 | 261 | 60 | 62 | 59 | 316 | 320 | 313 | -533 | -517 | -548 | 105 | 7 | 66 | 107 | 1 | 13 | 21 | 4881 | 4893 | 4869 | 1250 | -167 | -50 | -17 | -2 | -2 | -17 | 617 | 36 | 163 | 163 | 163 | 5 | 5 | 5
1134 | GiLA | PINT | 79 | 79 | 79 |  | 17 | 17 | 17 | 71 | 71 | 71 | -152 | -152 | -152 | 63 | 2 | 19 | 31 | 1 | 8 | 13 | 1398 | 1398 | 1398 |  | -54 | -17 | -2 | 0 | 0 | -6 | 516 | 25
1138 | 400 kV OHL Suceava (RO) - Balti (MD) | TOOT | 1 | 1 | 0 |  | 5 | 8 | 4 | 3 | 3 | 3 | -48 | -33 | -68 | 14 | 1 | 6 | 10 | 0 | 2 | 3 | 46 | 54 | 37 |  | -26 | -5 | -11 | -1 | -1 | -2 | 332 | 11 | 81 | 81 | 81 | 1 | 1 | 1
1139 | 380-kV Westtirol (AT) – Zell/Ziller (AT) | PINT | 39 | 51 | 22 | 143 | 56 | 61 | 50 | 168 | 169 | 168 | -492 | -442 | -535 | -63 | 6 | 61 | 99 | -1 | -8 | -13 | 2587 | 2608 | 2563 | 1600 | -187 | -50 | -38 | -2 | -3 | -18 | -334 | -21 | 8 | 8 | 8 | 0 | 0 | 0
1140 | 380-kV St. Peter (AT) - Dürnrohr (AT) | PINT | 34 | 37 | 31 | 124 | 51 | 54 | 49 | 162 | 164 | 160 | -450 | -435 | -472 | -39 | 6 | 56 | 91 | 0 | -5 | -8 | 2484 | 2512 | 2437 | 1500 | -162 | -47 | -19 | -2 | -2 | -16 | -242 | -14 | 44 | 44 | 44 | 1 | 1 | 1
1145 | 380-kV Obersielach (AT) - Hessenberg (AT) | TOOT | 7 | 13 | 2 | 200 | 58 | 60 | 56 | 216 | 219 | 213 | -507 | -490 | -532 | 12 | 6 | 63 | 102 | 0 | 1 | 2 | 3319 | 3354 | 3248 | 2000 | -184 | -52 | -27 | -2 | -3 | -18 | -33 | 1 | 9 | 9 | 9 | 0 | 0 | 0
1153 | PST romands | TOOT | 26 | 30 | 23 |  | 48 | 55 | 41 | 5 | 9 | 3 | -424 | -365 | -484 | 84 | 5 | 53 | 85 | 1 | 11 | 17 | 79 | 130 | 41 |  | -206 | -53 | -36 | -3 | -3 | -19 | 555 | 28 | 662 | 662 | 662 | 23 | 23 | 23
1155 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT) | TOOT | 15 | 19 | 12 | 345 | 100 | 102 | 98 | 365 | 367 | 362 | -881 | -862 | -900 | 50 | 11 | 110 | 178 | 1 | 6 | 10 | 5606 | 5671 | 5519 | 2000 | -313 | -89 | -46 | -4 | -4 | -31 | 163 | 14 | 9 | 9 | 9 | 0 | 0 | 0
1156 | 380-kV Greater Vienna (AT) - Hessenberg (AT) | TOOT | 9 | 16 | 2 | 273 | 80 | 82 | 77 | 290 | 294 | 288 | -702 | -680 | -719 | 24 | 9 | 87 | 142 | 0 | 3 | 5 | 4458 | 4502 | 4385 | 2500 | -246 | -72 | -31 | -3 | -3 | -25 | 36 | 5 | 9 | 9 | 9 | 0 | 0 | 0
1157 | HG North Tyrrhenian Corridor | TOOT | 61 | 62 | 61 |  | 20 | 27 | 15 | 36 | 37 | 35 | -174 | -128 | -234 | 141 | 2 | 22 | 35 | 2 | 18 | 29 | 553 | 561 | 548 |  | -61 | -15 | -13 | -1 | -1 | -5 | 639 | 40 | 2248 | 2248 | 2248 | 0 | 0 | 0
1158 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT) | PINT | 7 | 13 | 2 | 200 | 58 | 60 | 56 | 216 | 219 | 213 | -507 | -490 | -532 | 36 | 6 | 63 | 102 | 0 | 4 | 7 | 3319 | 3354 | 3248 | 2000 | -184 | -52 | -27 | -2 | -3 | -18 | 129 | 10 | 8 | 8 | 8 | 0 | 0 | 0
1159 | 220-kV Bisamberg (AT) – Wien Südost (AT) | TOOT | 4 | 8 | 0 | 24 | 8 | 9 | 6 | 32 | 35 | 28 | -67 | -57 | -82 | 1 | 1 | 8 | 13 | 0 | 0 | 0 | 493 | 537 | 433 | 500 | -26 | -8 | -3 | 0 | 0 | -3 | -9 | 0 | 5 | 5 | 5 | 0 | 0 | 0
1161 | Offshore Wind Connection South Atlantic Oléron 2 | TOOT | 19 | 25 | 15 | 266 | 61 | 62 | 59 | 338 | 344 | 331 | -538 | -520 | -547 | 122 | 7 | 67 | 108 | 2 | 15 | 25 | 5192 | 5273 | 5039 | 1200 | -155 | -48 | -11 | -1 | -2 | -17 | 704 | 40 | 156 | 156 | 156 | 5 | 5 | 5
1162 | Offshore Wind Connection Fécamp-Grand Large 1 | TOOT | 36 | 39 | 34 | 438 | 101 | 104 | 97 | 564 | 575 | 555 | -895 | -859 | -915 | 95 | 11 | 111 | 180 | 1 | 12 | 19 | 8784 | 8810 | 8759 | 2000 | -269 | -81 | -23 | -3 | -3 | -28 | 474 | 30 | 260 | 260 | 260 | 9 | 9 | 9
1163 | Offshore Wind Connection Fécamp-Grand Large 2 | TOOT | 36 | 39 | 34 | 438 | 101 | 104 | 97 | 564 | 575 | 555 | -895 | -859 | -915 | 89 | 11 | 111 | 180 | 1 | 11 | 18 | 8784 | 8810 | 8759 | 2000 | -269 | -81 | -23 | -3 | -3 | -28 | 474 | 30 | 261 | 261 | 261 | 9 | 9 | 9
1164 | Offshore Wind Connection Golfe de Lion Centre | TOOT | 36 | 39 | 34 | 438 | 101 | 104 | 97 | 564 | 575 | 555 | -895 | -859 | -915 | 55 | 11 | 111 | 180 | 1 | 7 | 11 | 8784 | 8810 | 8759 | 2000 | -269 | -81 | -23 | -3 | -3 | -28 | -133 | 5 | 261 | 261 | 261 | 9 | 9 | 9
1165 | Offshore Wind Connection Golfe de Gascogne Sud | TOOT | 19 | 25 | 15 | 266 | 61 | 62 | 59 | 338 | 344 | 331 | -538 | -520 | -547 | 85 | 7 | 67 | 108 | 1 | 11 | 17 | 5192 | 5273 | 5039 | 1200 | -155 | -48 | -11 | -1 | -2 | -17 | 593 | 32 | 156 | 156 | 156 | 5 | 5 | 5
1166 | HG Adriatic Corridor | PINT | 42 | 49 | 34 |  | 16 | 21 | 12 | 28 | 33 | 18 | -140 | -102 | -181 | 87 | 2 | 17 | 28 | 1 | 11 | 18 | 428 | 505 | 278 |  | -59 | -18 | -5 | -1 | -1 | -6 | 345 | 24 | 86 | 86 | 86 | 0 | 0 | 0
1167 | HG Central link | TOOT | 2 | 4 | 0 |  | -1 | 0 | -2 | -2 | 0 | -3 | 11 | 18 | 4 | 31 | 0 | 0 | 0 | 0 | 4 | 6 | -24 | 1 | -42 |  | -7 | -2 | -3 | 0 | 0 | -1 | 159 | 9 | 188 | 188 | 188 | 0 | 0 | 0
1168 | HG Ionian-Tyrrhenian Corridor | TOOT | 7 | 8 | 5 |  | 2 | 4 | 0 | 5 | 7 | 1 | -20 | -3 | -36 | 31 | 0 | 2 | 4 | 0 | 4 | 6 | 71 | 105 | 9 |  | -19 | -4 | -7 | 0 | 0 | -1 | 112 | 8 | 0 | 0 | 0 | 0 | 0 | 0
1169 | SAPEI 2 | PINT | 26 | 31 | 20 |  | 13 | 16 | 10 | 8 | 11 | 4 | -113 | -88 | -138 | 9 | 1 | 14 | 23 | 0 | 1 | 2 | 116 | 166 | 62 |  | -48 | -14 | -7 | -1 | -1 | -5 | 2 | 1 | 15 | 15 | 15 | 0 | 0 | 0
1171 | Interconnection IT-CH | PINT | 77 | 79 | 75 |  | 70 | 73 | 67 | 4 | 7 | 2 | -620 | -594 | -646 | 74 | 8 | 77 | 125 | 1 | 9 | 15 | 58 | 103 | 33 |  | -265 | -84 | -9 | -2 | -2 | -30 | 387 | 24 | 2 | 2 | 2 | 0 | 0 | 0
1182 | EHV S/S Thesprotias and its connection to the 400 kV System | Light PINT | 3 | 7 | 0 |  | -1 | 4 | -10 | 2 | 6 | 0 | 31 | 86 | -32 | 14 | 0 | 0 | 0 | 0 | 2 | 3 | 27 | 86 | -5 |  | -12 | -3 | -5 | 0 | 0 | -1 | 48 | 4 | 0 | 0 | 0 | 0 | 0 | 0
1183 | New interconnection line 400 kV Greece - Albania | Light PINT | 4 | 8 | 0 |  | 0 | 3 | -4 | 1 | 2 | 0 | -1 | 37 | -25 | -15 | 0 | 0 | 0 | 0 | -2 | -3 | 21 | 35 | 0 |  | -1 | -2 | -1 | 0 | 0 | -1 | -48 | -4 | 1 | 1 | 1 | 0 | 0 | 0
1185 | South Coast Offshore Transmission Project | TOOT | 0 | 0 | 0 | 64 | 15 | 18 | 12 | 91 | 98 | 86 | -131 | -104 | -162 | 0 | 2 | 16 | 26 | 0 | 0 | 0 | 1391 | 1523 | 1313 | 800 | -56 | -9 | -46 | -1 | -2 | -3 | 14 | 0 | 29 | 29 | 29 | 1 | 1 | 1
1192 | HansaLink - Phase 1 | PINT | 172 | 173 | 171 | 0 | 214 | 214 | 214 | 32 | 37 | 27 | -1886 | -1886 | -1886 | -42 | 24 | 235 | 380 | -1 | -5 | -8 | 485 | 558 | 413 | 2000 | -652 | -179 | -116 | -8 | -11 | -63 | -280 | -15 | 378 | 378 | 378 | 5 | 5 | 5
1193 | HansaLink - Phase 2 | PINT | 58 | 61 | 55 | 0 | 36 | 36 | 35 | -25 | -24 | -27 | -314 | -309 | -322 | -11 | 4 | 39 | 63 | 0 | -1 | -2 | -388 | -365 | -412 | 2000 | -106 | -29 | -21 | -1 | -2 | -10 | -90 | -4 | 375 | 375 | 375 | 5 | 5 | 5
1197 | NU-Link Interconnector | PINT | 82 | 95 | 65 |  | 92 | 97 | 89 | 39 | 44 | 30 | -813 | -785 | -851 | 42 | 10 | 101 | 164 | 1 | 5 | 8 | 595 | 670 | 461 |  | -286 | -80 | -46 | -3 | -4 | -28 | 253 | 13 | 136 | 136 | 136 | 4 | 4 | 4
1200 | Hybrid interconnector Norway-Sørvest F Windfarm-Continent (DK, DE or BE) | PINT | 38 | 42 | 34 |  | 184 | 185 | 184 | 47 | 51 | 42 | -1627 | -1622 | -1632 | 73 | 20 | 203 | 328 | 1 | 9 | 15 | 728 | 794 | 661 |  | -542 | -156 | -80 | -6 | -8 | -55 | 432 | 27 | 256 | 256 | 256 | 4 | 4 | 4
1201 | Reinvestment of Skagerrak 1 and 2 | PINT | 52 | 60 | 44 |  | 51 | 52 | 50 | 51 | 56 | 46 | -451 | -445 | -457 | 1 | 6 | 56 | 91 | 0 | 0 | 0 | 792 | 867 | 718 |  | -157 | -41 | -40 | -2 | -3 | -14 | 28 | 1 | 95 | 95 | 95 | 1 | 1 | 1
1202 | Increased capacity Norway-Finland, Back-to-Back | PINT | 12 | 18 | 6 |  | 3 | 4 | 2 | 9 | 11 | 8 | -30 | -20 | -35 | 1 | 0 | 4 | 6 | 0 | 0 | 0 | 143 | 174 | 122 |  | -17 | -2 | -11 | 0 | -1 | -1 | 63 | 3 | 23 | 23 | 23 | 0 | 0 | 0
1203 | Offshore Wind Connection Bretagne Nord-Ouest | PINT | 14 | 14 | 13 | 250 | 57 | 60 | 55 | 307 | 310 | 305 | -507 | -485 | -528 | 100 | 6 | 63 | 102 | 1 | 12 | 20 | 4742 | 4746 | 4737 | 1200 | -159 | -48 | -14 | -2 | -2 | -17 | 632 | 36 | 157 | 157 | 157 | 5 | 5 | 5
1207 | 380kV Niederstedem-Bertrange/Bofferdange | PINT | 3 | 5 | 2 |  | 1 | 2 | 1 | 0 | 3 | -2 | -10 | -1 | -19 | 41 | 0 | 1 | 2 | 1 | 5 | 8 | -5 | 40 | -32 |  | -4 | -1 | 0 | 0 | 0 | 0 | -17 | 9 | 0 | 0 | 0 | 0 | 0 | 0
1208 | Medlink | PINT | 391 | 474 | 328 | 0 | 626 | 632 | 621 | -19 | 8 | -47 | -5523 | -5475 | -5571 | 175 | 70 | 688 | 1113 | 2 | 22 | 35 | -298 | 127 | -724 | 9016 | -2009 | -628 | -81 | -17 | -18 | -220 | 508 | 43 | 5 | 5 | 5 | 0 | 0 | 0
1209 | Latvia and Lithuania cross-border strengthening project | PINT | 15 | 22 | 9 |  | 1 | 4 | -2 | 21 | 23 | 17 | -10 | 20 | -37 | -3 | 0 | 1 | 2 | 0 | 0 | -1 | 322 | 354 | 263 |  | -8 | -1 | -1 | 0 | 0 | 0 | -34 | -1 | 2 | 2 | 2 | 0 | 0 | 0
1210 | APOLLO-LINK | Light PINT | 547 | 549 | 546 |  | 291 | 305 | 277 | 184 | 200 | 170 | -2563 | -2445 | -2685 |  | 32 | 319 | 517 |  |  |  | 2822 | 3097 | 2598 |  | -1293 | -409 | -38 | -11 | -11 | -143 |  |  | 237 | 237 | 237 | 2 | 2 | 2
1211 | Baltic WindConnector (BWC) | PINT | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1213 | Offshore hybrid Interconnector (DE-NL) | Light PINT | 62 | 69 | 55 |  | 25 | 29 | 21 | 42 | 49 | 38 | -219 | -181 | -257 |  | 3 | 27 | 44 |  |  |  | 650 | 745 | 578 |  | -76 | -21 | -18 | -1 | -1 | -7 |  |  | 32 | 32 | 32 | 0 | 0 | 0
1214 | Hybrid Interconnector Denmark-Germany | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1215 | Xlinks Morocco - Germany | PINT | 884 | 913 | 851 | 0 | 464 | 465 | 464 | -18 | 4 | -39 | -4094 | -4090 | -4097 | 778 | 52 | 510 | 825 | 10 | 97 | 157 | -269 | 57 | -595 | 15200 | -1422 | -392 | -252 | -17 | -23 | -138 | 4259 | 262 | 34 | 34 | 34 | 0 | 0 | 0
1216 | High-Voltage Direct Current Interconnector Project Romania-Hungary | PINT | 16 | 19 | 12 |  | 15 | 17 | 14 | 1 | 2 | -2 | -131 | -120 | -147 | -57 | 2 | 16 | 26 | -1 | -7 | -11 | 9 | 27 | -24 |  | -27 | -13 | -6 | 0 | 0 | -4 | 190 | -31 | 46 | 46 | 46 | 1 | 1 | 1
1217 | Further Development of Offshore Renewables (MOG 3) | Light PINT | 39 | 49 | 34 | 367 | 86 | 90 | 82 | 483 | 495 | 475 | -762 | -727 | -795 |  | 10 | 95 | 154 |  |  |  | 7421 | 7576 | 7227 |  | -255 | -74 | -31 | -3 | -3 | -26 |  |  | 175 | 175 | 175 | 3 | 3 | 3
1218 | Hybrid HVDC Interconnector BE-NL | Light PINT | 5 | 6 | 4 |  | 1 | 1 | 0 | -2 | -1 | -2 | -4 | 3 | -11 |  | 0 | 1 | 2 |  |  |  | -23 | -14 | -33 | [9 empty] | 1 | 1 | 1 | 0 | 0 | 0
1219 | Bofferdange- Bertrange | Light PINT | 13 | 14 | 13 |  | 6 | 8 | 4 | 7 | 11 | 3 | -55 | -36 | -67 |  | 1 | 7 | 11 |  |  |  | 108 | 174 | 40 |  | -20 | -6 | -4 | 0 | 0 | -2 |  |  | 17 | 17 | 17 | 0 | 0 | 0
1220 | Offshore Wind Connection Viana do Castelo | TOOT | 4 | 8 | 0 | 113 | 22 | 23 | 21 | 158 | 161 | 152 | -192 | -183 | -204 | 21 | 2 | 24 | 39 | 0 | 3 | 4 | 2421 | 2472 | 2370 | 2000 | -43 | -8 | -14 | -1 | -1 | -3 | 198 | 11 | 74 | 74 | 74 | 1 | 1 | 1
1221 | Offshore Wind Connection Leixões | TOOT | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 143 | 143 | 1 | 1 | 1
1222 | Offshore Wind Connection Figueira da Foz (North) | TOOT | 5 | 9 | 1 | 137 | 26 | 27 | 24 | 191 | 196 | 184 | -226 | -208 | -237 | 16 | 3 | 28 | 46 | 0 | 2 | 3 | 2940 | 3005 | 2871 | 2000 | -22 | -6 | -1 | 0 | 0 | -2 | 185 | 9 | 92 | 92 | 92 | 1 | 1 | 1
1223 | Offshore Wind Connection Figueira da Foz (South) | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1224 | Offshore Wind Connection Ericeira | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1225 | Offshore Wind Connection Sines | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1226 | North-South Electricity Corridor in Eastern Europe | Light PINT | 121 | 145 | 100 |  | 47 | 76 | 20 | 27 | 39 | 17 | -411 | -175 | -671 |  | 5 | 51 | 83 |  |  |  | 408 | 596 | 269 |  | -81 | -78 | -170 | -4 | -10 | -27 |  |  | 99 | 99 | 99 | 0 | 0 | 0
1229 | Rhine-Main-Link | PINT | 294 | 379 | 237 |  | 33 | 71 | -48 | 129 | 165 | 107 | -488 | -401 | -425 | -58 | 4 | 36 | 59 | -1 | -7 | -12 | 1 | 2 | 1 |  | -226 | -61 | -28 | -2 | -3 | -22 | -1 | -25 | 0 | 0 | 0 | 0 | 0 | 0
1230 | TuNur Malta | PINT | 33 | 36 | 30 | 0 | 101 | 103 | 99 | -4 | -4 | -4 | -890 | -869 | -910 | 2 | 11 | 111 | 179 | 0 | 0 | 0 | -65 | -65 | -65 | 1400 | -328 | -103 | -13 | -3 | -3 | -36 | -6 | 0 | 2 | 2 | 2 | 0 | 0 | 0
1231 | Green Aegean Interconnector | Light PINT | 732 | 752 | 712 |  | 344 | 355 | 334 | 192 | 195 | 190 | -3038 | -2944 | -3132 |  | 38 | 379 | 612 |  |  |  | 2967 | 2985 | 2949 |  | -1215 | -352 | -161 | -13 | -16 | -124 |  |  | 416 | 416 | 416 | 6 | 6 | 6
1233 | Laufenburg - Beznau - Breite | Light PINT | 28 | 32 | 25 |  | 43 | 51 | 35 | 80 | 85 | 72 | -378 | -307 | -447 |  | 5 | 47 | 76 |  |  |  | 1226 | 1322 | 1097 |  | -164 | -50 | -15 | -2 | -2 | -18 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1234 | 220-kV Reitdorf (AT) - Weißenbach (AT) | TOOT | 0 | 0 | 0 | 46 | 12 | 15 | 10 | 47 | 48 | 46 | -108 | -90 | -128 | -8 | 1 | 13 | 22 | 0 | -1 | -2 | 724 | 752 | 708 | 500 | -33 | -11 | 0 | 0 | 0 | -4 | -58 | -3 | 3 | 3 | 3 | 0 | 0 | 0
1235 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | PINT | 13 | 16 | 9 |  | 5 | 8 | 3 | 1 | 3 | -3 | -45 | -25 | -67 | 93 | 1 | 6 | 9 | 1 | 12 | 19 | 15 | 47 | -41 |  | -11 | -5 | -7 | 0 | 0 | -2 | 349 | 26 | 0 | 0 | 0 | 0 | 0 | 0
1236 | Power-to-Gas for Austria (P2G4A) | PINT | 2 | 3 | 1 |  | 1 | 3 | 0 | 1 | 2 | 0 | -8 | 4 | -29 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 12 | 24 | 1 |  | -10 | -3 | -4 | 0 | 0 | -1 | 1 | 0
1239 | Interconnection Ukraine-Slovak Republic | Light PINT | 4 | 6 | 0 |  | 10 | 12 | 6 | 3 | 4 | 1 | -84 | -56 | -109 |  | 1 | 10 | 17 |  |  |  | 46 | 63 | 22 |  | -15 | -5 | 1 | 0 | 0 | -2
1240 | Interconnection Ukraine-Romania | Light PINT | 1 | 2 | 0 |  | 15 | 17 | 12 | 2 | 2 | 1 | -133 | -102 | -153 |  | 2 | 17 | 27 |  |  |  | 26 | 38 | 14 |  | -45 | -7 | -27 | -1 | -2 | -2

## 2040NT-EU27
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 48 | 66 | 30 | 43 | 14 | 16 | 12 | 194 | 232 | 154 | -94 | -79 | -109 | 4 | 18 | 45 | 48 | 1 | 2 | 2 | 3005 | 3627 | 2343 | 1154 | -22 | -5 | -3 | 0 | 0 | -2 | 349 | 9 | 2903 | 2903 | 2903 | 27 | 27 | 27
4 | Interconnection Portugal-Spain | TOOT | 50 | 55 | 42 |  | 16 | 16 | 15 | 29 | 60 | 7 | -107 | -104 | -108 | 4 | 20 | 51 | 55 | 1 | 2 | 2 | 454 | 929 | 106 |  | -23 | -7 | -2 | 0 | 0 | -2 | 60 | 8 | 92 | 92 | 92 | 1 | 1 | 1
16 | Biscay Gulf | TOOT | 770 | 778 | 763 |  | 52 | 54 | 50 | 513 | 513 | 512 | -353 | -339 | -368 | 29 | 68 | 170 | 182 | 6 | 14 | 15 | 8090 | 8489 | 7816 |  | -190 | -45 | -45 | -3 | -4 | -16 | 3415 | 98 | 3925 | 3925 | 3925 | 129 | 129 | 129
28 | Italy-Montenegro | TOOT | 28 | 39 | 21 |  | 34 | 36 | 33 | 31 | 36 | 28 | -233 | -222 | -245 | 0 | 45 | 112 | 120 | 0 | 0 | 0 | 483 | 563 | 429 |  | -58 | -20 | -2 | 0 | 0 | -7 | 159 | 4 | 108 | 108 | 108 | 2 | 2 | 2
29 | Italy-Tunisia | TOOT | 108 | 126 | 83 |  | -65 | -58 | -70 | 41 | 45 | 36 | 445 | 478 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 631 | 698 | 569 |  | -157 | -48 | -8 | -1 | -1 | -17 | -200 | -16 | 138 | 138 | 138 | 2 | 2 | 2
33 | Central Northern Italy | TOOT | 47 | 61 | 32 |  | 10 | 12 | 9 | 13 | 15 | 11 | -71 | -59 | -80 | 5 | 14 | 34 | 37 | 1 | 3 | 3 | 190 | 232 | 151 |  | -50 | -10 | -13 | -1 | -1 | -4 | 93 | -2 | 243 | 243 | 243 | 3 | 3 | 3
35 | CZ Southwest-east corridor | TOOT | 147 | 155 | 140 |  | 85 | 87 | 81 | 53 | 55 | 52 | -579 | -550 | -595 | 7 | 111 | 279 | 298 | 1 | 3 | 3 | 827 | 849 | 789 |  | -237 | -72 | -19 | -2 | -3 | -25 | 402 | 20 | 298 | 298 | 298 | 1 | 1 | 1
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 51 | 52 | 50 |  | 2 | 3 | 0 | 19 | 23 | 11 | -16 | -2 | -23 |  | 3 | 8 | 8 |  |  |  | 295 | 363 | 169 |  | -8 | -1 | -6 | 0 | 0 | 0 |  |  | 104 | 104 | 104 | 2 | 2 | 2
47 | Westtirol (AT) - Vöhringen (DE) | TOOT | 99 | 109 | 94 |  | 19 | 21 | 14 | 47 | 55 | 41 | -127 | -95 | -146 | -5 | 24 | 61 | 66 | -1 | -2 | -2 | 735 | 854 | 635 |  | -53 | -17 | -2 | 0 | -1 | -6 | 73 | -2 | 34 | 34 | 34 | 0 | 0 | 0
81 | North South Interconnector | TOOT | 35 | 41 | 28 |  | 8 | 10 | 6 | 16 | 25 | 10 | -53 | -42 | -67 | 0 | 10 | 26 | 27 | 0 | 0 | 0 | 243 | 377 | 154 |  | -12 | -2 | -4 | 0 | 0 | -1 | 32 | 3 | 366 | 366 | 366 | 7 | 7 | 7
85 | Integration of RES in Alentejo | TOOT | 4 | 14 | 0 | 1 | 1 | 3 | 0 | 6 | 9 | 3 | -8 | 0 | -17 | 0 | 2 | 4 | 4 | 0 | 0 | 0 | 98 | 143 | 40 | 553 | -4 | -1 | -5 | 0 | 0 | 0 | -36 | -1 | 0 | 0 | 0 | 0 | 0 | 0
94 | GerPol Improvements | TOOT | 334 | 345 | 319 |  | 122 | 127 | 119 | 51 | 54 | 47 | -832 | -810 | -867 | 9 | 160 | 400 | 428 | 2 | 4 | 5 | 794 | 829 | 729 |  | -433 | -51 | -309 | -11 | -20 | -19 | 368 | 15 | 509 | 509 | 509 | 9 | 9 | 9
107 | Celtic Interconnector | TOOT | 264 | 269 | 257 |  | 27 | 27 | 27 | 192 | 201 | 182 | -185 | -184 | -187 | 14 | 36 | 89 | 95 | 3 | 7 | 7 | 2968 | 3136 | 2843 |  | -70 | -16 | -16 | -1 | -1 | -6 | 1098 | 45 | 1281 | 1281 | 1281 | 42 | 42 | 42
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 81 | 92 | 71 |  | 8 | 9 | 7 | 68 | 72 | 60 | -54 | -50 | -62 | 0 | 10 | 26 | 28 | 0 | 0 | 0 | 1051 | 1124 | 952 |  | -9 | -3 | 0 | 0 | 0 | -1 | 56 | 4 | 698 | 698 | 698 | 9 | 9 | 9
120 | Princess Elisabeth Island (MOG 2) | TOOT | 362 | 370 | 354 | 523 | 83 | 89 | 80 | 738 | 748 | 724 | -567 | -543 | -608 | 23 | 109 | 273 | 292 | 4 | 11 | 12 | 11301 | 11305 | 11296 | 3500 | -307 | -61 | -94 | -5 | -7 | -22 | 278 | 25 | 1936 | 1936 | 1936 | 22 | 22 | 22
121 | Nautilus: multi-purpose interconnector Belgium - UK | TOOT | 199 | 202 | 196 |  | 34 | 36 | 33 | -22 | -22 | -22 | -232 | -223 | -244 | 13 | 45 | 112 | 120 | 2 | 6 | 7 | -342 | -340 | -345 |  | -153 | -28 | -50 | -3 | -3 | -10 | 82 | 7 | 451 | 451 | 451 | 9 | 9 | 9
124 | Ekhyddan-Nybro-Hemsjö | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 82 | 100 | 67 |  | 2 | 3 | -1 | -3 | -2 | -5 | -11 | 5 | -22 | 12 | 2 | 5 | 6 | 2 | 6 | 6 | -45 | -24 | -72 |  | -39 | -4 | -26 | -1 | -1 | -2 | 140 | 13 | 345 | 345 | 345 | 0 | 0 | 0
127 | Central Southern Italy | TOOT | 17 | 24 | 11 |  | 6 | 8 | 5 | 0 | 4 | -6 | -41 | -32 | -58 | 14 | 8 | 20 | 21 | 3 | 7 | 7 | -7 | 55 | -102 |  | -20 | -7 | 0 | 0 | 0 | -2 | 177 | 9 | 94 | 94 | 94 | 1 | 1 | 1
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 519 | 655 | 413 |  | 30 | 38 | 23 | 192 | 238 | 158 | -204 | -159 | -259 | 3 | 39 | 98 | 105 | 1 | 2 | 2 | 2 | 2 | 2 |  | -71 | -22 | -2 | -1 | -1 | -8 | 240 | 10 | 0 | 0 | 0 | 0 | 0 | 0
132 | HVDC Line A-North | TOOT | 1640 | 1900 | 1431 |  | 99 | 121 | 81 | 620 | 749 | 519 | -676 | -549 | -826 | 46 | 130 | 325 | 348 | 9 | 22 | 24 | 6 | 7 | 5 |  | -234 | -74 | -7 | -2 | -2 | -26 | 1003 | 56 | 0 | 0 | 0 | 0 | 0 | 0
138 | Black Sea Corridor | TOOT | 18 | 21 | 11 |  | 7 | 10 | 4 | 1 | 7 | -3 | -50 | -28 | -70 | 1 | 10 | 24 | 26 | 0 | 1 | 1 | 13 | 110 | -43 |  | -23 | -8 | -1 | 0 | 0 | -3 | -33 | -5 | 399 | 399 | 399 | 5 | 5 | 5
144 | Mid Continental East corridor | TOOT | 22 | 25 | 21 |  | 9 | 12 | 7 | 8 | 10 | 6 | -60 | -46 | -80 | 4 | 12 | 29 | 31 | 1 | 2 | 2 | 123 | 148 | 97 |  | -34 | -11 | -3 | 0 | 0 | -4 | 71 | 4 | 632 | 632 | 632 | 7 | 7 | 7
150 | Italy-Slovenia | TOOT | 23 | 28 | 18 |  | 21 | 22 | 20 | 3 | 7 | -1 | -142 | -133 | -148 | 5 | 27 | 68 | 73 | 1 | 2 | 3 | 48 | 107 | -17 |  | -51 | -17 | -1 | 0 | 0 | -6 | 131 | 9 | 206 | 206 | 206 | 3 | 3 | 3
153 | France-Alderney-Britain | TOOT | 108 | 119 | 94 |  | 35 | 36 | 34 | 8 | 14 | -1 | -236 | -230 | -245 | 20 | 45 | 113 | 121 | 4 | 9 | 10 | 125 | 213 | -20 |  | -88 | -26 | -9 | -1 | -1 | -9 | 998 | 51 | 2233 | 2233 | 2233 | 75 | 75 | 75
170 | Baltic States Synchronization with Continental Europe | TOOT | 429 | 436 | 422 |  | 214 | 220 | 204 | 169 | 178 | 161 | -1457 | -1390 | -1494 | 0 | 280 | 701 | 750 | 0 | 0 | 0 | 2623 | 2708 | 2522 |  | -528 | -102 | -392 | -14 | -27 | -34 | 153 | -6 | 781 | 781 | 781 | 15 | 15 | 15
174 | Greenconnector | TOOT | 72 | 77 | 67 |  | 84 | 86 | 83 | 8 | 14 | 4 | -574 | -565 | -583 | 4 | 110 | 276 | 296 | 1 | 2 | 2 | 123 | 208 | 66 |  | -225 | -60 | -30 | -3 | -3 | -21 | 408 | 26 | 436 | 436 | 436 | 6 | 6 | 6
176 | Hansa PowerBridge I | TOOT | 149 | 151 | 147 |  | 9 | 12 | 6 | 37 | 42 | 28 | -59 | -38 | -83 | -2 | 11 | 28 | 30 | 0 | -1 | -1 | 565 | 648 | 435 |  | -93 | -16 | -93 | -3 | -5 | -4 | -128 | -7 | 614 | 614 | 614 | 8 | 8 | 8
187 | St. Peter (AT) - Pleinting (DE) | TOOT | 484 | 505 | 466 |  | 87 | 102 | 72 | 204 | 208 | 199 | -593 | -490 | -696 | 15 | 114 | 285 | 306 | 3 | 7 | 8 | 3160 | 3252 | 3114 |  | -322 | -83 | -57 | -4 | -5 | -29 | 1579 | 78 | 305 | 305 | 305 | 3 | 3 | 3
200 | CZ Northwest-South corridor | TOOT | 147 | 155 | 140 |  | 85 | 87 | 81 | 53 | 55 | 52 | -579 | -550 | -595 | 1 | 111 | 279 | 298 | 0 | 0 | 0 | 827 | 849 | 789 |  | -237 | -72 | -19 | -2 | -3 | -25 | 259 | 6 | 294 | 294 | 294 | 0 | 0 | 0
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 40 | 50 | 31 |  | 10 | 12 | 7 | 0 | 3 | -3 | -68 | -47 | -80 | 2 | 13 | 33 | 35 | 0 | 1 | 1 | 3 | 51 | -55 |  | -19 | -4 | -5 | 0 | 0 | -2 | 33 | 2 | 167 | 167 | 167 | 1 | 1 | 1
219 | Great Sea Interconnector | TOOT | 568 | 589 | 547 |  | -22 | -21 | -23 | 192 | 198 | 188 | 152 | 160 | 145 | 36 | 0 | 0 | 0 | 7 | 17 | 19 | 2976 | 3014 | 2937 |  | -50 | -15 | -2 | 0 | 0 | -5 | -2354 | -192 | 567 | 567 | 567 | 5 | 5 | 5
225 | 2nd interconnector Belgium - Germany | light PINT | 189 | 196 | 179 |  | 11 | 13 | 9 | 73 | 82 | 62 | -78 | -64 | -89 | 35 | 15 | 38 | 40 | 7 | 17 | 18 | 1134 | 1272 | 942 |  | -57 | -5 | -37 | -1 | -2 | -2 | 919 | 41 | 366 | 366 | 366 | 4 | 4 | 4
227 | Transbalkan Corridor | TOOT | 46 | 47 | 45 |  | 16 | 17 | 12 | 1 | 7 | -7 | -105 | -82 | -118 | 2 | 20 | 51 | 54 | 0 | 1 | 1 | 5 | 101 | -115 |  | -81 | -24 | -10 | -1 | -1 | -9 | 60 | 4 | 498 | 498 | 498 | 7 | 7 | 7
228 | Muhlbach - Eichstetten | TOOT | 64 | 73 | 56 |  | 5 | 6 | 4 | 23 | 28 | 20 | -35 | -24 | -41 | 4 | 7 | 17 | 18 | 1 | 2 | 2 | 355 | 436 | 299 |  | -29 | -3 | -16 | -1 | -1 | -1 | 179 | 9 | 305 | 305 | 305 | 9 | 9 | 9
231 | Beznau - Tiengen | TOOT | 37 | 40 | 33 |  | 23 | 27 | 17 | 39 | 43 | 31 | -153 | -115 | -186 | -11 | 29 | 74 | 79 | -2 | -5 | -6 | 599 | 672 | 478 |  | -80 | -24 | -5 | -1 | -1 | -8 | 60 | -4 | 102 | 102 | 102 | 2 | 2 | 2
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 1511 | 1801 | 1327 |  | 89 | 112 | 73 | 589 | 721 | 505 | -608 | -493 | -764 | 57 | 117 | 292 | 313 | 11 | 27 | 29 | 6 | 7 | 5 |  | -832 | -263 | -25 | -7 | -7 | -92 | 1948 | 99 | 0 | 0 | 0 | 0 | 0 | 0
239 | Fenno-Skan 3 | Light PINT | 60 | 66 | 56 |  | 2 | 3 | 1 | 42 | 44 | 40 | -16 | -7 | -22 |  | 3 | 8 | 8 |  |  |  | 657 | 687 | 604 |  | -29 | -1 | -21 | -1 | -1 | 0 |  |  | 212 | 212 | 212 | 2 | 2 | 2
243 | New 400 kV interconnection line between Serbia and Croatia | Light PINT | 4 | 7 | 2 |  | 0 | 2 | -1 | 2 | 10 | -2 | -2 | 5 | -14 |  | 0 | 1 | 1 |  |  |  | 37 | 155 | -35 |  | -5 | -1 | -2 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
244 | Vigy - Uchtelfangen area | TOOT | 330 | 332 | 329 |  | 23 | 29 | 18 | 101 | 102 | 100 | -155 | -123 | -196 | 41 | 30 | 74 | 80 | 8 | 20 | 21 | 1564 | 1575 | 1552 |  | -134 | -18 | -67 | -3 | -4 | -7 | 1031 | 57 | 1703 | 1703 | 1703 | 45 | 45 | 45
247 | AQUIND Interconnector | TOOT | 182 | 191 | 174 |  | 62 | 64 | 62 | 20 | 26 | 14 | -425 | -421 | -433 | 22 | 82 | 205 | 219 | 4 | 10 | 11 | 311 | 399 | 220 |  | -189 | -46 | -39 | -2 | -3 | -16 | 796 | 45 | 3762 | 3762 | 3762 | 125 | 125 | 125
250 | Merchant line Castasegna (CH) - Mese (IT) | TOOT | 23 | 29 | 18 |  | 17 | 22 | 14 | 7 | 7 | 6 | -116 | -94 | -151 | 2 | 22 | 56 | 60 | 0 | 1 | 1 | 101 | 104 | 97 |  | -34 | -10 | -4 | 0 | 0 | -4 | 29 | 5 | 42 | 42 | 42 | 1 | 1 | 1
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 713 | 814 | 635 |  | 40 | 48 | 32 | 249 | 298 | 215 | -269 | -221 | -329 | 33 | 52 | 130 | 139 | 6 | 16 | 17 | 2 | 3 | 2 |  | -210 | -66 | -6 | -2 | -2 | -23 | 848 | 45 | 0 | 0 | 0 | 0 | 0 | 0
259 | HU-RO | TOOT | 25 | 30 | 17 |  | 9 | 15 | 4 | 1 | 5 | -4 | -62 | -29 | -99 | 2 | 12 | 30 | 32 | 0 | 1 | 1 | 13 | 77 | -59 |  | -50 | -15 | -5 | -1 | -1 | -5 | 168 | 12 | 699 | 699 | 699 | 9 | 9 | 9
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | TOOT | 197 | 198 | 196 |  | 27 | 30 | 24 | 20 | 31 | 11 | -187 | -161 | -205 | 30 | 36 | 90 | 96 | 6 | 14 | 15 | 308 | 486 | 163 |  | -78 | -23 | -11 | -1 | -1 | -8 | 303 | 22 | 860 | 860 | 860 | 33 | 33 | 33
267 | Hansa PowerBridge II | Light PINT | 149 | 151 | 147 |  | 9 | 12 | 6 | 37 | 42 | 28 | -59 | -38 | -83 | -2 | 11 | 28 | 30 | 0 | -1 | -1 | 565 | 648 | 435 |  | -93 | -16 | -93 | -3 | -5 | -4 | -128 | -7 | 614 | 614 | 614 | 8 | 8 | 8
270 | FR-ES project -Aragón-Atlantic Pyrenees | TOOT | 517 | 526 | 508 |  | 32 | 35 | 30 | 368 | 368 | 367 | -221 | -204 | -239 | 16 | 42 | 106 | 114 | 3 | 8 | 8 | 5727 | 5735 | 5719 |  | -119 | -26 | -33 | -2 | -2 | -9 | 1771 | 61 | 2606 | 2606 | 2606 | 86 | 86 | 86
276 | FR-ES project -Navarra-Landes | PINT | 469 | 487 | 450 |  | 28 | 32 | 26 | 345 | 369 | 319 | -189 | -174 | -215 | 26 | 36 | 91 | 97 | 5 | 13 | 13 | 5335 | 5770 | 4866 |  | -168 | -25 | -64 | -3 | -4 | -10 | 2575 | 85 | 1744 | 1744 | 1744 | 57 | 57 | 57
280 | FR-BE: Lonny-Achene-Gramme | TOOT | 141 | 155 | 124 |  | 9 | 12 | 5 | 41 | 45 | 34 | -63 | -37 | -82 | 14 | 12 | 30 | 32 | 3 | 7 | 7 | 631 | 708 | 520 |  | -72 | -4 | -42 | -2 | -2 | -2 | 452 | 24 | 1179 | 1179 | 1179 | 39 | 39 | 39
283 | TuNur Italy | PINT | 50 | 62 | 38 |  | 168 | 182 | 157 | -65 | -55 | -79 | -1144 | -1066 | -1239 | -1 | 220 | 550 | 589 | 0 | 0 | 0 | -1008 | -862 | -1210 | 5000 | -419 | -127 | -25 | -4 | -4 | -45 | -59 | -1 | 15 | 15 | 15 | 0 | 0 | 0
285 | GridLink | TOOT | 108 | 119 | 94 |  | 35 | 36 | 34 | 8 | 14 | -1 | -236 | -230 | -245 | 20 | 45 | 113 | 121 | 4 | 10 | 10 | 125 | 213 | -20 |  | -88 | -26 | -9 | -1 | -1 | -9 | 493 | 30 | 2232 | 2232 | 2232 | 75 | 75 | 75
297 | BRABO III | TOOT | 43 | 43 | 42 |  | 7 | 9 | 5 | 11 | 16 | 5 | -45 | -32 | -62 | 6 | 9 | 22 | 23 | 1 | 3 | 3 | 177 | 254 | 76 |  | -6 | -5 | -12 | 0 | 0 | -1 | 162 | 8 | 0 | 0 | 0 | 0 | 0 | 0
299 | SACOI 3 | TOOT | 178 | 181 | 175 |  | 90 | 94 | 82 | 8 | 12 | 4 | -609 | -559 | -636 | 2 | 117 | 293 | 314 | 0 | 1 | 1 | 118 | 189 | 54 |  | -2052 | -5 | -1379 | -53 | -74 | -18 | -67 | -7 | 348 | 348 | 348 | 8 | 8 | 8
309 | NeuConnect | TOOT | 221 | 232 | 213 |  | 46 | 52 | 41 | 32 | 48 | 17 | -313 | -279 | -354 | 28 | 60 | 151 | 161 | 5 | 14 | 15 | 490 | 744 | 252 |  | -211 | -37 | -82 | -4 | -6 | -14 | 506 | 33 | 1820 | 1820 | 1820 | 21 | 21 | 21
312 | St. Peter (AT) - Tauern (AT) | TOOT | 369 | 384 | 358 |  | 67 | 79 | 54 | 158 | 166 | 150 | -455 | -368 | -536 | -32 | 87 | 219 | 234 | -6 | -15 | -16 | 2446 | 2588 | 2348 |  | -244 | -65 | -38 | -3 | -4 | -23 | -233 | -17 | 215 | 215 | 215 | 2 | 2 | 2
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 244 | 254 | 232 |  | 43 | 51 | 36 | 109 | 119 | 101 | -294 | -243 | -344 | 1 | 56 | 141 | 151 | 0 | 0 | 0 | 1606 | 1631 | 1580 |  | -157 | -42 | -24 | -2 | -2 | -15 | 371 | 10 | 125 | 125 | 125 | 1 | 1 | 1
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 2 | 2 | 2 |  | 1 | 3 | 0 | -7 | -3 | -14 | -10 | 1 | -17 | 1 | 2 | 5 | 5 | 0 | 1 | 1 | -108 | -48 | -216 |  | -7 | 0 | -5 | 0 | 0 | 0 | 274 | 19 | 7 | 7 | 7 | 0 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 13 | 20 | 4 |  | 4 | 5 | 3 | -1 | 9 | -9 | -28 | -23 | -37 | 2 | 5 | 13 | 14 | 0 | 1 | 1 | -10 | 140 | -139 |  | 0 | -4 | -9 | 0 | 0 | -1 | 284 | 20 | 22 | 22 | 22 | 0 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | TOOT | 188 | 196 | 179 |  | 75 | 83 | 62 | 13 | 14 | 12 | -507 | -424 | -567 | 9 | 97 | 244 | 261 | 2 | 4 | 5 | 194 | 208 | 183 |  | -193 | -45 | -40 | -3 | -3 | -16 | 191 | 11 | 920 | 920 | 920 | 9 | 9 | 9
328 | Interconnector DE-LUX | TOOT | 11 | 22 | 2 |  | 1 | 2 | 0 | 3 | 6 | -1 | -8 | 0 | -16 | -13 | 2 | 4 | 4 | -3 | -6 | -7 | 38 | 96 | -18 |  | -6 | -1 | -2 | 0 | 0 | 0 | -198 | -13 | 0 | 0 | 0 | 0 | 0 | 0
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 283 | 297 | 269 |  | 101 | 106 | 96 | 221 | 231 | 209 | -1692 | -1777 | -1595 | -11 | 574 | 1063 | 1120 | -2 | -5 | -5 | 4688 | 4435 | 4922 | 0 | -1536 | -177 | -74 | -122 | -79 | -53 | -351 | -33 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | TOOT | 91 | 100 | 82 |  | 1 | 3 | -1 | -3 | 2 | -8 | -6 | 7 | -19 | 8 | 1 | 3 | 3 | 1 | 4 | 4 | -46 | 25 | -124 |  | -32 | -1 | -27 | -1 | -2 | 0 | 66 | 7 | 656 | 656 | 656 | 1 | 1 | 1
335 | North Sea Wind Power Hub | Light PINT | 1686 | 1714 | 1662 | 1493 | 220 | 242 | 205 | 2981 | 2990 | 2969 | -1500 | -1395 | -1648 |  | 288 | 721 | 772 |  |  |  | 46532 | 46605 | 46459 | 14000 | -894 | -142 | -402 | -18 | -26 | -53 |  |  | 3397 | 3397 | 3397 | 42 | 42 | 42
338 | Adriatic HVDC link | TOOT | 123 | 147 | 111 |  | 32 | 34 | 29 | 34 | 35 | 32 | -217 | -199 | -231 | 27 | 42 | 104 | 112 | 5 | 13 | 14 | 518 | 545 | 490 |  | -88 | -32 | -4 | -1 | -1 | -11 | 372 | 15 | 669 | 669 | 669 | 9 | 9 | 9
339 | Tyrrhenian link | TOOT | 78 | 81 | 76 |  | 33 | 37 | 29 | 22 | 29 | 15 | -227 | -199 | -253 | 13 | 44 | 109 | 117 | 2 | 6 | 7 | 319 | 440 | 231 |  | -91 | -29 | -2 | -1 | -1 | -10 | 401 | 12 | 438 | 438 | 438 | 8 | 8 | 8
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 322 | 352 | 298 |  | 115 | 126 | 107 | 251 | 274 | 232 | -2907 | -3193 | -2680 | -10 | 986 | 1826 | 1925 | -2 | -5 | -5 | 4614 | 4282 | 5070 | 0 | -3069 | -252 | -2149 | -190 | -241 | -81 | -605 | -46 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | TOOT | 8 | 15 | 0 |  | 5 | 7 | 2 | -1 | 4 | -7 | -31 | -17 | -51 | 3 | 6 | 15 | 16 | 1 | 1 | 1 | -10 | 69 | -105 |  | -19 | -5 | -4 | 0 | 0 | -2 | 1162 | 84 | 428 | 428 | 428 | 4 | 4 | 4
342 | Central Balkan Corridor | TOOT | 5 | 8 | 1 |  | 6 | 7 | 5 | -3 | -1 | -4 | -38 | -31 | -45 | 2 | 7 | 18 | 19 | 0 | 1 | 1 | -47 | -16 | -64 |  | -25 | -6 | -5 | 0 | 0 | -2 | 37 | 0 | 320 | 320 | 320 | 4 | 4 | 4
343 | CSE1 New | TOOT | 17 | 27 | 10 |  | 3 | 5 | 2 | 1 | 11 | -4 | -21 | -17 | -31 | 1 | 4 | 10 | 11 | 0 | 1 | 1 | 20 | 161 | -69 |  | -1 | -2 | -3 | 0 | 0 | -1 | 91 | 6 | 35 | 35 | 35 | 1 | 1 | 1
346 | ZuidWest380 NL Oost | TOOT | 18 | 22 | 15 |  | 0 | 1 | -1 | -3 | -1 | -4 | -1 | 8 | -8 | -3 | 0 | 0 | 0 | -1 | -1 | -1 | -45 | -21 | -61 |  | -32 | -1 | -18 | -1 | -1 | -1 | -121 | -6 | 0 | 0 | 0 | 0 | 0 | 0
349 | MaresConnect | TOOT | 71 | 83 | 61 |  | 13 | 16 | 12 | 104 | 109 | 101 | -91 | -81 | -110 | 0 | 17 | 44 | 47 | 0 | 0 | 0 | 1603 | 1685 | 1549 |  | -20 | -2 | -9 | 0 | -1 | -1 | 76 | 1 | 513 | 513 | 513 | 9 | 9 | 9
350 | South Balkan Corridor | TOOT | 5 | 7 | 3 |  | -1 | 3 | -5 | -1 | 9 | -11 | 5 | 32 | -22 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | -21 | 144 | -167 |  | -10 | -7 | -8 | 0 | 0 | -2 | 1156 | 83 | 123 | 123 | 123 | 2 | 2 | 2
375 | Lienz (AT) - Veneto region (IT) 220 kV | TOOT | 124 | 130 | 117 |  | 37 | 42 | 31 | -1 | 3 | -8 | -254 | -212 | -283 | 17 | 49 | 122 | 131 | 3 | 8 | 9 | -19 | 38 | -125 |  | -102 | -24 | -23 | -1 | -2 | -9 | 117 | 9 | 628 | 628 | 628 | 6 | 6 | 6
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | Light PINT | 11 | 16 | 2 |  | 0 | 1 | -1 | 6 | 17 | -1 | 3 | 9 | -5 |  | 0 | 0 | 0 |  |  |  | 99 | 260 | -16 |  | -26 | -3 | -11 | -1 | -1 | -1 |  |  | 1 | 1 | 1 | 0 | 0 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | TOOT | 47 | 60 | 37 |  | 6 | 9 | 5 | 12 | 16 | 10 | -44 | -32 | -62 | 7 | 8 | 21 | 23 | 1 | 3 | 3 | 190 | 254 | 153 |  | -8 | -4 | 0 | 0 | 0 | -1 | 187 | 9 | 0 | 0 | 0 | 0 | 0 | 0
378 | Transformer Gatica | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 339 | 352 | 331 |  | 22 | 23 | 21 | 139 | 146 | 130 | -148 | -142 | -159 | 39 | 28 | 71 | 76 | 8 | 19 | 20 | 1 | 1 | 1 |  | -51 | -16 | -2 | 0 | 0 | -6 | 896 | 51 | 0 | 0 | 0 | 0 | 0 | 0
1039 | SE North-south long-term reinforcements | PINT | 59 | 70 | 49 |  | 4 | 7 | 1 | 4 | 10 | -1 | -28 | -3 | -49 | 6 | 5 | 13 | 14 | 1 | 3 | 3 | 58 | 159 | -22 |  | -37 | -3 | -24 | -1 | -1 | -1 | 140 | 4 | 312 | 312 | 312 | 0 | 0 | 0
1040 | LirIC | TOOT | 76 | 83 | 66 |  | 13 | 16 | 9 | 26 | 29 | 22 | -88 | -64 | -109 | 0 | 17 | 42 | 45 | 0 | 0 | 0 | 404 | 453 | 338 |  | -24 | -5 | -8 | 0 | -1 | -2 | 67 | 1 | 509 | 509 | 509 | 11 | 11 | 11
1041 | GREGY Green Energy Interconnector | TOOT | 345 | 351 | 339 |  | -401 | -401 | -401 | 49 | 59 | 41 | 2728 | 2729 | 2726 | -2 | 0 | 0 | 0 | 0 | -1 | -1 | 763 | 893 | 630 |  | -234 | -63 | -28 | -3 | -3 | -23 | 748 | 52 | 114 | 114 | 114 | 2 | 2 | 2
1046 | Finnish North-South reinforcement | PINT | 156 | 156 | 156 |  | 10 | 10 | 10 | 232 | 232 | 232 | 66 | 66 | 66 | 0 | 13 | 32 | 34 | 0 | 0 | 0 | 3634 | 3634 | 3634 |  | -1 | -1 | -1 | 0 | 0 | 0 | -138 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 57 | 58 | 56 |  | -50 | -49 | -52 | 19 | 24 | 15 | 344 | 351 | 336 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 368 | 234 |  | -36 | -16 | -8 | 0 | 0 | -5 | -4568 | -334 | 75 | 75 | 75 | 1 | 1 | 1
1049 | Cronos Energy Ltd | PINT | 157 | 164 | 150 |  | 40 | 42 | 39 | -24 | -20 | -31 | -275 | -266 | -288 | 9 | 53 | 132 | 142 | 2 | 4 | 5 | -373 | -317 | -481 |  | -152 | -34 | -39 | -2 | -3 | -12 | -106 | 1 | 511 | 511 | 511 | 6 | 6 | 6
1050 | Tarchon Energy Ltd | TOOT | 221 | 232 | 213 |  | 46 | 52 | 41 | 32 | 48 | 17 | -313 | -279 | -354 | 25 | 60 | 151 | 161 | 5 | 12 | 13 | 490 | 744 | 252 |  | -211 | -37 | -82 | -4 | -6 | -14 | 330 | 21 | 1828 | 1828 | 1828 | 22 | 22 | 22
1052 | Lienz (AT) - Malta (AT) - Obersielach (AT) | TOOT | 523 | 567 | 478 | 164 | 131 | 138 | 124 | 212 | 235 | 189 | -892 | -846 | -939 | 13 | 171 | 429 | 460 | 2 | 6 | 7 | 3306 | 3659 | 2954 | 2000 | -363 | -91 | -78 | -5 | -7 | -32 | -97 | -6 | 1736 | 1736 | 1736 | 17 | 17 | 17
1054 | 220-kV Westtirol (AT) - Zell/Ziller (AT) | TOOT | 99 | 109 | 95 |  | 19 | 21 | 14 | 47 | 55 | 41 | -128 | -98 | -146 | 15 | 25 | 62 | 66 | 3 | 7 | 8 | 724 | 854 | 635 |  | -53 | -17 | -2 | 0 | -1 | -6 | 391 | 24 | 34 | 34 | 34 | 0 | 0 | 0
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 172 | 177 | 164 |  | -2 | 4 | -7 | 132 | 141 | 124 | 12 | 45 | -24 | 46 | 0 | 0 | 0 | 9 | 22 | 23 | 2052 | 2186 | 1893 |  | -2 | -4 | -7 | 0 | 0 | -1 | 7117 | 532 | 234 | 234 | 234 | 1 | 1 | 1
1058 | HVDC Interconnector DE-CH | Light PINT | 145 | 148 | 142 |  | 24 | 32 | 15 | 67 | 69 | 65 | -165 | -105 | -218 |  | 32 | 79 | 85 |  |  |  | 1041 | 1057 | 1010 |  | -118 | -28 | -27 | -2 | -2 | -10 |  |  | 461 | 461 | 461 | 7 | 7 | 7
1059 | Southern Italy | TOOT | 6 | 9 | 3 |  | 2 | 4 | 1 | -2 | 2 | -7 | -16 | -5 | -28 | 7 | 3 | 8 | 8 | 1 | 3 | 4 | -34 | 21 | -111 |  | 0 | -2 | -3 | 0 | 0 | -1 | 152 | 3 | 96 | 96 | 96 | 1 | 1 | 1
1066 | Bulgaria - Turkey | Light PINT | 83 | 86 | 79 |  | -184 | -176 | -189 | 7 | 10 | 4 | 1251 | 1284 | 1200 |  | 0 | 0 | 0 |  |  |  | 106 | 152 | 58 |  | -483 | -151 | -23 | -4 | -5 | -53 |  |  | 165 | 165 | 165 | 2 | 2 | 2
1067 | New AC 400 kV interconnection line Greece - Turkey | Light PINT | 37 | 58 | 21 |  | -85 | -72 | -98 | 3 | 9 | -6 | 580 | 666 | 487 |  | 0 | 0 | 0 |  |  |  | 52 | 144 | -91 |  | -129 | -42 | -1 | -1 | -1 | -15 |  |  | 116 | 116 | 116 | 2 | 2 | 2
1068 | LaSGo Link | PINT | 88 | 92 | 81 |  | 8 | 10 | 7 | 76 | 80 | 71 | -57 | -48 | -68 | 2 | 11 | 27 | 29 | 0 | 1 | 1 | 1176 | 1213 | 1119 |  | -144 | -3 | -94 | -4 | -5 | -2 | 179 | 9 | 65 | 65 | 65 | 0 | 0 | 0
1074 | Pannonian Corridor | TOOT | 11 | 19 | 6 |  | 6 | 11 | 1 | -5 | -2 | -10 | -43 | -5 | -75 | 2 | 8 | 21 | 22 | 0 | 1 | 1 | -82 | -35 | -155 |  | -42 | -12 | -7 | -1 | -1 | -4 | 26 | 2 | 301 | 301 | 301 | 4 | 4 | 4
1085 | Malta-Italy Cable Link No.2 | TOOT | 85 | 102 | 64 |  | 47 | 52 | 42 | 11 | 15 | 7 | -320 | -287 | -353 | 2 | 61 | 154 | 165 | 0 | 1 | 1 | 170 | 237 | 104 |  | -159 | -51 | -3 | -1 | -1 | -18 | 43 | 2 | 80 | 80 | 80 | 1 | 1 | 1
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 4 | 10 | 0 | 35 | 5 | 6 | 5 | 48 | 63 | 36 | -37 | -34 | -39 | -1 | 7 | 18 | 19 | 0 | 0 | 0 | 751 | 987 | 561 | 700 | -144 | 0 | -97 | -4 | -5 | -1 | -371 | -5 | 6 | 6 | 6 | 0 | 0 | 0
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | TOOT | 31 | 60 | 9 | 44 | 12 | 15 | 7 | 74 | 76 | 72 | -79 | -46 | -103 | 0 | 15 | 38 | 40 | 0 | 0 | 0 | 1158 | 1182 | 1134 | 1000 | -103 | -1 | -69 | -3 | -4 | -1 | -214 | -5 | 0 | 0 | 0 | 0 | 0 | 0
1092 | TritonLink: offshore hybrid HVDC interconnector Belgium – Denmark | TOOT | 1132 | 1136 | 1128 | 202 | 103 | 106 | 101 | 1190 | 1191 | 1188 | -698 | -684 | -719 | 29 | 134 | 336 | 359 | 6 | 14 | 15 | 18310 | 18621 | 18100 | 10000 | -321 | -57 | -118 | -6 | -8 | -21 | 435 | 31 | 3467 | 3467 | 3467 | 37 | 37 | 37
1094 | Estlink 3 | TOOT | 113 | 121 | 108 |  | 28 | 31 | 26 | 119 | 126 | 114 | -193 | -176 | -210 | -5 | 37 | 93 | 99 | -1 | -2 | -2 | 1848 | 1970 | 1779 |  | -297 | -15 | -173 | -7 | -10 | -7 | 523 | 17 | 761 | 761 | 761 | 10 | 10 | 10
1095 | Aurora line 2 (4th AC Finland-Sweden north) | TOOT | 55 | 59 | 49 |  | 7 | 8 | 6 | 61 | 63 | 60 | -45 | -40 | -55 | 0 | 9 | 22 | 23 | 0 | 0 | 0 | 950 | 963 | 937 |  | -14 | -2 | -5 | 0 | 0 | -1 | 43 | 3 | 698 | 698 | 698 | 9 | 9 | 9
1096 | Beznau - Mettlen | Light TOOT | 31 | 34 | 28 |  | 27 | 33 | 20 | 45 | 48 | 43 | -181 | -135 | -227 |  | 35 | 87 | 93 |  |  |  | 699 | 734 | 664 |  | -87 | -29 | -1 | -1 | -1 | -10 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1097 | Upgrade to Konti-Skan | PINT | 93 | 103 | 84 |  | 5 | 6 | 4 | 36 | 44 | 28 | -31 | -26 | -38 | 10 | 6 | 15 | 16 | 2 | 5 | 5 | 567 | 691 | 434 |  | -42 | -6 | -17 | -1 | -1 | -2 | 264 | 14 | 105 | 105 | 105 | 2 | 2 | 2
1098 | Offshore Wind LT 2 | TOOT | 8 | 10 | 7 | 46 | 9 | 10 | 8 | 54 | 58 | 49 | -61 | -52 | -65 | 0 | 12 | 29 | 31 | 0 | 0 | 0 | 838 | 907 | 755 | 700 | -62 | 0 | -43 | -2 | -2 | -1 | 104 | 3 | 147 | 147 | 147 | 1 | 1 | 1
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | TOOT | 137 | 145 | 131 |  | 83 | 84 | 81 | 44 | 50 | 41 | -567 | -554 | -575 | 17 | 109 | 273 | 292 | 3 | 8 | 9 | 688 | 756 | 636 |  | -232 | -71 | -18 | -2 | -3 | -25 | 530 | 26 | 296 | 296 | 296 | 1 | 1 | 1
1102 | Mettlen - Ulrichen | Light TOOT | 17 | 26 | 11 |  | 0 | 1 | -2 | 1 | 3 | 0 | -2 | 12 | -10 |  | 0 | 1 | 1 |  |  |  | 22 | 46 | 2 |  | -17 | 0 | -11 | 0 | -1 | 0 |  |  | 221 | 221 | 221 | 3 | 3 | 3
1103 | Bickigen - Chippis | Light TOOT | 31 | 51 | 18 |  | 19 | 23 | 14 | 36 | 41 | 33 | -131 | -96 | -155 |  | 25 | 63 | 67 |  |  |  | 562 | 638 | 509 |  | -51 | -19 | -5 | 0 | 0 | -7 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1104 | Bauler - Roost | TOOT | 4 | 6 | 3 |  | 1 | 2 | 0 | -2 | 2 | -8 | -6 | -3 | -10 | -14 | 1 | 3 | 3 | -3 | -7 | -7 | -32 | 30 | -136 |  | -1 | -1 | -2 | 0 | 0 | 0 | -210 | -14 | 0 | 0 | 0 | 0 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 130 | 146 | 116 |  | -20 | -16 | -23 | 0 | 2 | -2 | 133 | 159 | 106 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | -3 | 28 | -34 |  | -54 | -18 | 0 | 0 | 0 | -6 | -59 | -3 | 538 | 538 | 538 | 8 | 8 | 8
1106 | Bornholm Energy Island (BEI) | TOOT | 199 | 204 | 195 | 399 | 41 | 43 | 39 | 564 | 573 | 554 | -278 | -262 | -291 | -15 | 53 | 134 | 143 | -3 | -7 | -8 | 8646 | 8663 | 8629 | 3000 | -82 | -30 | -4 | -1 | -1 | -10 | -527 | -30 | 805 | 805 | 805 | 10 | 10 | 10
1109 | Basilicata - Campania reinforcements | TOOT | 13 | 18 | 6 |  | 5 | 6 | 5 | -1 | 2 | -9 | -36 | -31 | -41 | 5 | 7 | 18 | 19 | 1 | 3 | 3 | -26 | 28 | -144 |  | -12 | -5 | -1 | 0 | 0 | -2 | 0 | -4 | 94 | 94 | 94 | 1 | 1 | 1
1110 | Sicily - Calabria | TOOT | 5 | 11 | 2 |  | 1 | 4 | -3 | -3 | 2 | -9 | -9 | 18 | -28 | 2 | 2 | 4 | 4 | 0 | 1 | 1 | -45 | 26 | -141 |  | -10 | -2 | -10 | 0 | 0 | 0 | 28 | -4 | 0 | 0 | 0 | 0 | 0 | 0
1112 | GRITA 2 | TOOT | 191 | 202 | 177 |  | 75 | 76 | 71 | 58 | 62 | 51 | -507 | -486 | -519 | 8 | 97 | 244 | 261 | 1 | 4 | 4 | 889 | 947 | 786 |  | -138 | -45 | -1 | -1 | -1 | -16 | 509 | 35 | 767 | 767 | 767 | 11 | 11 | 11
1121 | 220-kV Hessenberg (AT) - Weißenbach (AT) | TOOT | 4 | 9 | 1 | 69 | 9 | 10 | 8 | 64 | 72 | 56 | -61 | -56 | -69 | 4 | 12 | 29 | 31 | 1 | 2 | 2 | 996 | 1092 | 874 | 600 | -28 | -8 | -4 | 0 | 0 | -3 | -95 | -2 | 4 | 4 | 4 | 0 | 0 | 0
1122 | Offshore Wind farm connection Centre Manche 1 | TOOT | 42 | 53 | 26 | 243 | 22 | 24 | 20 | 338 | 348 | 330 | -153 | -139 | -161 | 10 | 29 | 74 | 79 | 2 | 5 | 5 | 5148 | 5166 | 5130 | 1050 | -47 | -14 | -4 | 0 | -1 | -5 | 911 | 42 | 260 | 260 | 260 | 9 | 9 | 9
1123 | Offshore Wind farm connection Centre Manche 2 | TOOT | 42 | 53 | 26 | 243 | 22 | 24 | 20 | 338 | 348 | 330 | -153 | -139 | -161 | 7 | 29 | 74 | 79 | 1 | 4 | 4 | 5148 | 5166 | 5130 | 1250 | -47 | -14 | -4 | 0 | -1 | -5 | 661 | 31 | 261 | 261 | 261 | 9 | 9 | 9
1124 | Offshore Wind Connection South Britanny | TOOT | 27 | 29 | 24 | 152 | 14 | 15 | 12 | 204 | 210 | 196 | -93 | -80 | -104 | 7 | 18 | 45 | 48 | 1 | 3 | 4 | 3158 | 3219 | 3061 | 250 | -24 | -7 | -4 | 0 | 0 | -2 | 664 | 27 | 156 | 156 | 156 | 5 | 5 | 5
1125 | Offshore Wind Connection Occitanie | TOOT | 31 | 41 | 21 | 162 | 17 | 18 | 17 | 205 | 207 | 201 | -118 | -113 | -121 | 3 | 23 | 57 | 61 | 1 | 1 | 1 | 3178 | 3234 | 3145 | 250 | -40 | -11 | -6 | 0 | -1 | -4 | 80 | 6 | 157 | 157 | 157 | 5 | 5 | 5
1126 | Offshore Wind Connection PACA | TOOT | 31 | 35 | 21 | 159 | 18 | 20 | 17 | 197 | 201 | 191 | -124 | -116 | -134 | 1 | 24 | 59 | 64 | 0 | 1 | 1 | 3054 | 3128 | 2998 | 250 | -57 | -12 | -15 | -1 | -1 | -4 | -218 | -7 | 158 | 158 | 158 | 5 | 5 | 5
1127 | Offshore Wind Connection South Atlantic Oléron 1 | TOOT | 36 | 43 | 31 | 232 | 22 | 24 | 21 | 296 | 298 | 293 | -149 | -142 | -163 | 6 | 29 | 72 | 77 | 1 | 3 | 3 | 4582 | 4630 | 4536 | 1250 | -51 | -14 | -7 | -1 | -1 | -5 | 626 | 29 | 260 | 260 | 260 | 9 | 9 | 9
1134 | GiLA | PINT | 329 | 329 | 329 |  | 27 | 27 | 27 | 231 | 231 | 231 | -184 | -184 | -184 | 12 | 0 | 0 | 0 | 2 | 6 | 6 | 4522 | 4522 | 4522 |  | -80 | -25 | -2 | -1 | -1 | -9 | 752 | 32 | 0 | 0 | 0 | 0 | 0 | 0
1138 | 400 kV OHL Suceava (RO) - Balti (MD) | TOOT | 8 | 19 | 0 |  | 4 | 9 | 0 | 4 | 10 | -1 | -25 | 3 | -59 | 6 | 5 | 12 | 13 | 1 | 3 | 3 | 62 | 153 | -24 |  | -1 | -3 | -3 | 0 | 0 | -1 | 1632 | 106 | 99 | 99 | 99 | 1 | 1 | 1
1139 | 380-kV Westtirol (AT) – Zell/Ziller (AT) | PINT | 80 | 92 | 70 | 153 | 21 | 24 | 19 | 170 | 176 | 165 | -142 | -129 | -162 | -20 | 27 | 68 | 73 | -4 | -10 | -10 | 2642 | 2681 | 2573 | 1600 | -103 | -17 | -40 | -2 | -3 | -6 | -681 | -39 | 12 | 12 | 12 | 0 | 0 | 0
1140 | 380-kV St. Peter (AT) - Dürnrohr (AT) | PINT | 100 | 116 | 88 | 135 | 30 | 34 | 26 | 191 | 198 | 186 | -204 | -179 | -233 | -8 | 39 | 98 | 105 | -2 | -4 | -4 | 2964 | 3101 | 2837 | 1500 | -114 | -30 | -17 | -1 | -2 | -11 | -293 | -17 | 14 | 14 | 14 | 1 | 1 | 1
1145 | 380-kV Obersielach (AT) - Hessenberg (AT) | TOOT | 90 | 93 | 86 | 154 | 31 | 34 | 27 | 224 | 229 | 220 | -209 | -186 | -232 | -16 | 40 | 101 | 108 | -3 | -8 | -8 | 3461 | 3483 | 3440 | 2000 | -104 | -25 | -22 | -1 | -2 | -9 | -225 | -15 | 12 | 12 | 12 | 0 | 0 | 0
1153 | PST romands | TOOT | 30 | 41 | 17 |  | 40 | 53 | 29 | 13 | 19 | 10 | -275 | -196 | -358 | 4 | 53 | 132 | 142 | 1 | 2 | 2 | 204 | 287 | 160 |  | -150 | -44 | -13 | -1 | -2 | -15 | 711 | 36 | 1351 | 1351 | 1351 | 45 | 45 | 45
1155 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT) | TOOT | 42 | 61 | 27 | 410 | 56 | 64 | 50 | 399 | 408 | 393 | -382 | -340 | -433 | 3 | 73 | 184 | 197 | 0 | 1 | 1 | 6188 | 6353 | 6061 | 2000 | -185 | -48 | -33 | -2 | -3 | -17 | -132 | -6 | 12 | 12 | 12 | 0 | 0 | 0
1156 | 380-kV Greater Vienna (AT) - Hessenberg (AT) | TOOT | 38 | 53 | 19 | 319 | 44 | 52 | 39 | 314 | 319 | 310 | -300 | -262 | -356 | -8 | 58 | 145 | 155 | -2 | -4 | -4 | 4859 | 4973 | 4745 | 2500 | -149 | -39 | -27 | -2 | -2 | -14 | -213 | -12 | 12 | 12 | 12 | 0 | 0 | 0
1157 | HG North Tyrrhenian Corridor | TOOT | 309 | 314 | 301 |  | 80 | 85 | 74 | 90 | 99 | 85 | -547 | -504 | -577 | 49 | 105 | 263 | 282 | 9 | 23 | 25 | 1310 | 1531 | 1087 |  | -322 | -93 | -33 | -3 | -4 | -33 | 757 | 49 | 2414 | 2414 | 2414 | 36 | 36 | 36
1158 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT) | PINT | 27 | 39 | 15 | 223 | 28 | 32 | 25 | 226 | 230 | 223 | -189 | -173 | -215 | -1 | 36 | 91 | 97 | 0 | -1 | -1 | 3501 | 3602 | 3417 | 2000 | -113 | -25 | -27 | -2 | -2 | -9 | -191 | -10 | 12 | 12 | 12 | 0 | 0 | 0
1159 | 220-kV Bisamberg (AT) – Wien Südost (AT) | TOOT | 0 | 1 | 0 | 24 | 2 | 3 | 2 | 25 | 30 | 19 | -17 | -13 | -21 | 2 | 3 | 8 | 9 | 0 | 1 | 1 | 389 | 462 | 295 | 500 | -6 | -2 | 0 | 0 | 0 | -1 | -3 | 2 | 6 | 6 | 6 | 0 | 0 | 0
1161 | Offshore Wind Connection South Atlantic Oléron 2 | TOOT | 25 | 27 | 23 | 207 | 19 | 20 | 18 | 261 | 266 | 253 | -130 | -119 | -136 | 10 | 25 | 63 | 67 | 2 | 5 | 5 | 4043 | 4119 | 3960 | 1200 | -59 | -12 | -17 | -1 | -1 | -4 | 901 | 44 | 252 | 252 | 252 | 8 | 8 | 8
1162 | Offshore Wind Connection Fécamp-Grand Large 1 | TOOT | 50 | 54 | 43 | 345 | 31 | 33 | 28 | 440 | 447 | 430 | -213 | -194 | -226 | 2 | 41 | 102 | 110 | 0 | 1 | 1 | 6732 | 6733 | 6732 | 2000 | -85 | -18 | -24 | -1 | -2 | -6 | 451 | 26 | 418 | 418 | 418 | 14 | 14 | 14
1163 | Offshore Wind Connection Fécamp-Grand Large 2 | TOOT | 50 | 54 | 43 | 345 | 31 | 33 | 28 | 440 | 447 | 430 | -213 | -194 | -226 | 2 | 41 | 102 | 110 | 0 | 1 | 1 | 6732 | 6733 | 6732 | 2000 | -85 | -18 | -24 | -1 | -2 | -6 | 451 | 26 | 417 | 417 | 417 | 14 | 14 | 14
1164 | Offshore Wind Connection Golfe de Lion Centre | TOOT | 50 | 54 | 43 | 345 | 31 | 33 | 28 | 440 | 447 | 430 | -213 | -194 | -226 | -4 | 41 | 102 | 110 | -1 | -2 | -2 | 6732 | 6733 | 6732 | 2000 | -85 | -18 | -24 | -1 | -2 | -6 | -634 | -24 | 418 | 418 | 418 | 14 | 14 | 14
1165 | Offshore Wind Connection Golfe de Gascogne Sud | TOOT | 25 | 27 | 23 | 207 | 19 | 20 | 18 | 261 | 266 | 253 | -130 | -119 | -136 | 5 | 25 | 63 | 67 | 1 | 3 | 3 | 4043 | 4119 | 3960 | 1200 | -59 | -12 | -17 | -1 | -1 | -4 | 468 | 23 | 250 | 250 | 250 | 8 | 8 | 8
1166 | HG Adriatic Corridor | PINT | 138 | 147 | 131 |  | 35 | 40 | 29 | 50 | 56 | 40 | -235 | -196 | -274 | 9 | 45 | 113 | 121 | 2 | 4 | 5 | 849 | 878 | 820 |  | -127 | -37 | -12 | -1 | -1 | -13 | 373 | 28 | 34 | 34 | 34 | 0 | 0 | 0
1167 | HG Central link | TOOT | 14 | 24 | 6 |  | 4 | 6 | 3 | -1 | 3 | -6 | -30 | -21 | -41 | 12 | 6 | 15 | 16 | 2 | 6 | 6 | -23 | 38 | -96 |  | -18 | -3 | -5 | 0 | 0 | -1 | 319 | 16 | 319 | 319 | 319 | 4 | 4 | 4
1168 | HG Ionian-Tyrrhenian Corridor | TOOT | 29 | 33 | 27 |  | 10 | 13 | 8 | 8 | 9 | 7 | -69 | -53 | -85 | 11 | 13 | 33 | 35 | 2 | 5 | 6 | 113 | 138 | 85 |  | -25 | -6 | -6 | 0 | 0 | -2 | 188 | 7 | 35 | 35 | 35 | 1 | 1 | 1
1169 | SAPEI 2 | PINT | 17 | 18 | 15 |  | 7 | 8 | 6 | 1 | 5 | -7 | -47 | -42 | -57 | -9 | 9 | 23 | 24 | -2 | -4 | -5 | 6 | 70 | -106 |  | -20 | -5 | -4 | 0 | 0 | -2 | 21 | 3 | 2 | 2 | 2 | 0 | 0 | 0
1171 | Interconnection IT-CH | PINT | 88 | 112 | 63 |  | 60 | 65 | 53 | 12 | 13 | 10 | -411 | -359 | -444 | 2 | 79 | 198 | 212 | 0 | 1 | 1 | 181 | 197 | 150 |  | -131 | -46 | -5 | -1 | -1 | -16 | 267 | 16 | 55 | 55 | 55 | 1 | 1 | 1
1182 | EHV S/S Thesprotias and its connection to the 400 kV System | Light PINT | 0 | 0 | 0 |  | 0 | 2 | -4 | 4 | 9 | -1 | 1 | 28 | -15 |  | 0 | 0 | 0 |  |  |  | 62 | 136 | -21 |  | -12 | 0 | -8 | 0 | 0 | 0 |  |  | 2 | 2 | 2 | 0 | 0 | 0
1183 | New interconnection line 400 kV Greece - Albania | Light PINT | 8 | 15 | 2 |  | 0 | 1 | -2 | 6 | 11 | 1 | 0 | 13 | -10 |  | 0 | 0 | 0 |  |  |  | 97 | 174 | 18 |  | -7 | 0 | -4 | 0 | 0 | 0 |  |  | 1 | 1 | 1 | 0 | 0 | 0
1185 | South Coast Offshore Transmission Project | TOOT | 0 | 1 | 0 | 56 | 6 | 7 | 5 | 68 | 82 | 56 | -39 | -33 | -45 | 0 | 8 | 19 | 20 | 0 | 0 | 0 | 1051 | 1253 | 876 | 800 | -19 | -1 | -12 | 0 | -1 | 0 | 17 | 1 | 57 | 57 | 57 | 1 | 1 | 1
1192 | HansaLink - Phase 1 | PINT | 355 | 414 | 293 |  | 67 | 80 | 54 | 19 | 22 | 17 | -458 | -365 | -541 | -14 | 88 | 220 | 236 | -3 | -7 | -7 | 302 | 342 | 262 | 2000 | -316 | -52 | -134 | -6 | -9 | -19 | -207 | -19 | 2249 | 2249 | 2249 | 28 | 28 | 28
1193 | HansaLink - Phase 2 | PINT | 68 | 70 | 67 |  | 8 | 9 | 7 | -29 | -21 | -35 | -57 | -49 | -63 | 2 | 11 | 27 | 29 | 0 | 1 | 1 | -445 | -335 | -533 | 2000 | -46 | -5 | -21 | -1 | -1 | -2 | -231 | -8 | 193 | 193 | 193 | 23 | 23 | 23
1197 | NU-Link Interconnector | PINT | 114 | 131 | 93 |  | 25 | 28 | 21 | -17 | -12 | -25 | -172 | -141 | -188 | 9 | 33 | 83 | 89 | 2 | 4 | 5 | -259 | -178 | -381 |  | -93 | -22 | -22 | -1 | -2 | -8 | -71 | -3 | 193 | 193 | 193 | 5 | 5 | 5
1200 | Hybrid interconnector Norway-Sørvest F Windfarm-Continent (DK, DE or BE) | PINT | 197 | 239 | 141 |  | 61 | 67 | 55 | 26 | 48 | -1 | -415 | -375 | -456 | 21 | 80 | 200 | 214 | 4 | 10 | 11 | 406 | 749 | -21 |  | -224 | -50 | -64 | -3 | -4 | -18 | 270 | 18 | 868 | 868 | 868 | 11 | 11 | 11
1201 | Reinvestment of Skagerrak 1 and 2 | PINT | 105 | 128 | 79 |  | 16 | 19 | 14 | 10 | 26 | -6 | -112 | -94 | -128 | 0 | 21 | 54 | 58 | 0 | 0 | 0 | 152 | 416 | -95 |  | -87 | -7 | -50 | -2 | -3 | -3 | 19 | 1 | 228 | 228 | 228 | 4 | 4 | 4
1202 | Increased capacity Norway-Finland, Back-to-Back | PINT | 12 | 18 | 7 |  | 3 | 4 | 2 | 15 | 21 | 12 | -22 | -17 | -28 | 0 | 4 | 11 | 12 | 0 | 0 | 0 | 241 | 336 | 183 |  | -18 | -1 | -15 | -1 | -1 | 0 | 86 | 4 | 51 | 51 | 51 | 1 | 1 | 1
1203 | Offshore Wind Connection Bretagne Nord-Ouest | PINT | 37 | 40 | 33 | 215 | 19 | 23 | 17 | 284 | 285 | 283 | -131 | -116 | -155 | 5 | 25 | 63 | 68 | 1 | 2 | 3 | 4402 | 4450 | 4322 | 1200 | -64 | -13 | -19 | -1 | -1 | -5 | 906 | 43 | 251 | 251 | 251 | 8 | 8 | 8
1207 | 380kV Niederstedem-Bertrange/Bofferdange | PINT | 6 | 9 | 3 |  | -1 | 0 | -2 | 3 | 5 | 0 | 6 | 10 | -1 | 11 | 0 | 0 | 0 | 2 | 5 | 5 | 46 | 82 | 1 |  | -12 | -1 | -11 | 0 | -1 | 0 | 203 | 13 | 0 | 0 | 0 | 0 | 0 | 0
1208 | Medlink | PINT | 325 | 332 | 318 |  | 305 | 312 | 297 | -103 | -103 | -103 | -2074 | -2023 | -2125 | 12 | 398 | 998 | 1068 | 2 | 6 | 6 | -1600 | -1598 | -1603 | 9016 | -835 | -244 | -70 | -8 | -9 | -86 | 538 | 46 | 18 | 18 | 18 | 0 | 0 | 0
1209 | Latvia and Lithuania cross-border strengthening project | PINT | 52 | 58 | 44 |  | 11 | 12 | 9 | 26 | 33 | 17 | -72 | -63 | -81 | 1 | 14 | 34 | 37 | 0 | 0 | 0 | 404 | 521 | 275 |  | -51 | -1 | -38 | -1 | -2 | -1 | -70 | 0 | 265 | 265 | 265 | 3 | 3 | 3
1210 | APOLLO-LINK | Light PINT | 956 | 958 | 955 |  | 217 | 220 | 213 | 475 | 476 | 475 | -1477 | -1451 | -1496 |  | 284 | 711 | 761 |  |  |  | 7575 | 8080 | 7237 |  | -674 | -207 | -33 | -6 | -6 | -73 |  |  | 285 | 285 | 285 | 3 | 3 | 3
1211 | Baltic WindConnector (BWC) | PINT | 657 | 709 | 598 | 142 | 45 | 51 | 39 | 493 | 523 | 472 | -309 | -269 | -347 | 21 | 59 | 149 | 159 | 4 | 10 | 11 | 7644 | 8166 | 7190 | 2000 | -73 | -39 | -11 | 0 | 0 | -13 | 352 | 25 | 1594 | 1594 | 1594 | 21 | 21 | 21
1213 | Offshore hybrid Interconnector (DE-NL) | Light PINT | 181 | 190 | 176 |  | 17 | 19 | 16 | 57 | 66 | 52 | -115 | -107 | -129 |  | 22 | 55 | 59 |  |  |  | 878 | 1033 | 786 |  | -94 | -15 | -41 | -2 | -3 | -6 |  |  | 418 | 418 | 418 | 7 | 7 | 7
1214 | Hybrid Interconnector Denmark-Germany | TOOT | 620 | 633 | 610 | 86 | 50 | 52 | 49 | 576 | 580 | 571 | -340 | -331 | -352 | 104 | 65 | 164 | 175 | 20 | 50 | 54 | 8956 | 9133 | 8798 | 2000 | -227 | -34 | -99 | -4 | -6 | -13 | 2380 | 147 | 0 | 0 | 0 | 0 | 0 | 0
1215 | Xlinks Morocco - Germany | PINT | 1072 | 1113 | 1037 |  | 155 | 165 | 146 | -54 | -53 | -55 | -1054 | -991 | -1120 | 230 | 202 | 507 | 543 | 44 | 111 | 118 | -846 | -829 | -863 | 15200 | -712 | -99 | -341 | -15 | -21 | -38 | 4049 | 259 | 130 | 130 | 130 | 3 | 3 | 3
1216 | High-Voltage Direct Current Interconnector Project Romania-Hungary | PINT | 41 | 45 | 36 |  | 9 | 14 | 5 | 8 | 12 | 1 | -63 | -32 | -97 | 14 | 12 | 31 | 33 | 3 | 7 | 7 | 122 | 183 | 15 |  | -51 | -14 | -11 | -1 | -1 | -5 | 119 | 10 | 36 | 36 | 36 | 0 | 0 | 0
1217 | Further Development of Offshore Renewables (MOG 3) | Light PINT | 50 | 60 | 41 | 360 | 28 | 29 | 26 | 454 | 460 | 450 | -191 | -179 | -198 |  | 37 | 92 | 98 |  |  |  | 7030 | 7061 | 7010 |  | -78 | -17 | -23 | -1 | -2 | -6 |  |  | 454 | 454 | 454 | 5 | 5 | 5
1218 | Hybrid HVDC Interconnector BE-NL | Light PINT | 57 | 62 | 47 |  | 6 | 7 | 5 | 22 | 27 | 13 | -42 | -36 | -49 |  | 8 | 20 | 22 |  |  |  | 336 | 422 | 204 |  | -48 | -12 | -9 | -1 | -1 | -4 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1219 | Bofferdange- Bertrange | Light PINT | 39 | 44 | 31 |  | 2 | 3 | 1 | 10 | 17 | 6 | -15 | -9 | -19 |  | 3 | 7 | 7 |  |  |  | 148 | 271 | 84 |  | -12 | -3 | -5 | 0 | 0 | -1 |  |  | 81 | 81 | 81 | 1 | 1 | 1
1220 | Offshore Wind Connection Viana do Castelo | TOOT | 5 | 14 | 0 | 45 | 5 | 8 | 4 | 155 | 157 | 153 | -36 | -25 | -51 | 3 | 7 | 17 | 19 | 0 | 1 | 1 | 2221 | 2443 | 1888 | 2000 | 0 | -2 | -4 | 0 | 0 | -1 | 140 | 6 | 243 | 243 | 243 | 2 | 2 | 2
1221 | Offshore Wind Connection Leixões | TOOT | 2 | 7 | 0 | 36 | 5 | 9 | 2 | 117 | 118 | 115 | -33 | -16 | -59 | 0 | 6 | 16 | 17 | 0 | 0 | 0 | 1798 | 1849 | 1746 | 1500 | -3 | -1 | -1 | 0 | 0 | 0 | 134 | 5 | 184 | 184 | 184 | 2 | 2 | 2
1222 | Offshore Wind Connection Figueira da Foz (North) | TOOT | 17 | 26 | 9 | 33 | 5 | 8 | 4 | 155 | 157 | 153 | -36 | -25 | -51 | 1 | 7 | 17 | 19 | 0 | 1 | 1 | 2221 | 2443 | 1888 | 2000 | 0 | -2 | -4 | 0 | 0 | -1 | 121 | 6 | 245 | 245 | 245 | 2 | 2 | 2
1223 | Offshore Wind Connection Figueira da Foz (South) | TOOT | 17 | 26 | 9 | 33 | 5 | 8 | 4 | 155 | 157 | 153 | -36 | -25 | -51 | 1 | 7 | 17 | 19 | 0 | 1 | 1 | 2221 | 2443 | 1888 | 2000 | 0 | -2 | -4 | 0 | 0 | -1 | 133 | 6 | 244 | 244 | 244 | 2 | 2 | 2
1224 | Offshore Wind Connection Ericeira | TOOT | 2 | 6 | 0 | 24 | 4 | 5 | 2 | 74 | 74 | 74 | -25 | -17 | -36 | 1 | 5 | 12 | 13 | 0 | 0 | 0 | 1148 | 1163 | 1132 | 1000 | -7 | -3 | -11 | 0 | -1 | -1 | 15 | 3 | 118 | 118 | 118 | 1 | 1 | 1
1225 | Offshore Wind Connection Sines | TOOT | 14 | 19 | 7 | 24 | 5 | 9 | 2 | 117 | 118 | 115 | -33 | -16 | -59 | 0 | 6 | 16 | 17 | 0 | 0 | 0 | 1798 | 1849 | 1746 | 1500 | -3 | -1 | -1 | 0 | 0 | 0 | -64 | 3 | 179 | 179 | 179 | 2 | 2 | 2
1226 | North-South Electricity Corridor in Eastern Europe | Light PINT | 251 | 349 | 185 |  | 58 | 60 | 55 | 35 | 36 | 33 | -393 | -376 | -410 |  | 75 | 189 | 202 |  |  |  | 539 | 555 | 523 |  | -430 | -139 | -12 | -4 | -3 | -48 |  |  | 148 | 148 | 148 | 2 | 2 | 2
1229 | Rhine-Main-Link | PINT | 1653 | 1994 | 1409 |  | 99 | 125 | 79 | 650 | 795 | 547 | -676 | -536 | -852 | 46 | 130 | 325 | 348 | 9 | 22 | 24 | 5 | 8 | 1 |  | -234 | -74 | -7 | -2 | -2 | -26 | 1451 | 69 | 0 | 0 | 0 | 0 | 0 | 0
1230 | TuNur Malta | PINT | 19 | 20 | 17 |  | 60 | 63 | 58 | -6 | 3 | -15 | -409 | -393 | -430 | 0 | 79 | 197 | 211 | 0 | 0 | 0 | -98 | 41 | -227 | 1400 | -165 | -51 | -8 | -1 | -2 | -18 | -96 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1231 | Green Aegean Interconnector | Light PINT | 1203 | 1206 | 1201 |  | 306 | 335 | 263 | 277 | 281 | 275 | -2081 | -1791 | -2278 |  | 400 | 1001 | 1072 |  |  |  | 4296 | 4397 | 4190 |  | -586 | -139 | -139 | -8 | -11 | -50 |  |  | 2687 | 2687 | 2687 | 35 | 35 | 35
1233 | Laufenburg - Beznau - Breite | Light PINT | 43 | 51 | 35 |  | 43 | 52 | 32 | 104 | 113 | 97 | -290 | -214 | -352 |  | 56 | 140 | 149 |  |  |  | 1610 | 1759 | 1476 |  | -130 | -49 | -14 | -1 | 0 | -17 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1234 | 220-kV Reitdorf (AT) - Weißenbach (AT) | TOOT | 4 | 8 | 1 | 51 | 7 | 8 | 6 | 51 | 51 | 50 | -49 | -42 | -56 | 1 | 9 | 24 | 25 | 0 | 1 | 1 | 785 | 799 | 769 | 500 | -21 | -6 | -4 | 0 | 0 | -2 | -59 | -1 | 4 | 4 | 4 | 0 | 0 | 0
1235 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | PINT | 7 | 11 | 2 |  | 2 | 3 | 1 | 3 | 5 | 0 | -12 | -5 | -23 | -1 | 2 | 6 | 6 | 0 | -1 | -1 | 44 | 74 | 4 |  | -22 | -2 | -12 | 0 | -1 | -1 | -438 | -27 | 13 | 13 | 13 | 0 | 0 | 0
1236 | Power-to-Gas for Austria (P2G4A) | PINT | 1 | 2 | 0 |  | 0 | 2 | -1 | 0 | 9 | -10 | -2 | 6 | -11 | 3 | 0 | 1 | 1 | 1 | 1 | 2 | 4 | 141 | -162 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0
1239 | Interconnection Ukraine-Slovak Republic | Light PINT | 4 | 13 | 0 |  | 4 | 10 | -1 | 5 | 7 | 4 | -27 | 7 | -71 |  | 5 | 13 | 14 |  |  |  | 79 | 108 | 63 |  | -13 | 0 | -13 | 0 | -1 | 0
1240 | Interconnection Ukraine-Romania | Light PINT | 3 | 6 | 1 |  | 18 | 26 | 8 | 10 | 17 | 2 | -126 | -55 | -176 |  | 24 | 60 | 65 |  |  |  | 161 | 258 | 35 |  | -53 | -2 | -58 | -2 | -3 | -1

## 2040DE-EU27
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_Producer | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | avg | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 89 | 93 | 86 | 130.4 | 34 | 39 | 27 | 239 | 285 | 179 | -234 | -187 | -262 | 1 | 45 | 113 | 121 | 0 | 1 | 1 | 3400 | 4001 | 2555 | 1154 | -62 | -6 | -29 | -1 | -2 | -2 | 349 | 15 | 2251 | 2251 | 2251 | 18 | 18 | 18
4 | Interconnection Portugal-Spain | TOOT | 141 | 145 | 135 |  | 23 | 25 | 21 | 143 | 153 | 130 | -156 | -144 | -168 | 3 | 30 | 75 | 80 | 1 | 1 | 1 | 2030 | 2194 | 1853 |  | -48 | -7 | -21 | -1 | -1 | -3 | 60 | 9 | 606 | 606 | 606 | 4 | 4 | 4
16 | Biscay Gulf | TOOT | 335 | 340 | 326 |  | 73 | 77 | 66 | 216 | 216 | 215 | -497 | -452 | -525 | 36 | 95 | 239 | 256 | 7 | 17 | 18 | 3055 | 3094 | 3017 |  | -163 | -36 | -36 | -2 | -3 | -13 | 3415 | 128 | 3664 | 3664 | 3664 | 55 | 55 | 55
28 | Italy-Montenegro | TOOT | 1 | 1 | 1 |  | 27 | 30 | 24 | 34 | 35 | 30 | -182 | -165 | -203 | 0 | 35 | 88 | 94 | 0 | 0 | 0 | 479 | 509 | 433 |  | -41 | -15 | 1 | 0 | 0 | -5 | 159 | 6 | 319 | 319 | 319 | 7 | 7 | 7
29 | Italy-Tunisia | TOOT | 115 | 140 | 91 |  | -7 | 29 | -33 | 27 | 35 | 20 | 180 | 221 | 120 | -7 | 0 | 0 | 0 | -1 | -3 | -3 | 379 | 492 | 285 |  | -67 | -15 | -19 | -1 | -1 | -5 | -200 | -16 | 41 | 41 | 41 | 1 | 1 | 1
33 | Central Northern Italy | TOOT | 52 | 56 | 47 |  | 9 | 11 | 7 | 18 | 24 | 15 | -55 | -31 | -72 | 1 | 12 | 30 | 32 | 0 | 0 | 1 | 242 | 342 | 178 |  | -42 | -13 | -2 | 0 | 0 | -4 | 93 | -2 | 230 | 230 | 230 | 3 | 3 | 3
35 | CZ Southwest-east corridor | TOOT | 182 | 184 | 181 |  | 48 | 50 | 46 | 61 | 64 | 58 | -330 | -315 | -339 | 23 | 63 | 159 | 170 | 4 | 11 | 12 | 869 | 905 | 831 |  | -208 | -57 | -41 | -3 | -3 | -20 | 402 | 20 | 487 | 487 | 487 | 6 | 6 | 6
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 54 | 58 | 51 |  | 4 | 5 | 3 | 27 | 32 | 23 | -24 | -19 | -33 |  | 5 | 12 | 12 |  |  |  | 387 | 463 | 326 |  | -15 | -1 | -10 | 0 | -1 | 0 |  |  | 727 | 727 | 727 | 9 | 9 | 9
47 | Westtirol (AT) - Vöhringen (DE) | TOOT | 109 | 112 | 107 |  | 8 | 9 | 6 | 41 | 43 | 38 | -53 | -44 | -61 | 7 | 10 | 25 | 27 | 1 | 3 | 3 | 578 | 603 | 548 |  | -29 | -4 | -9 | 0 | -1 | -2 | 73 | -9 | 796 | 796 | 796 | 10 | 10 | 10
81 | North South Interconnector | TOOT | 80 | 85 | 75 |  | -13 | -12 | -15 | 114 | 115 | 113 | 88 | 99 | 82 | 3 | 0 | 0 | 0 | 1 | 2 | 2 | 1615 | 1620 | 1610 |  | -35 | -11 | -4 | 0 | 0 | -4 | 32 | 4 | 330 | 330 | 330 | 3 | 3 | 3
85 | Integration of RES in Alentejo | TOOT | 0 | 1 | 0 | 8 | 0 | 1 | -1 | 9 | 12 | 7 | 1 | 8 | -9 | -1 | 0 | 0 | 0 | 0 | -1 | -1 | 135 | 169 | 100 | 700 | -3 | 0 | -5 | 0 | 0 | 0 | -36 | -2 | 0 | 0 | 0 | 0 | 0 | 0
94 | GerPol Improvements | TOOT | 322 | 325 | 320 |  | 38 | 40 | 37 | 105 | 107 | 103 | -262 | -249 | -275 | 14 | 50 | 126 | 135 | 3 | 7 | 7 | 1498 | 1532 | 1452 |  | -193 | -34 | -93 | -4 | -6 | -12 | 368 | 19 | 1994 | 1994 | 1994 | 26 | 26 | 26
107 | Celtic Interconnector | TOOT | 251 | 255 | 249 |  | 29 | 30 | 28 | 159 | 163 | 154 | -196 | -191 | -206 | 26 | 38 | 94 | 101 | 5 | 12 | 13 | 2263 | 2337 | 2198 |  | -70 | -22 | -7 | -1 | -1 | -8 | 1098 | 54 | 1438 | 1438 | 1438 | 14 | 14 | 14
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 71 | 76 | 68 |  | 4 | 5 | 2 | 53 | 55 | 51 | -27 | -17 | -33 | 2 | 5 | 13 | 14 | 0 | 1 | 1 | 754 | 775 | 724 |  | -41 | -4 | -25 | -1 | -2 | -1 | 56 | 2 | 1173 | 1173 | 1173 | 9 | 9 | 9
120 | Princess Elisabeth Island (MOG 2) | TOOT | 331 | 353 | 309 | 594 | 75 | 76 | 73 | 808 | 838 | 779 | -507 | -495 | -519 | 24 | 97 | 244 | 261 | 5 | 12 | 12 | 11464 | 11765 | 11163 | 3500 | -427 | -50 | -235 | -10 | -16 | -19 | 278 | 26 | 4156 | 4156 | 4156 | 190 | 190 | 190
121 | Nautilus: multi-purpose interconnector Belgium - UK | TOOT | 165 | 176 | 154 |  | 21 | 23 | 20 | 15 | 30 | -5 | -144 | -135 | -154 | 12 | 28 | 69 | 74 | 2 | 6 | 6 | 216 | 417 | -72 |  | -83 | -20 | -14 | -1 | -1 | -7 | 82 | 7 | 837 | 837 | 837 | 54 | 54 | 54
124 | Ekhyddan-Nybro-Hemsjö | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 69 | 69 | 68 |  | 6 | 12 | 3 | 11 | 11 | 10 | -44 | -23 | -79 | 20 | 8 | 21 | 23 | 4 | 10 | 11 | 153 | 162 | 144 |  | -38 | -7 | -20 | -1 | -1 | -2 | 140 | 14 | 79 | 79 | 79 | 0 | 0 | 0
127 | Central Southern Italy | TOOT | 22 | 35 | 12 |  | 3 | 6 | -5 | 4 | 7 | 0 | -35 | -28 | -42 | 22 | 4 | 9 | 10 | 4 | 10 | 11 | 55 | 94 | -2 |  | -24 | -6 | -5 | 0 | 0 | -2 | 177 | 9 | 453 | 453 | 453 | 0 | 0 | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 606 | 699 | 541 |  | 15 | 19 | 13 | 225 | 270 | 195 | -105 | -90 | -128 | 8 | 20 | 50 | 54 | 1 | 4 | 4 | 2 | 3 | 2 |  | -79 | -25 | -2 | -1 | -1 | -9 | 240 | 8 | 0 | 0 | 0 | 0 | 0 | 0
132 | HVDC Line A-North | TOOT | 970 | 1172 | 841 |  | 25 | 32 | 20 | 357 | 452 | 294 | -168 | -139 | -216 | 48 | 32 | 81 | 87 | 9 | 23 | 25 | 4 | 5 | 3 |  | -127 | -40 | -4 | -1 | -1 | -14 | 1003 | 58 | 0 | 0 | 0 | 0 | 0 | 0
138 | Black Sea Corridor | TOOT | 16 | 19 | 13 |  | 1 | 2 | 0 | 4 | 9 | 0 | 0 | 3 | -5 | -15 | 1 | 2 | 3 | -3 | -7 | -8 | 57 | 133 | 1 |  | 5 | -2 | 18 | 0 | 1 | -1 | -33 | -5 | 522 | 522 | 522 | 0 | 0 | 0
144 | Mid Continental East corridor | TOOT | 40 | 49 | 32 |  | 3 | 4 | 2 | 6 | 9 | 4 | -23 | -12 | -29 | 23 | 4 | 11 | 12 | 4 | 11 | 12 | 84 | 133 | 58 |  | 16 | -3 | 29 | 1 | 1 | -1 | 71 | 6 | 950 | 950 | 950 | 8 | 8 | 8
150 | Italy-Slovenia | TOOT | 40 | 46 | 30 |  | 18 | 22 | 16 | 11 | 13 | 9 | -123 | -108 | -147 | 11 | 24 | 59 | 63 | 2 | 5 | 6 | 161 | 182 | 127 |  | -29 | -8 | -14 | -1 | -1 | -3 | 131 | 9 | 252 | 252 | 252 | 3 | 3 | 3
153 | France-Alderney-Britain | TOOT | 108 | 127 | 92 |  | 21 | 22 | 20 | 41 | 42 | 40 | -142 | -136 | -153 | 15 | 27 | 68 | 73 | 3 | 7 | 8 | 577 | 583 | 572 |  | -59 | -12 | -15 | -1 | -1 | -4 | 998 | 55 | 549 | 549 | 549 | 22 | 22 | 22
170 | Baltic States Synchronization with Continental Europe | TOOT | 176 | 179 | 173 |  | 82 | 86 | 78 | 77 | 81 | 75 | -555 | -533 | -587 | 2 | 107 | 267 | 286 | 0 | 1 | 1 | 1095 | 1140 | 1072 |  | -290 | -48 | -193 | -7 | -13 | -17 | 153 | 10 | 1379 | 1379 | 1379 | 23 | 23 | 23
174 | Greenconnector | TOOT | 85 | 112 | 64 |  | 46 | 51 | 37 | 22 | 25 | 18 | -313 | -253 | -344 | 26 | 60 | 151 | 161 | 5 | 12 | 13 | 306 | 350 | 263 |  | -134 | -40 | -8 | -1 | -1 | -14 | 408 | 26 | 793 | 793 | 793 | 24 | 24 | 24
176 | Hansa PowerBridge I | TOOT | 168 | 173 | 160 |  | 8 | 9 | 7 | 79 | 80 | 77 | -55 | -48 | -60 | -1 | 11 | 27 | 28 | 0 | -1 | -1 | 1125 | 1152 | 1104 |  | -35 | -10 | -2 | 0 | 0 | -3 | 1 | -1 | 1470 | 1470 | 1470 | 18 | 18 | 18
187 | St. Peter (AT) - Pleinting (DE) | TOOT | 531 | 535 | 526 |  | 41 | 44 | 37 | 189 | 197 | 183 | -281 | -251 | -296 | 50 | 54 | 135 | 144 | 10 | 24 | 26 | 2691 | 2766 | 2611 |  | -192 | -31 | -72 | -3 | -5 | -11 | 1579 | 74 | 4670 | 4670 | 4670 | 57 | 57 | 57
200 | CZ Northwest-South corridor | TOOT | 182 | 184 | 181 |  | 48 | 50 | 46 | 61 | 64 | 58 | -330 | -315 | -339 | -10 | 63 | 159 | 170 | -2 | -5 | -5 | 869 | 905 | 831 |  | -208 | -57 | -41 | -3 | -3 | -20 | 259 | 7 | 493 | 493 | 493 | 6 | 6 | 6
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 42 | 46 | 40 |  | 10 | 11 | 10 | 11 | 16 | 5 | -71 | -67 | -78 | 2 | 14 | 34 | 37 | 0 | 1 | 1 | 154 | 218 | 74 |  | -32 | -8 | -7 | 0 | -1 | -3 | 33 | 2 | 94 | 94 | 94 | 1 | 1 | 1
219 | Great Sea Interconnector | TOOT | 370 | 394 | 343 |  | -8 | 29 | -36 | 88 | 94 | 78 | 187 | 246 | 116 | 60 | 0 | 0 | 0 | 12 | 29 | 31 | 1246 | 1317 | 1112 |  | -104 | -34 | -3 | -1 | -1 | -12 | -2354 | -172 | 108 | 108 | 108 | 1 | 1 | 1
225 | 2nd interconnector Belgium - Germany | light PINT | 204 | 218 | 193 |  | 11 | 11 | 10 | 109 | 112 | 103 | -74 | -70 | -78 | 20 | 14 | 36 | 38 | 4 | 10 | 10 | 1548 | 1599 | 1477 |  | -63 | -4 | -53 | -2 | -3 | -2 | 919 | 50 | 2040 | 2040 | 2040 | 25 | 25 | 25
227 | Transbalkan Corridor | TOOT | 50 | 66 | 28 |  | 26 | 29 | 24 | 16 | 26 | 9 | -178 | -161 | -196 | 8 | 34 | 86 | 92 | 2 | 4 | 4 | 230 | 364 | 137 |  | -351 | -106 | -38 | -4 | -4 | -37 | 60 | 4 | 1864 | 1864 | 1864 | 20 | 20 | 20
228 | Muhlbach - Eichstetten | TOOT | 79 | 87 | 73 |  | 3 | 4 | 2 | 33 | 35 | 30 | -24 | -15 | -29 | 6 | 5 | 11 | 12 | 1 | 3 | 3 | 465 | 506 | 424 |  | -14 | -4 | -3 | 0 | 0 | -1 | 179 | 9 | 630 | 630 | 630 | 8 | 8 | 8
231 | Beznau - Tiengen | TOOT | 25 | 30 | 18 |  | 17 | 21 | 13 | 60 | 64 | 56 | -115 | -89 | -141 | 6 | 22 | 55 | 59 | 1 | 3 | 3 | 856 | 901 | 795 |  | -78 | -22 | -5 | -1 | -1 | -8 | 60 | -11 | 128 | 128 | 128 | 2 | 2 | 2
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 1438 | 1656 | 1233 |  | 34 | 43 | 29 | 508 | 619 | 423 | -232 | -198 | -290 | 72 | 45 | 112 | 120 | 14 | 35 | 37 | 5 | 6 | 4 |  | -176 | -55 | -5 | -1 | -1 | -19 | 1948 | 100 | 0 | 0 | 0 | 0 | 0 | 0
239 | Fenno-Skan 3 | Light PINT | 59 | 60 | 57 |  | 5 | 8 | 3 | 40 | 47 | 34 | -37 | -22 | -52 |  | 7 | 18 | 19 |  |  |  | 577 | 669 | 482 |  | -65 | -3 | -40 | -2 | -2 | -2 |  |  | 172 | 172 | 172 | 2 | 2 | 2
243 | New 400 kV interconnection line between Serbia and Croatia | Light PINT | 14 | 24 | 9 |  | 7 | 13 | 3 | 0 | 7 | -5 | -46 | -21 | -88 |  | 9 | 22 | 24 |  |  |  | 1 | 102 | -76 |  | -71 | -22 | -4 | -1 | -1 | -8 |  |  | 6 | 6 | 6 | 0 | 0 | 0
244 | Vigy - Uchtelfangen area | TOOT | 398 | 415 | 376 |  | 22 | 23 | 20 | 156 | 165 | 147 | -148 | -137 | -154 | 51 | 28 | 71 | 76 | 10 | 24 | 26 | 2224 | 2360 | 2110 |  | -128 | -20 | -58 | -3 | -4 | -8 | 1031 | 58 | 3208 | 3208 | 3208 | 39 | 39 | 39
247 | AQUIND Interconnector | TOOT | 182 | 211 | 156 |  | 37 | 39 | 35 | 69 | 71 | 67 | -252 | -236 | -268 | 19 | 48 | 121 | 130 | 4 | 9 | 10 | 979 | 1001 | 958 |  | -105 | -21 | -30 | -2 | -2 | -8 | 796 | 48 | 1091 | 1091 | 1091 | 39 | 39 | 39
250 | Merchant line Castasegna (CH) - Mese (IT) | TOOT | 18 | 21 | 15 |  | 8 | 9 | 5 | 4 | 4 | 4 | -53 | -37 | -64 | 5 | 10 | 25 | 27 | 1 | 2 | 2 | 56 | 59 | 54 |  | -20 | -7 | 2 | 0 | 0 | -2 | 29 | 5 | 88 | 88 | 88 | 4 | 4 | 4
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 276 | 313 | 236 |  | 5 | 5 | 5 | 80 | 88 | 74 | -33 | -31 | -35 | 36 | 6 | 16 | 17 | 7 | 17 | 19 | 1 | 1 | 1 |  | -25 | -8 | -1 | 0 | 0 | -3 | 848 | 46 | 0 | 0 | 0 | 0 | 0 | 0
259 | HU-RO | TOOT | 73 | 78 | 69 |  | 5 | 7 | 3 | 2 | 6 | -2 | -31 | -20 | -46 | 39 | 6 | 15 | 16 | 8 | 19 | 20 | 29 | 89 | -31 |  | 34 | -3 | 44 | 1 | 2 | -1 | 168 | 12 | 1087 | 1087 | 1087 | 10 | 10 | 10
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | TOOT | 190 | 204 | 176 |  | 20 | 21 | 18 | 74 | 79 | 68 | -133 | -125 | -145 | 35 | 26 | 64 | 69 | 7 | 17 | 18 | 1054 | 1125 | 977 |  | -102 | -22 | -29 | -2 | -2 | -8 | 303 | 24 | 991 | 991 | 991 | 45 | 45 | 45
267 | Hansa PowerBridge II | Light PINT | 168 | 173 | 160 |  | 8 | 9 | 7 | 79 | 80 | 77 | -55 | -48 | -60 | -1 | 11 | 27 | 28 | 0 | -1 | -1 | 1125 | 1152 | 1104 |  | -35 | -10 | -2 | 0 | 0 | -3 | 1 | -1 | 1470 | 1470 | 1470 | 18 | 18 | 18
270 | FR-ES project -Aragón-Atlantic Pyrenees | TOOT | 230 | 252 | 214 |  | 48 | 49 | 47 | 133 | 156 | 101 | -328 | -319 | -336 | 19 | 63 | 158 | 169 | 4 | 9 | 10 | 1886 | 2187 | 1450 |  | -121 | -23 | -33 | -2 | -2 | -9 | 1771 | 68 | 2215 | 2215 | 2215 | 31 | 31 | 31
276 | FR-ES project -Navarra-Landes | PINT | 180 | 185 | 176 |  | 42 | 46 | 35 | 128 | 130 | 127 | -284 | -237 | -315 | 32 | 54 | 136 | 146 | 6 | 15 | 16 | 1817 | 1859 | 1775 |  | -43 | -16 | 7 | 0 | 0 | -6 | 2575 | 103 | 729 | 729 | 729 | 9 | 9 | 9
280 | FR-BE: Lonny-Achene-Gramme | TOOT | 182 | 189 | 177 |  | 6 | 8 | 5 | 56 | 61 | 50 | -40 | -34 | -52 | 18 | 8 | 19 | 21 | 3 | 9 | 9 | 804 | 878 | 712 |  | -30 | -10 | 6 | 0 | 0 | -4 | 452 | 24 | 832 | 832 | 832 | 30 | 30 | 30
283 | TuNur Italy | PINT | 55 | 128 | 5 |  | 106 | 108 | 105 | -93 | -76 | -110 | -724 | -715 | -733 | 8 | 139 | 348 | 373 | 2 | 4 | 4 | -1323 | -1097 | -1572 | 5000 | -346 | -88 | -68 | -4 | -6 | -31 | -59 | -4 | 0 | 0 | 0 | 0 | 0 | 0
285 | GridLink | TOOT | 108 | 127 | 92 |  | 21 | 22 | 20 | 41 | 42 | 40 | -142 | -136 | -153 | 17 | 27 | 68 | 73 | 3 | 8 | 9 | 577 | 583 | 572 |  | -59 | -12 | -15 | -1 | -1 | -4 | 493 | 30 | 566 | 566 | 566 | 22 | 22 | 22
297 | BRABO III | TOOT | 74 | 76 | 72 |  | 5 | 5 | 4 | 48 | 50 | 46 | -32 | -26 | -36 | 7 | 6 | 16 | 17 | 1 | 3 | 4 | 683 | 717 | 654 |  | -35 | -3 | -26 | -1 | -2 | -1 | 162 | 8 | 521 | 521 | 521 | 30 | 30 | 30
299 | SACOI 3 | TOOT | 176 | 179 | 173 |  | 98 | 100 | 97 | 23 | 25 | 22 | -668 | -658 | -677 | -2 | 128 | 321 | 344 | 0 | -1 | -1 | 329 | 350 | 309 |  | -2063 | -2 | -1371 | -53 | -74 | -20 | -67 | -6 | 688 | 688 | 688 | 14 | 14 | 14
309 | NeuConnect | TOOT | 189 | 201 | 175 |  | 35 | 38 | 32 | 79 | 82 | 77 | -237 | -217 | -257 | 37 | 45 | 114 | 122 | 7 | 18 | 19 | 1127 | 1145 | 1101 |  | -170 | -27 | -72 | -3 | -5 | -10 | 506 | 34 | 3012 | 3012 | 3012 | 37 | 37 | 37
312 | St. Peter (AT) - Tauern (AT) | TOOT | 408 | 413 | 404 |  | 31 | 34 | 29 | 148 | 153 | 141 | -211 | -197 | -228 | -32 | 41 | 101 | 109 | -6 | -15 | -16 | 2105 | 2153 | 2019 |  | -144 | -23 | -51 | -3 | -4 | -9 | -233 | -17 | 3588 | 3588 | 3588 | 44 | 44 | 44
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 269 | 273 | 266 |  | 23 | 28 | 20 | 97 | 101 | 93 | -158 | -138 | -193 | -18 | 30 | 76 | 81 | -3 | -9 | -9 | 1374 | 1422 | 1336 |  | -89 | -13 | -31 | -2 | -2 | -5 | 371 | 6 | 2307 | 2307 | 2307 | 28 | 28 | 28
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 5 | 11 | 1 |  | 1 | 2 | -1 | 5 | 10 | 0 | -5 | 4 | -13 | 26 | 1 | 2 | 3 | 5 | 13 | 13 | 69 | 143 | 4 |  | 1 | 0 | 2 | 0 | 0 | 0 | 274 | 18 | 9 | 9 | 9 | 0 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 8 | 15 | 3 |  | 1 | 3 | -1 | 4 | 7 | 2 | -9 | 4 | -21 | 27 | 2 | 4 | 5 | 5 | 13 | 14 | 53 | 102 | 27 |  | -5 | -1 | -3 | 0 | 0 | -1 | 284 | 18 | 24 | 24 | 24 | 0 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | TOOT | 199 | 201 | 198 |  | 76 | 81 | 71 | 57 | 61 | 53 | -517 | -484 | -551 | 9 | 99 | 249 | 266 | 2 | 4 | 5 | 811 | 869 | 751 |  | -194 | -68 | 15 | -1 | 0 | -24 | 191 | 11 | 737 | 737 | 737 | 9 | 9 | 9
328 | Interconnector DE-LUX | TOOT | 50 | 52 | 48 |  | -1 | 1 | -3 | 5 | 8 | 2 | 13 | 20 | 6 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 72 | 116 | 33 |  | -3 | 0 | -1 | 0 | 0 | 0 | -198 | -20 | 46 | 46 | 46 | 1 | 1 | 1
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 232 | 269 | 219 |  | 83 | 96 | 78 | 180 | 209 | 170 | -1816 | -2843 | -1503 | -8 | 615 | 1140 | 1202 | -2 | -4 | -4 | 3630 | 3568 | 3690 |  | -2080 | -138 | -2107 | -111 | -190 | -47 | -351 | -30 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | TOOT | 123 | 130 | 115 |  | 3 | 4 | 1 | 4 | 7 | 1 | -18 | -8 | -27 | 18 | 4 | 9 | 9 | 3 | 9 | 9 | 61 | 95 | 21 |  | -13 | -10 | 18 | 0 | 1 | -3 | 66 | 8 | 256 | 256 | 256 | 2 | 2 | 2
335 | North Sea Wind Power Hub | Light PINT | 1811 | 1819 | 1804 | 1326 | 227 | 232 | 222 | 2865 | 2874 | 2856 | -1545 | -1512 | -1578 |  | 297 | 743 | 796 |  |  |  | 40620 | 40932 | 40307 | 14000 | -1058 | -140 | -500 | -22 | -31 | -54 |  |  | 4973 | 4973 | 4973 | 61 | 61 | 61
338 | Adriatic HVDC link | TOOT | 137 | 141 | 132 |  | 30 | 33 | 29 | 54 | 60 | 44 | -207 | -199 | -222 | 27 | 40 | 100 | 107 | 5 | 13 | 14 | 761 | 848 | 633 |  | -142 | -38 | -22 | -2 | -2 | -14 | 372 | 15 | 1353 | 1353 | 1353 | 11 | 11 | 11
339 | Tyrrhenian link | TOOT | 99 | 105 | 95 |  | 2 | 31 | -30 | 52 | 62 | 47 | -182 | -127 | -213 | 13 | 3 | 8 | 8 | 3 | 6 | 7 | 704 | 728 | 668 |  | -98 | -28 | -9 | -1 | -1 | -10 | 401 | 12 | 1436 | 1436 | 1436 | 0 | 0 | 0
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 258 | 294 | 189 |  | 92 | 105 | 68 | 201 | 229 | 147 | -2563 | -3132 | -1285 | -5 | 869 | 1610 | 1697 | -1 | -2 | -2 | 3659 | 3094 | 4045 |  | -3036 | -182 | -3444 | -152 | -293 | -63 | -605 | -45 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | TOOT | 5 | 6 | 4 |  | 2 | 4 | 0 | 4 | 12 | -2 | -13 | 0 | -27 | 115 | 2 | 6 | 7 | 22 | 55 | 59 | 51 | 178 | -28 |  | 1 | -1 | 8 | 0 | 0 | 0 | 1162 | 75 | 105 | 105 | 105 | 0 | 0 | 0
342 | Central Balkan Corridor | TOOT | 7 | 7 | 6 |  | 1 | 2 | 0 | 3 | 6 | 0 | 0 | 6 | -5 | 5 | 1 | 3 | 3 | 1 | 2 | 2 | 41 | 79 | -2 |  | 9 | 0 | 3 | 0 | 0 | 0 | 37 | 1 | 336 | 336 | 336 | 3 | 3 | 3
343 | CSE1 New | TOOT | 8 | 9 | 7 |  | 1 | 3 | -1 | -2 | 3 | -5 | -7 | 4 | -18 | 13 | 1 | 3 | 4 | 3 | 6 | 7 | -22 | 46 | -67 |  | -29 | -7 | -7 | 0 | -1 | -2 | 91 | 7 | 94 | 94 | 94 | 0 | 0 | 0
346 | ZuidWest380 NL Oost | TOOT | 23 | 33 | 18 |  | 0 | 1 | 0 | 7 | 9 | 5 | -1 | 3 | -5 | -4 | 0 | 1 | 1 | -1 | -2 | -2 | 96 | 131 | 68 |  | 6 | 0 | 3 | 0 | 0 | 0 | -121 | -6 | 329 | 329 | 329 | 28 | 28 | 28
349 | MaresConnect | TOOT | 71 | 87 | 56 |  | 22 | 24 | 21 | 92 | 101 | 82 | -151 | -142 | -163 | -1 | 29 | 73 | 78 | 0 | 0 | 0 | 1311 | 1423 | 1172 |  | -58 | -17 | -10 | -1 | -1 | -6 | 76 | 2 | 1540 | 1540 | 1540 | 15 | 15 | 15
350 | South Balkan Corridor | TOOT | 9 | 13 | 5 |  | 9 | 14 | 5 | 10 | 16 | 3 | -62 | -33 | -93 | 100 | 12 | 30 | 32 | 19 | 48 | 51 | 136 | 222 | 36 |  | -30 | -12 | 2 | 0 | 0 | -4 | 1156 | 73 | 6 | 6 | 6 | 0 | 0 | 0
375 | Lienz (AT) - Veneto region (IT) 220 kV | TOOT | 134 | 144 | 125 |  | 33 | 37 | 29 | 32 | 33 | 31 | -228 | -199 | -255 | 17 | 44 | 109 | 117 | 3 | 8 | 9 | 451 | 471 | 436 |  | -101 | -28 | -15 | -1 | -1 | -10 | 117 | 9 | 389 | 389 | 389 | 5 | 5 | 5
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | Light PINT | 5 | 8 | 2 |  | 5 | 8 | 3 | 7 | 11 | 5 | -31 | -19 | -53 |  | 6 | 15 | 16 |  |  |  | 102 | 158 | 71 |  | -30 | -10 | 1 | 0 | 0 | -3 |  |  | 0 | 0 | 0 | 0 | 0 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | TOOT | 74 | 76 | 72 |  | 5 | 5 | 4 | 48 | 49 | 46 | -32 | -26 | -36 | 9 | 6 | 16 | 17 | 2 | 4 | 4 | 677 | 701 | 654 |  | -35 | -3 | -26 | -1 | -2 | -1 | 187 | 9 | 504 | 504 | 504 | 30 | 30 | 30
378 | Transformer Gatica | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 226 | 292 | 184 |  | 7 | 10 | 5 | 106 | 151 | 78 | -48 | -32 | -70 | 41 | 9 | 23 | 25 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | -36 | -11 | -1 | 0 | 0 | -4 | 886 | 51 | 0 | 0 | 0 | 0 | 0 | 0
1039 | SE North-south long-term reinforcements | PINT | 55 | 64 | 44 |  | 6 | 8 | 3 | 5 | 7 | 3 | -39 | -17 | -53 | 6 | 7 | 19 | 20 | 1 | 3 | 3 | 72 | 93 | 46 |  | -24 | -4 | -11 | 0 | -1 | -2 | 140 | 4 | 80 | 80 | 80 | 0 | 0 | 0
1040 | LirIC | TOOT | 4 | 7 | 2 |  | 9 | 10 | 7 | 30 | 42 | 19 | -58 | -51 | -67 | 1 | 11 | 28 | 30 | 0 | 1 | 1 | 424 | 587 | 264 |  | -23 | -7 | -4 | 0 | 0 | -3 | 67 | 3 | 550 | 550 | 550 | 6 | 6 | 6
1041 | GREGY Green Energy Interconnector | TOOT | 530 | 532 | 529 |  | -215 | -171 | -260 | 232 | 232 | 232 | 1770 | 1770 | 1770 | 16 | 0 | 0 | 0 | 3 | 8 | 8 | 3256 | 3256 | 3256 |  | -146 | -38 | -29 | -2 | -2 | -13 | 748 | 48 | 44 | 44 | 44 | 0 | 0 | 0
1046 | Finnish North-South reinforcement | PINT | 287 | 287 | 287 |  | 14 | 14 | 14 | 413 | 413 | 413 | 95.093 | 95.093 | 95.093 | -1 | 18 | 46 | 49 | 0 | 0 | 0 | 6463 | 6463 | 6463 |  | -15 | -4 | -14 | 0 | -1 | -1 | -138 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 67 | 72 | 64 |  | -35 | -29 | -41 | 38 | 42 | 32 | 256 | 292 | 198 | -65 | 0 | 0 | 0 | -12 | -31 | -34 | 546 | 606 | 448 |  | -22 | -6 | -3 | 0 | 0 | -2 | -4568 | -289 | 1 | 1 | 1 | 0 | 0 | 0
1049 | Cronos Energy Ltd | PINT | 130 | 130 | 130 |  | 30 | 31 | 29 | -6 | 7 | -16 | -202 | -198 | -208 | 8 | 39 | 97 | 104 | 2 | 4 | 4 | -89 | 107 | -228 |  | -148 | -24 | -61 | -3 | -4 | -9 | -106 | -1 | 526 | 526 | 526 | 14 | 14 | 14
1050 | Tarchon Energy Ltd | TOOT | 189 | 201 | 175 |  | 35 | 38 | 32 | 79 | 82 | 77 | -237 | -217 | -257 | 26 | 45 | 114 | 122 | 5 | 12 | 13 | 1127 | 1145 | 1101 |  | -170 | -27 | -72 | -3 | -5 | -10 | 330 | 21 | 3004 | 3004 | 3004 | 37 | 37 | 37
1052 | Lienz (AT) - Malta (AT) - Obersielach (AT) | TOOT | 524 | 534 | 513 | 124 | 129 | 133 | 125 | 324 | 355 | 292 | -878 | -848 | -907 | 13 | 169 | 422 | 452 | 2 | 6 | 7 | 4595 | 5097 | 4094 | 2000 | -377 | -116 | -23 | -3 | -4 | -41 | -97 | -6 | 1024 | 1024 | 1024 | 13 | 13 | 13
1054 | 220-kV Westtirol (AT) - Zell/Ziller (AT) | TOOT | 110 | 115 | 107 |  | 8 | 9 | 6 | 41 | 43 | 39 | -53 | -44 | -61 | 15 | 10 | 26 | 28 | 3 | 7 | 8 | 582 | 603 | 561 |  | -29 | -4 | -9 | 0 | -1 | -2 | 391 | 24 | 778 | 778 | 778 | 10 | 10 | 10
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 77 | 81 | 74 |  | -2 | 4 | -6 | 58 | 65 | 48 | 27 | 42 | 19 | 234 | 0 | 0 | 0 | 45 | 112 | 120 | 829 | 908 | 693 |  | 9 | 1 | 7 | 0 | 0 | 0 | 7117 | 457 | 116 | 116 | 116 | 1 | 1 | 1
1058 | HVDC Interconnector DE-CH | Light PINT | 100 | 113 | 89 |  | 18 | 21 | 13 | 95 | 98 | 94 | -123 | -85 | -144 |  | 24 | 59 | 63 |  |  |  | 1358 | 1398 | 1330 |  | -93 | -19 | -35 | -2 | -2 | -7 |  |  | 331 | 331 | 331 | 4 | 4 | 4
1059 | Southern Italy | TOOT | 8 | 11 | 3 |  | 1 | 3 | -3 | 1 | 2 | 1 | -15 | -9 | -20 | 8 | 1 | 2 | 3 | 2 | 4 | 4 | 19 | 23 | 13 |  | -20 | -3 | -9 | 0 | -1 | -1 | 152 | 3 | 686 | 686 | 686 | 0 | 0 | 0
1066 | Bulgaria - Turkey | Light PINT | 90 | 91 | 89 |  | -139 | -136 | -141 | 6 | 7 | 6 | 944 | 961 | 926 |  | 0 | 0 | 0 |  |  |  | 85 | 91 | 79 |  | -466 | -148 | -6 | -4 | -4 | -52 |  |  | 241 | 241 | 241 | 1 | 1 | 1
1067 | New AC 400 kV interconnection line Greece - Turkey | Light PINT | 82 | 84 | 79 |  | -56 | -51 | -60 | 25 | 28 | 20 | 398 | 435 | 348 |  | 0 | 0 | 0 |  |  |  | 351 | 395 | 284 |  | -69 | -18 | -12 | -1 | -1 | -7 |  |  | 33 | 33 | 33 | 0 | 0 | 0
1068 | LaSGo Link | PINT | 50 | 53 | 47 |  | 9 | 13 | 5 | 31 | 38 | 24 | -58 | -34 | -85 | 1 | 11 | 28 | 30 | 0 | 1 | 1 | 445 | 547 | 330 |  | -154 | -4 | -98 | -4 | -5 | -3 | 77 | 4 | 129 | 129 | 129 | 0 | 0 | 0
1074 | Pannonian Corridor | TOOT | 21 | 28 | 13 |  | 2 | 3 | 0 | 1 | 5 | -5 | -15 | -3 | -22 | 6 | 3 | 7 | 8 | 1 | 3 | 3 | 19 | 74 | -75 |  | 21 | -2 | 32 | 1 | 2 | -1 | 26 | 2 | 632 | 632 | 632 | 6 | 6 | 6
1085 | Malta-Italy Cable Link No.2 | TOOT | 91 | 93 | 90 |  | 28 | 35 | 21 | 21 | 21 | 21 | -193 | -145 | -235 | 4 | 37 | 93 | 99 | 1 | 2 | 2 | 300 | 305 | 292 |  | -109 | -38 | 7 | -1 | 0 | -13 | 43 | 5 | 28 | 28 | 28 | 0 | 0 | 0
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 8 | 14 | 5 | 75 | 8 | 10 | 7 | 92 | 96 | 88 | -54 | -46 | -68 | -2 | 10 | 26 | 28 | 0 | -1 | -1 | 1304 | 1376 | 1234 | 700 | -128 | -3 | -85 | -3 | -5 | -2 | -371 | -13 | 0 | 0 | 0 | 0 | 0 | 0
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | TOOT | 50 | 55 | 45 | 114 | 16 | 16 | 15 | 174 | 176 | 173 | -106 | -101 | -111 | 0 | 20 | 51 | 54 | 0 | 0 | 0 | 2475 | 2482 | 2468 | 1000 | -82 | -6 | -49 | -2 | -3 | -3 | -214 | -10 | 0 | 0 | 0 | 0 | 0 | 0
1092 | TritonLink: offshore hybrid HVDC interconnector Belgium – Denmark | TOOT | 1174 | 1219 | 1140 | 151 | 100 | 106 | 96 | 1158 | 1215 | 1096 | -682 | -650 | -719 | 29 | 131 | 328 | 351 | 6 | 14 | 15 | 16441 | 17035 | 15655 | 10000 | -520 | -64 | -290 | -12 | -19 | -24 | 435 | 30 | 6504 | 6504 | 6504 | 219 | 219 | 219
1094 | Estlink 3 | TOOT | 72 | 74 | 71 |  | 8 | 10 | 6 | 56 | 57 | 55 | -55 | -40 | -70 | 6 | 11 | 26 | 28 | 1 | 3 | 3 | 800 | 808 | 791 |  | -55 | -9 | -17 | -1 | -1 | -3 | 63 | 4 | 782 | 782 | 782 | 6 | 6 | 6
1095 | Aurora line 2 (4th AC Finland-Sweden north) | TOOT | 70 | 73 | 68 |  | 3 | 5 | 3 | 45 | 53 | 35 | -24 | -18 | -32 | 2 | 5 | 11 | 12 | 0 | 1 | 1 | 636 | 744 | 497 |  | -52 | -4 | -32 | -1 | -2 | -2 | 43 | 2 | 1178 | 1178 | 1178 | 9 | 9 | 9
1096 | Beznau - Mettlen | Light TOOT | 22 | 26 | 17 |  | 21 | 25 | 16 | 67 | 69 | 66 | -144 | -109 | -169 |  | 28 | 69 | 74 |  |  |  | 959 | 967 | 943 |  | -93 | -29 | -3 | -1 | -1 | -10 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1097 | Upgrade to Konti-Skan | PINT | 144 | 149 | 138 |  | 11 | 11 | 9 | 118 | 122 | 116 | -72 | -64 | -78 | 10 | 14 | 35 | 37 | 2 | 5 | 5 | 1686 | 1716 | 1651 |  | -20 | -5 | -1 | 0 | 0 | -2 | 264 | 14 | 177 | 177 | 177 | 0 | 0 | 0
1098 | Offshore Wind LT 2 | TOOT | 10 | 15 | 7 | 96 | 8 | 10 | 7 | 115 | 120 | 112 | -58 | -49 | -67 | 0 | 11 | 28 | 30 | 0 | 0 | 0 | 1637 | 1689 | 1597 | 700 | -61 | -2 | -39 | -2 | -2 | -1 | 104 | 5 | 121 | 121 | 121 | 1 | 1 | 1
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | TOOT | 182 | 191 | 176 |  | 48 | 50 | 45 | 64 | 68 | 60 | -329 | -307 | -342 | 20 | 63 | 158 | 169 | 4 | 9 | 10 | 907 | 959 | 855 |  | -205 | -58 | -37 | -2 | -3 | -20 | 530 | 22 | 0 | 0 | 0 | 0 | 0 | 0
1102 | Mettlen - Ulrichen | Light TOOT | 13 | 16 | 10 |  | -1 | 1 | -2 | 2 | 4 | 0 | 10 | 13 | 8 |  | 0 | 0 | 0 |  |  |  | 33 | 52 | 7 |  | 1 | -2 | 5 | 0 | 0 | -1 |  |  | 282 | 282 | 282 | 3 | 3 | 3
1103 | Bickigen - Chippis | Light TOOT | 13 | 18 | 10 |  | 14 | 16 | 11 | 49 | 49 | 48 | -94 | -74 | -109 |  | 18 | 45 | 48 |  |  |  | 697 | 712 | 682 |  | -62 | -19 | -3 | -1 | 0 | -7 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1104 | Bauler - Roost | TOOT | 3 | 4 | 1 |  | -1 | 0 | -3 | 3 | 6 | 1 | 7 | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 91 | 8 |  | -2 | 0 | -2 | 0 | 0 | 0 | -210 | -21 | 0 | 0 | 0 | 0 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 112 | 116 | 108 |  | -14 | -12 | -15 | -4 | -3 | -5 | 92 | 103 | 82 | -20 | 0 | 0 | 0 | -4 | -10 | -10 | -59 | -48 | -71 |  | -58 | -20 | 14 | 0 | 0 | -7 | -59 | -3 | 488 | 488 | 488 | 4 | 4 | 4
1106 | Bornholm Energy Island (BEI) | TOOT | 339 | 341 | 337 | 299 | 48 | 51 | 45 | 548 | 559 | 533 | -330 | -306 | -347 | -9 | 63 | 159 | 170 | -2 | -4 | -5 | 7793 | 7923 | 7616 | 3000 | -104 | -27 | -18 | -1 | -2 | -10 | -466 | -21 | 3410 | 3410 | 3410 | 42 | 42 | 42
1109 | Basilicata - Campania reinforcements | TOOT | 21 | 35 | 9 |  | 2 | 6 | -5 | 4 | 7 | -2 | -32 | -28 | -38 | -3 | 3 | 8 | 8 | -1 | -1 | -2 | 48 | 94 | -31 |  | -24 | -6 | -5 | 0 | 0 | -2 | 0 | -4 | 449 | 449 | 449 | 0 | 0 | 0
1110 | Sicily - Calabria | TOOT | 6 | 13 | 0 |  | 2 | 9 | -1 | 3 | 5 | 2 | 18 | 63 | 0 | -2 | 3 | 8 | 8 | 0 | -1 | -1 | 48 | 76 | 20 |  | 4 | 1 | 2 | 0 | 0 | 0 | 28 | -4 | 0 | 0 | 0 | 0 | 0 | 0
1112 | GRITA 2 | TOOT | 206 | 210 | 203 |  | 59 | 61 | 58 | 81 | 82 | 81 | -403 | -393 | -413 | 35 | 77 | 194 | 208 | 7 | 17 | 18 | 1154 | 1156 | 1152 |  | -94 | -34 | 9 | 0 | 0 | -12 | 509 | 37 | 1109 | 1109 | 1109 | 0 | 0 | 0
1121 | 220-kV Hessenberg (AT) - Weißenbach (AT) | TOOT | 0 | 2 | 0 | 51 | 3 | 4 | 3 | 59 | 64 | 56 | -21 | -18 | -26 | 4 | 4 | 10 | 11 | 1 | 2 | 2 | 842 | 904 | 800 | 600 | -14 | -3 | -4 | 0 | 0 | -1 | -95 | -2 | 0 | 0 | 0 | 0 | 0 | 0
1122 | Offshore Wind farm connection Centre Manche 1 | TOOT | 25 | 26 | 24 | 249 | 25 | 27 | 24 | 344 | 356 | 330 | -173 | -160 | -184 | 105 | 33 | 83 | 89 | 20 | 50 | 54 | 4978 | 5007 | 4949 | 1050 | -90 | -10 | -44 | -2 | -3 | -4 | 911 | 45 | 165 | 165 | 165 | 3 | 3 | 3
1123 | Offshore Wind farm connection Centre Manche 2 | TOOT | 94 | 95 | 93 | 180 | 25 | 27 | 24 | 344 | 356 | 330 | -173 | -160 | -184 | 79 | 33 | 83 | 89 | 15 | 38 | 41 | 4978 | 5007 | 4949 | 1250 | -90 | -10 | -44 | -2 | -3 | -4 | 661 | 34 | 167 | 167 | 167 | 3 | 3 | 3
1124 | Offshore Wind Connection South Britanny | TOOT | 18 | 19 | 17 | 155 | 17 | 18 | 16 | 210 | 220 | 202 | -113 | -106 | -120 | 63 | 22 | 55 | 58 | 12 | 30 | 32 | 2983 | 3089 | 2880 | 250 | -53 | -6 | -29 | -1 | -2 | -2 | 664 | 28 | 99 | 99 | 99 | 2 | 2 | 2
1125 | Offshore Wind Connection Occitanie | TOOT | 65 | 68 | 63 | 125 | 18 | 20 | 18 | 213 | 223 | 204 | -125 | -120 | -133 | 12 | 24 | 60 | 64 | 2 | 6 | 6 | 3024 | 3127 | 2912 | 250 | -68 | -9 | -30 | -1 | -2 | -3 | 80 | 4 | 99 | 99 | 99 | 2 | 2 | 2
1126 | Offshore Wind Connection PACA | TOOT | 61 | 70 | 54 | 120 | 18 | 19 | 17 | 203 | 213 | 196 | -121 | -116 | -127 | -17 | 23 | 58 | 62 | -3 | -8 | -9 | 2892 | 2986 | 2795 | 250 | -74 | -9 | -34 | -1 | -2 | -4 | -218 | -9 | 99 | 99 | 99 | 2 | 2 | 2
1127 | Offshore Wind Connection South Atlantic Oléron 1 | TOOT | 20 | 24 | 16 | 234 | 23 | 26 | 20 | 302 | 314 | 292 | -159 | -139 | -176 | 70 | 30 | 76 | 82 | 13 | 34 | 36 | 4300 | 4412 | 4172 | 1250 | -84 | -11 | -41 | -2 | -3 | -4 | 626 | 30 | 165 | 165 | 165 | 3 | 3 | 3
1134 | GiLA | PINT | 455 | 455 | 455 |  | 39 | 39 | 39 | 287 | 287 | 287 | -264 | -264 | -264 | 13 | 0 | 0 | 0 | 2 | 6 | 7 | 5647 | 5647 | 5647 |  | -115 | -36 | -5 | -1 | -1 | -13 | 752 | 31 | 0 | 0 | 0 | 0 | 0 | 0
1138 | 400 kV OHL Suceava (RO) - Balti (MD) | TOOT | 21 | 30 | 10 |  | -28 | -25 | -31 | 8 | 11 | 6 | 167 | 209 | 119 | 64 | 0 | 0 | 0 | 12 | 31 | 33 | 120 | 162 | 81 |  | -106 | -33 | -5 | -1 | -1 | -12 | 1632 | 90 | 252 | 252 | 252 | 2 | 2 | 2
1139 | 380-kV Westtirol (AT) – Zell/Ziller (AT) | PINT | 77 | 117 | 35 | 77 | 5 | 16 | -9 | 158 | 178 | 132 | -78 | -60 | -111 | -20 | 7 | 17 | 18 | -4 | -10 | -10 | 2249 | 2495 | 1886 | 1600 | -61 | -9 | -32 | -1 | -2 | -3 | -681 | -39 | 0 | 0 | 0 | 0 | 0 | 0
1140 | 380-kV St. Peter (AT) - Dürnrohr (AT) | PINT | 119 | 124 | 114 | 68 | 16 | 17 | 14 | 159 | 164 | 154 | -106 | -97 | -114 | -8 | 20 | 51 | 55 | -2 | -4 | -4 | 2256 | 2300 | 2212 | 1500 | -72 | -10 | -34 | -1 | -2 | -4 | -293 | -17 | 287 | 287 | 287 | 4 | 4 | 4
1145 | 380-kV Obersielach (AT) - Hessenberg (AT) | TOOT | 1 | 4 | 0 | 170 | 13 | 13 | 13 | 196 | 204 | 190 | -90 | -88 | -92 | -16 | 17 | 43 | 47 | -3 | -8 | -8 | 2794 | 2866 | 2726 | 2000 | -53 | -11 | -19 | -1 | -1 | -4 | -225 | -15 | 0 | 0 | 0 | 0 | 0 | 0
1153 | PST romands | TOOT | 19 | 23 | 13 |  | 33 | 35 | 27 | 33 | 39 | 27 | -221 | -185 | -240 | 93 | 42 | 106 | 114 | 18 | 45 | 48 | 466 | 560 | 383 |  | -155 | -50 | -3 | -1 | -1 | -17 | 711 | 38 | 382 | 382 | 382 | 9 | 9 | 9
1155 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT) | TOOT | 4 | 6 | 3 | 298 | 24 | 26 | 21 | 348 | 362 | 337 | -164 | -146 | -178 | 3 | 31 | 79 | 84 | 0 | 1 | 1 | 4942 | 5084 | 4814 | 2000 | -82 | -18 | -27 | -1 | -2 | -6 | -132 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1156 | 380-kV Greater Vienna (AT) - Hessenberg (AT) | TOOT | 5 | 10 | 0 | 233 | 18 | 19 | 16 | 265 | 265 | 265 | -121 | -108 | -129 | -8 | 23 | 58 | 62 | -2 | -4 | -4 | 3860 | 3985 | 3788 | 2500 | -66 | -14 | -23 | -1 | -2 | -5 | -213 | -12 | 0 | 0 | 0 | 0 | 0 | 0
1157 | HG North Tyrrhenian Corridor | TOOT | 349 | 357 | 344 |  | 87 | 92 | 84 | 127 | 138 | 112 | -592 | -571 | -623 | 98 | 114 | 285 | 305 | 19 | 47 | 51 | 1809 | 1945 | 1600 |  | -386 | -108 | -49 | -4 | -5 | -38 | 757 | 49 | 3833 | 3833 | 3833 | 41 | 41 | 41
1158 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT) | PINT | 2 | 3 | 1 | 163 | 13 | 15 | 10 | 191 | 197 | 186 | -87 | -70 | -105 | -1 | 17 | 42 | 45 | 0 | -1 | -1 | 2716 | 2769 | 2671 | 2000 | -48 | -10 | -18 | -1 | -1 | -4 | -191 | -10 | 0 | 0 | 0 | 0 | 0 | 0
1159 | 220-kV Bisamberg (AT) – Wien Südost (AT) | TOOT | 1 | 3 | 0 | 19 | 0 | 1 | -1 | 26 | 29 | 22 | 2 | 8 | -6 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 370 | 410 | 314 | 500 | 4 | 1 | 0 | 0 | 0 | 0 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0
1161 | Offshore Wind Connection South Atlantic Oléron 2 | TOOT | 10 | 13 | 7 | 210 | 20 | 22 | 19 | 270 | 283 | 259 | -138 | -130 | -148 | 106 | 26 | 66 | 71 | 20 | 51 | 55 | 3844 | 3970 | 3704 | 1200 | -78 | -9 | -37 | -2 | -2 | -4 | 901 | 46 | 157 | 157 | 157 | 3 | 3 | 3
1162 | Offshore Wind Connection Fécamp-Grand Large 1 | TOOT | 15 | 18 | 12 | 351 | 35 | 37 | 33 | 450 | 468 | 430 | -236 | -225 | -254 | 70 | 45 | 113 | 121 | 13 | 34 | 36 | 6399 | 6575 | 6147 | 2000 | -112 | -15 | -54 | -2 | -3 | -6 | 451 | 28 | 263 | 263 | 263 | 5 | 5 | 5
1163 | Offshore Wind Connection Fécamp-Grand Large 2 | TOOT | 125 | 128 | 122 | 241 | 35 | 37 | 33 | 450 | 468 | 430 | -236 | -225 | -254 | 70 | 45 | 113 | 121 | 13 | 34 | 36 | 6399 | 6575 | 6147 | 2000 | -112 | -15 | -54 | -2 | -3 | -6 | 451 | 28 | 262 | 262 | 262 | 4 | 4 | 4
1164 | Offshore Wind Connection Golfe de Lion Centre | TOOT | 125 | 128 | 122 | 241 | 35 | 37 | 33 | 450 | 468 | 430 | -236 | -225 | -254 | -62 | 45 | 113 | 121 | -12 | -30 | -32 | 6399 | 6575 | 6147 | 2000 | -112 | -15 | -54 | -2 | -3 | -6 | -634 | -29 | 265 | 265 | 265 | 4 | 4 | 4
1165 | Offshore Wind Connection Golfe de Gascogne Sud | TOOT | 75 | 78 | 72 | 145 | 20 | 22 | 19 | 270 | 283 | 259 | -138 | -130 | -148 | 56 | 26 | 66 | 71 | 11 | 27 | 29 | 3844 | 3970 | 3704 | 1200 | -78 | -9 | -37 | -2 | -2 | -4 | 468 | 25 | 158 | 158 | 158 | 3 | 3 | 3
1166 | HG Adriatic Corridor | PINT | 158 | 166 | 151 |  | 37 | 39 | 35 | 64 | 66 | 62 | -252 | -235 | -266 | 38 | 48 | 121 | 130 | 7 | 18 | 20 | 912 | 929 | 882 |  | -143 | -39 | -21 | -2 | -2 | -14 | 373 | 29 | 119 | 119 | 119 | 1 | 1 | 1
1167 | HG Central link | TOOT | 24 | 47 | 1 |  | 2 | 7 | -3 | 4 | 5 | 3 | -16 | 22 | -48 | 20 | 3 | 7 | 8 | 4 | 10 | 10 | 59 | 66 | 46 |  | -19 | -6 | 0 | 0 | 0 | -2 | 319 | 16 | 715 | 715 | 715 | 5 | 5 | 5
1168 | HG Ionian-Tyrrhenian Corridor | TOOT | 37 | 53 | 29 |  | 7 | 10 | 1 | 12 | 18 | 4 | -51 | -9 | -71 | 8 | 10 | 24 | 26 | 2 | 4 | 4 | 164 | 206 | 52 |  | -31 | -8 | -5 | 0 | 0 | -3 | 188 | 7 | 0 | 0 | 0 | 0 | 0 | 0
1169 | SAPEI 2 | PINT | 14 | 17 | 10 |  | 6 | 11 | -3 | 8 | 10 | 5 | -50 | -20 | -74 | -6 | 8 | 19 | 20 | -1 | -3 | -3 | 111 | 128 | 75 |  | -16 | -6 | 2 | 0 | 0 | -2 | 21 | 3 | 14 | 14 | 14 | 0 | 0 | 0
1171 | Interconnection IT-CH | PINT | 66 | 91 | 50 |  | 33 | 38 | 25 | 14 | 15 | 12 | -225 | -167 | -261 | 12 | 43 | 108 | 116 | 2 | 6 | 6 | 191 | 214 | 165 |  | -81 | -24 | -12 | -1 | -1 | -8 | 267 | 16 | 85 | 85 | 85 | 1 | 1 | 1
1182 | EHV S/S Thesprotias and its connection to the 400 kV System | Light PINT | 5 | 9 | 1 |  | 6 | 9 | 4 | 11 | 16 | 8 | -41 | -29 | -62 |  | 8 | 20 | 21 |  |  |  | 162 | 232 | 115 |  | -7 | -2 | -2 | 0 | 0 | -1 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1183 | New interconnection line 400 kV Greece - Albania | Light PINT | 3 | 3 | 2 |  | 2 | 5 | -2 | -4 | 3 | -14 | -10 | 15 | -34 |  | 2 | 5 | 5 |  |  |  | -59 | 50 | -202 |  | 4 | 1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1185 | South Coast Offshore Transmission Project | TOOT | 0 | 0 | 0 | 117 | 8 | 10 | 7 | 135 | 142 | 129 | -56 | -48 | -65 | 0 | 11 | 27 | 29 | 0 | 0 | 0 | 1917 | 1982 | 1848 | 800 | -28 | -6 | -9 | 0 | -1 | -2 | 17 | 1 | 177 | 177 | 177 | 2 | 2 | 2
1192 | HansaLink - Phase 1 | PINT | 251 | 253 | 250 |  | 65 | 68 | 63 | 22 | 24 | 21 | -445 | -427 | -463 | -41 | 85 | 214 | 229 | -8 | -20 | -21 | 312 | 327 | 297 | 2000 | -267 | -45 | -113 | -5 | -7 | -16 | -207 | -19 | 3869 | 3869 | 3869 | 47 | 47 | 47
1193 | HansaLink - Phase 2 | PINT | 51 | 53 | 47 |  | 20 | 23 | 17 | -46 | -46 | -47 | -137 | -116 | -158 | 2 | 26 | 66 | 70 | 0 | 1 | 1 | -658 | -652 | -664 | 2000 | -49 | -8 | -22 | -1 | -2 | -3 | -231 | -9 | 23 | 23 | 23 | 57 | 57 | 57
1197 | NU-Link Interconnector | PINT | 116 | 119 | 113 |  | 22 | 23 | 21 | 34 | 40 | 30 | -151 | -145 | -156 | -13 | 29 | 73 | 78 | -3 | -6 | -7 | 488 | 573 | 416 |  | -108 | -16 | -44 | -2 | -3 | -6 | -71 | -4 | 198 | 198 | 198 | 9 | 9 | 9
1200 | Hybrid interconnector Norway-Sørvest F Windfarm-Continent (DK, DE or BE) | PINT | 162 | 164 | 159 |  | 61 | 67 | 54 | 44 | 49 | 35 | -415 | -365 | -456 | 12 | 80 | 199 | 213 | 2 | 6 | 6 | 628 | 716 | 503 |  | -175 | -44 | -23 | -2 | -2 | -16 | 270 | 15 | 3108 | 3108 | 3108 | 38 | 38 | 38
1201 | Reinvestment of Skagerrak 1 and 2 | PINT | 99 | 100 | 99 |  | 17 | 20 | 14 | 34 | 36 | 32 | -119 | -94 | -136 | 1 | 23 | 57 | 61 | 0 | 0 | 0 | 481 | 502 | 457 |  | -92 | -7 | -67 | -3 | -4 | -3 | 19 | 1 | 296 | 296 | 296 | 11 | 11 | 11
1202 | Increased capacity Norway-Finland, Back-to-Back | PINT | 14 | 23 | 7 |  | 5 | 7 | 3 | 16 | 18 | 15 | -32 | -22 | -50 | 1 | 6 | 15 | 17 | 0 | 0 | 1 | 234 | 251 | 204 |  | -42 | -2 | -30 | -1 | -2 | -1 | 86 | 5 | 72 | 72 | 72 | 1 | 1 | 1
1203 | Offshore Wind Connection Bretagne Nord-Ouest | PINT | 4 | 7 | 1 | 236 | 23 | 25 | 22 | 291 | 301 | 278 | -156 | -147 | -170 | 99 | 30 | 75 | 80 | 19 | 47 | 51 | 4212 | 4218 | 4206 | 1200 | -48 | -8 | -23 | -1 | -2 | -3 | 906 | 45 | 157 | 157 | 157 | 2 | 2 | 2
1207 | 380kV Niederstedem-Bertrange/Bofferdange | PINT | 1 | 2 | 0 |  | 1 | 2 | 0 | 0 | 3 | -2 | -5 | 0 | -14 | -5 | 1 | 3 | 3 | -1 | -2 | -2 | -3 | 36 | -28 |  | -2 | 0 | -5 | 0 | 0 | 0 | 203 | 19 | 0 | 0 | 0 | 0 | 0 | 0
1208 | Medlink | PINT | 292 | 294 | 291 |  | 230 | 234 | 227 | -156 | -149 | -163 | -1562 | -1541 | -1593 | 12 | 300 | 751 | 804 | 2 | 6 | 6 | -2213 | -2090 | -2326 | 9016 | -732 | -202 | -101 | -8 | -10 | -71 | 538 | 45 | 0 | 0 | 0 | 0 | 0 | 0
1209 | Latvia and Lithuania cross-border strengthening project | PINT | 28 | 36 | 19 |  | 4 | 6 | 2 | 30 | 31 | 29 | -27 | -15 | -41 | 0 | 5 | 13 | 14 | 0 | 0 | 0 | 432 | 450 | 405 |  | -163 | -2 | -108 | -4 | -6 | -2 | -70 | -2 | 3 | 3 | 3 | 0 | 0 | 0
1210 | APOLLO-LINK | Light PINT | 386 | 386 | 386 |  | 125 | 130 | 118 | 199 | 212 | 186 | -852 | -803 | -883 |  | 164 | 410 | 439 |  |  |  | 2823 | 3038 | 2653 |  | -520 | -169 | -11 | -4 | -4 | -59 |  |  | 456 | 456 | 456 | 4 | 4 | 4
1211 | Baltic WindConnector (BWC) | PINT | 548 | 548 | 547 | 248 | 43 | 44 | 42 | 523 | 523 | 523 | -292 | -285 | -300 | 17 | 56 | 141 | 150 | 3 | 8 | 9 | 7428 | 7513 | 7343 | 2000 | -181 | -31 | -77 | -3 | -5 | -11 | 352 | 21 | 2808 | 2808 | 2808 | 34 | 34 | 34
1213 | Offshore hybrid Interconnector (DE-NL) | Light PINT | 161 | 167 | 155 |  | 11 | 13 | 10 | 75 | 79 | 69 | -73 | -65 | -89 |  | 14 | 35 | 38 |  |  |  | 1061 | 1122 | 996 |  | -46 | -6 | -28 | -1 | -2 | -2 |  |  | 1368 | 1368 | 1368 | 17 | 17 | 17
1214 | Hybrid Interconnector Denmark-Germany | TOOT | 743 | 752 | 730 | 51 | 56 | 60 | 53 | 637 | 648 | 627 | -427 | -359 | -514 | 112 | 74 | 184 | 197 | 22 | 54 | 58 | 9075 | 9184 | 8957 | 2000 | -223 | -37 | -95 | -4 | -6 | -14 | 2380 | 141 | 0 | 0 | 0 | 0 | 0 | 0
1215 | Xlinks Morocco - Germany | PINT | 1023 | 1050 | 990 |  | 168 | 190 | 149 | -102 | -100 | -105 | -1145 | -1016 | -1292 | 284 | 220 | 551 | 590 | 54 | 136 | 146 | -1448 | -1428 | -1469 | 15200 | -627 | -95 | -297 | -13 | -19 | -35 | 4049 | 273 | 0 | 0 | 0 | 0 | 0 | 0
1216 | High-Voltage Direct Current Interconnector Project Romania-Hungary | PINT | 79 | 84 | 69 |  | 3 | 6 | 0 | 2 | 2 | 2 | -23 | 3 | -39 | 50 | 4 | 11 | 12 | 10 | 24 | 26 | 32 | 33 | 30 |  | -16 | 6 | -42 | -1 | -2 | 2 | 119 | 12 | 110 | 110 | 110 | 1 | 1 | 1
1217 | Further Development of Offshore Renewables (MOG 3) | Light PINT | 36 | 44 | 26 | 409 | 32 | 37 | 29 | 476 | 489 | 462 | -216 | -199 | -249 |  | 41 | 104 | 111 |  |  |  | 6863 | 6869 | 6857 |  | -184 | -19 | -112 | -4 | -7 | -7 |  |  | 323 | 323 | 323 | 19 | 19 | 19
1218 | Hybrid HVDC Interconnector BE-NL | Light PINT | 111 | 117 | 107 |  | 8 | 11 | 5 | 85 | 86 | 85 | -54 | -31 | -78 |  | 10 | 26 | 28 |  |  |  | 1209 | 1225 | 1194 |  | -83 | -9 | -61 | -2 | -4 | -3 |  |  | 1 | 1 | 1 | 7 | 7 | 7
1219 | Bofferdange- Bertrange | Light PINT | 22 | 27 | 14 |  | 3 | 3 | 2 | 11 | 15 | 8 | -18 | -12 | -23 |  | 3 | 9 | 9 |  |  |  | 155 | 216 | 120 |  | -1 | -1 | -1 | 0 | 0 | 0 |  |  | 467 | 467 | 467 | 6 | 6 | 6
1220 | Offshore Wind Connection Viana do Castelo | TOOT | 27 | 34 | 23 | 161 | 29 | 30 | 27 | 204 | 218 | 191 | -196 | -185 | -203 | 1 | 38 | 94 | 101 | 0 | 1 | 1 | 2907 | 3061 | 2736 | 2000 | -60 | -5 | -32 | -1 | -2 | -2 | 140 | 14 | 183 | 183 | 183 | 1 | 1 | 1
1221 | Offshore Wind Connection Leixões | TOOT | 16 | 23 | 10 | 116 | 20 | 21 | 18 | 150 | 160 | 139 | -138 | -124 | -145 | 6 | 26 | 66 | 71 | 1 | 3 | 3 | 2131 | 2243 | 1997 | 1500 | -38 | -4 | -20 | -1 | -1 | -2 | 134 | 12 | 136 | 136 | 136 | 1 | 1 | 1
1222 | Offshore Wind Connection Figueira da Foz (North) | TOOT | 29 | 36 | 25 | 159 | 29 | 30 | 27 | 204 | 218 | 191 | -196 | -185 | -203 | 4 | 38 | 94 | 101 | 1 | 2 | 2 | 2907 | 3061 | 2736 | 2000 | -60 | -5 | -32 | -1 | -2 | -2 | 121 | 13 | 183 | 183 | 183 | 1 | 1 | 1
1223 | Offshore Wind Connection Figueira da Foz (South) | TOOT | 29 | 36 | 25 | 159 | 29 | 30 | 27 | 204 | 218 | 191 | -196 | -185 | -203 | 4 | 38 | 94 | 101 | 1 | 2 | 2 | 2907 | 3061 | 2736 | 2000 | -60 | -5 | -32 | -1 | -2 | -2 | 133 | 13 | 183 | 183 | 183 | 1 | 1 | 1
1224 | Offshore Wind Connection Ericeira | TOOT | 11 | 14 | 6 | 77 | 12 | 14 | 11 | 97 | 104 | 90 | -84 | -72 | -94 | 4 | 16 | 40 | 43 | 1 | 2 | 2 | 1377 | 1461 | 1288 | 1000 | -31 | -3 | -15 | -1 | -1 | -1 | 15 | 3 | 91 | 91 | 91 | 1 | 1 | 1
1225 | Offshore Wind Connection Sines | TOOT | 13 | 20 | 7 | 119 | 20 | 21 | 18 | 150 | 160 | 139 | -138 | -124 | -145 | 3 | 26 | 66 | 71 | 1 | 1 | 2 | 2131 | 2243 | 1997 | 1500 | -38 | -4 | -20 | -1 | -1 | -2 | -64 | 0 | 136 | 136 | 136 | 1 | 1 | 1
1226 | North-South Electricity Corridor in Eastern Europe | Light PINT | 607 | 624 | 590 |  | 171 | 171 | 171 | 150 | 151 | 150 | -1160 | -1160 | -1160 |  | 223 | 558 | 597 |  |  |  | 2143 | 2154 | 2132 |  | -902 | -255 | -155 | -11 | -13 | -90 |  |  | 667 | 667 | 667 | 8 | 8 | 8
1229 | Rhine-Main-Link | PINT | 1887 | 2170 | 1705 |  | 46 | 56 | 40 | 683 | 813 | 602 | -315 | -271 | -382 | 51 | 61 | 152 | 162 | 10 | 24 | 26 | 7 | 8 | 6 |  | -238 | -75 | -7 | -2 | -2 | -26 | 1451 | 69 | 0 | 0 | 0 | 0 | 0 | 20
1230 | TuNur Malta | PINT | 21 | 23 | 19 |  | 64 | 65 | 63 | 1 | 4 | -3 | -439 | -430 | -444 | -2 | 84 | 211 | 226 | 0 | -1 | -1 | 12 | 64 | -37 | 1400 | -67 | -21 | -3 | -1 | -1 | -7 | -96 | -4 | 0 | 0 | 0 | 0 | 0 | 0
1231 | Green Aegean Interconnector | Light PINT | 1114 | 1154 | 1084 |  | 208 | 210 | 207 | 350 | 356 | 347 | -1418 | -1405 | -1431 |  | 272 | 682 | 730 |  |  |  | 4986 | 5083 | 4887 |  | -224 | -80 | 9 | -1 | 0 | -28 |  |  | 1687 | 1687 | 1687 | 21 | 21 | 21
1233 | Laufenburg - Beznau - Breite | Light PINT | 33 | 44 | 24 |  | 32 | 37 | 23 | 136 | 142 | 132 | -217 | -154 | -251 |  | 42 | 105 | 112 |  |  |  | 1941 | 2033 | 1858 |  | -126 | -43 | 0 | -1 | -1 | -15 |  |  | 0 | 0 | 0 | 0 | 0 | 0
1234 | 220-kV Reitdorf (AT) - Weißenbach (AT) | TOOT | 4 | 6 | 1 | 37 | 2 | 3 | 2 | 45 | 50 | 40 | -14 | -11 | -18 | 1 | 3 | 7 | 7 | 0 | 1 | 1 | 636 | 710 | 577 | 500 | -16 | -2 | -8 | 0 | -1 | -1 | -59 | -1 | 0 | 0 | 0 | 0 | 0 | 0
1235 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK) | PINT | 15 | 18 | 13 |  | 5 | 7 | 4 | 1 | 3 | -2 | -37 | -27 | -45 | -50 | 7 | 18 | 19 | -10 | -24 | -26 | 11 | 46 | -23 |  | 7 | -4 | 37 | 1 | 1 | -1 | -438 | -29 | 32 | 32 | 32 | 0 | 0 | 0
1236 | Power-to-Gas for Austria (P2G4A) | PINT | 1 | 3 | 0 |  | 0 | 1 | -1 | 0 | 11 | -10 | -1 | 6 | -9 | 3 | 0 | 1 | 1 | 1 | 1 | 2 | 6 | 154 | -140 |  | -1 | 0 | -2 | 0 | 0 | 0 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0
1239 | Interconnection Ukraine-Slovak Republic | Light PINT | 9 | 11 | 7 |  | -19 | -15 | -23 | 4 | 10 | 0 | 127 | 157 | 105 |  | 0 | 0 | 0 |  |  |  | 64 | 141 | -6 |  | -59 | -19 | -15 | -1 | -1 | -6
1240 | Interconnection Ukraine-Romania | Light PINT | 0 | 0 | 0 |  | -35 | -29 | -40 | 12 | 13 | 11 | 236 | 274 | 197 |  | 0 | 0 | 0 |  |  |  | 171 | 182 | 159 |  | -109 | -36 | -16 | -1 | 0 | -13

## Trans.ProjectLevelBenefits
Project ID | Project name | B7.1 Balancing Energy Exchange | [5 empty] | B8.1 Frequency stability | [5 empty] | B9 Reduction of necessary reserve for re-dispatch power plants
|  | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040 | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040 | NT2030 |  | NT2040 |  | DE2030 |  | DE2040 |  | 2030 | 2040
|  | Qualitative assessment by ENTSO-E | [5 empty] | MWh/year | [5 empty] | M€ / year |  | M€ / year |  | M€ / year |  | M€ / year |  | M€ / year | M€ / year
1 | RES in north of Portugal
4 | Interconnection Portugal-Spain
16 | Biscay Gulf
28 | Italy-Montenegro
29 | Italy-Tunisia
33 | Central Northern Italy
35 | CZ Southwest-east corridor
40 | Belgium-Luxembourg-Germany: long-term perspective
47 | Westtirol (AT) - Vöhringen (DE)
81 | North South Interconnector
85 | Integration of RES in Alentejo
94 | GerPol Improvements
107 | Celtic Interconnector
111 | Aurora line (3rd AC Finland-Sweden north)
120 | Princess Elisabeth Island (MOG 2)
121 | Nautilus: multi-purpose interconnector Belgium - UK
124 | Ekhyddan-Nybro-Hemsjö
126 | SE North-south short-term reinforcements
127 | Central Southern Italy
130 | HVDC SuedOstLink Wolmirstedt to area Isar | [12 empty] | 12.88874 | 649.07 MW/year | 36.9 | 1848.34 MW/year |  | MW/year | 12.9428 | 647.87 MW/year
132 | HVDC Line A-North | [12 empty] | 37.18742 | 1859.67 MW/year | 58.5 | 2926.12 MW/year |  | MW/year | 1.31948 | 66.04 MW/year
138 | Black Sea Corridor
144 | Mid Continental East corridor
150 | Italy-Slovenia
153 | France-Alderney-Britain
170 | Baltic States Synchronization with Continental Europe
174 | Greenconnector
176 | Hansa PowerBridge I
187 | St. Peter (AT) - Pleinting (DE) | + | + |  | +
200 | CZ Northwest-South corridor
210 | Würmlach (AT) - Somplago (IT) interconnection
219 | Great Sea Interconnector
225 | 2nd interconnector Belgium - Germany
227 | Transbalkan Corridor
228 | Muhlbach - Eichstetten
231 | Beznau - Tiengen
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | [12 empty] | 76.33838 | 3819.55 MW/year | 80.3 | 4014.1 MW/year |  | MW/year | 14.23298 | 713.68 MW/year
239 | Fenno-Skan 3
243 | New 400 kV interconnection line between Serbia and Croatia
244 | Vigy - Uchtelfangen area
247 | AQUIND Interconnector
250 | Merchant line Castasegna (CH) - Mese (IT)
254 | HVDC Ultranet Osterath to Philippsburg | [12 empty] | 17.3454 | 870.6 MW/year | 29.6 | 1480.31 MW/year |  | MW/year | 29.23726 | 1461.36 MW/year
259 | HU-RO
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands
267 | Hansa PowerBridge II
270 | FR-ES project -Aragón-Atlantic Pyrenees
276 | FR-ES project -Navarra-Landes
280 | FR-BE: Lonny-Achene-Gramme
283 | TuNur Italy
285 | GridLink
297 | BRABO III
299 | SACOI 3
309 | NeuConnect
312 | St. Peter (AT) - Tauern (AT) | + | + |  | +
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | + | + |  | +
323 | Dekani (SI) - Zaule (IT) interconnection
324 | Redipuglia (IT) - Vrtojba (SI) interconnection
325 | Obersielach (AT) - Podlog (SI)
328 | Interconnector DE-LUX
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor
330 | 4th 400kV CZ-SK interconnector
335 | North Sea Wind Power Hub
338 | Adriatic HVDC link
339 | Tyrrhenian link
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor
341 | North CSE Corridor
342 | Central Balkan Corridor
343 | CSE1 New
346 | ZuidWest380 NL Oost
349 | MaresConnect
350 | South Balkan Corridor
375 | Lienz (AT) - Veneto region (IT) 220 kV
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht
378 | Transformer Gatica
379 | Uprate Gatica lines
1034 | HVDC corridor from Northern Germany to Western Germany | [12 empty] | 0.50436 | 29.55 MW/year | 52.5 | 2625.78 MW/year |  | MW/year | -31.46476 | -1571.84 MW/year
1039 | SE North-south long-term reinforcements
1040 | LirIC
1041 | GREGY Green Energy Interconnector | [13 empty] | Please see attached document "Unit for quantified value and Explanation of the monetisation factor". |  | Please see attached document "Unit for quantified value and Explanation of the monetisation factor". |  | Please see attached document "Unit for quantified value and Explanation of the monetisation factor". |  | Please see attached document "Unit for quantified value and Explanation of the monetisation factor".
1046 | Finnish North-South reinforcement
1048 | Greece - Africa Power Interconnector (GAP Interconnector)
1049 | Cronos Energy Ltd
1050 | Tarchon Energy Ltd
1052 | Lienz (AT) - Malta (AT) - Obersielach (AT) | + | + |  | +
1054 | 220-kV Westtirol (AT) - Zell/Ziller (AT)
1055 | Interconnection of Crete to the Mainland System of Greece
1058 | HVDC Interconnector DE-CH
1059 | Southern Italy
1066 | Bulgaria - Turkey
1067 | New AC 400 kV interconnection line Greece - Turkey
1068 | LaSGo Link
1074 | Pannonian Corridor
1085 | Malta-Italy Cable Link No.2
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project)
1088 | Latvia and Estonia Hybrid Off-Shore interconnector
1092 | TritonLink: offshore hybrid HVDC interconnector Belgium – Denmark
1094 | Estlink 3
1095 | Aurora line 2 (4th AC Finland-Sweden north)
1096 | Beznau - Mettlen
1097 | Upgrade to Konti-Skan
1098 | Offshore Wind LT 2
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side
1102 | Mettlen - Ulrichen
1103 | Bickigen - Chippis
1104 | Bauler - Roost
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project
1106 | Bornholm Energy Island (BEI)
1109 | Basilicata - Campania reinforcements
1110 | Sicily - Calabria
1112 | GRITA 2
1121 | 220-kV Hessenberg (AT) - Weißenbach (AT)
1122 | Offshore Wind farm connection Centre Manche 1
1123 | Offshore Wind farm connection Centre Manche 2
1124 | Offshore Wind Connection South Britanny
1125 | Offshore Wind Connection Occitanie
1126 | Offshore Wind Connection PACA
1127 | Offshore Wind Connection South Atlantic Oléron 1
1134 | GiLA
1138 | 400 kV OHL Suceava (RO) - Balti (MD)
1139 | 380-kV Westtirol (AT) – Zell/Ziller (AT)
1140 | 380-kV St. Peter (AT) - Dürnrohr (AT) | +
1145 | 380-kV Obersielach (AT) - Hessenberg (AT)
1153 | PST romands
1155 | 380-kV Burgenland North (AT) - Sarasdorf (AT) - Greater Vienna (AT)
1156 | 380-kV Greater Vienna (AT) - Hessenberg (AT)
1157 | HG North Tyrrhenian Corridor
1158 | 380-kV Bisamberg (AT) – Gaweinstal (AT) – Zaya (AT)
1159 | 220-kV Bisamberg (AT) – Wien Südost (AT)
1161 | Offshore Wind Connection South Atlantic Oléron 2
1162 | Offshore Wind Connection Fécamp-Grand Large 1
1163 | Offshore Wind Connection Fécamp-Grand Large 2
1164 | Offshore Wind Connection Golfe de Lion Centre
1165 | Offshore Wind Connection Golfe de Gascogne Sud
1166 | HG Adriatic Corridor
1167 | HG Central link
1168 | HG Ionian-Tyrrhenian Corridor
1169 | SAPEI 2
1171 | Interconnection IT-CH
1182 | EHV S/S Thesprotias and its connection to the 400 kV System
1183 | New interconnection line 400 kV Greece - Albania
1185 | South Coast Offshore Transmission Project
1192 | HansaLink - Phase 1
1193 | HansaLink - Phase 2
1197 | NU-Link Interconnector
1200 | Hybrid interconnector Norway-Sørvest F Windfarm-Continent (DK, DE or BE)
1201 | Reinvestment of Skagerrak 1 and 2
1202 | Increased capacity Norway-Finland, Back-to-Back
1203 | Offshore Wind Connection Bretagne Nord-Ouest
1207 | 380kV Niederstedem-Bertrange/Bofferdange
1208 | Medlink
1209 | Latvia and Lithuania cross-border strengthening project
1210 | APOLLO-LINK | ++
1211 | Baltic WindConnector (BWC)
1213 | Offshore hybrid Interconnector (DE-NL)
1214 | Hybrid Interconnector Denmark-Germany
1215 | Xlinks Morocco - Germany
1216 | High-Voltage Direct Current Interconnector Project Romania-Hungary
1217 | Further Development of Offshore Renewables (MOG 3)
1218 | Hybrid HVDC Interconnector BE-NL
1219 | Bofferdange- Bertrange
1220 | Offshore Wind Connection Viana do Castelo
1221 | Offshore Wind Connection Leixões
1222 | Offshore Wind Connection Figueira da Foz (North)
1223 | Offshore Wind Connection Figueira da Foz (South)
1224 | Offshore Wind Connection Ericeira
1225 | Offshore Wind Connection Sines
1226 | North-South Electricity Corridor in Eastern Europe
1229 | Rhine-Main-Link | [12 empty] | 3.53702 | 173.42 MW/year | 33.4 | 1676.7 MW/year |  | MW/year | 28.03302 | 1402.08 MW/year
1230 | TuNur Malta
1231 | Green Aegean Interconnector
1233 | Laufenburg - Beznau - Breite
1234 | 220-kV Reitdorf (AT) - Weißenbach (AT)
1235 | Second circuit of the 400 kV OHL Sajóivánka (HU) – Rimavská Sobota (SK)
1236 | Power-to-Gas for Austria (P2G4A)
1239 | Interconnection Ukraine-Slovak Republic
1240 | Interconnection Ukraine-Romania

## Stor.ProjectLevelBenefits
Project ID | Project name | B7.1 Balancing Energy Exchange | [5 empty] | B9 Reduction of necessary reserve for re-dispatch power plants
|  | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040 | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040
|  | Qualitative assessment by ENTSO-E | [5 empty] | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year