**01/November/2021**

**To Whom it may concern:**

**Protection of Tilt Skillet:**

When intending to protect a Tilt Skillet, it must be addressed like a Fryer.

Fryers is protected with nozzle 93429 and the coverage area of this nozzle is 18" x 28".

When it comes to calculating the number of nozzles needed to cover Tilt Skillet, must take the size of the Tilt Skillet (width and length) and divide it by the coverage area of one Fryer nozzle (93429) 18" x 28".

The number of nozzles that will be obtained after this calculation, should always be rounded up.

The height of nozzles installation above the Tilt Skillet will be 31.5" – 47", and the nozzles can be installed anywhere within the protected perimeter of the Tilt skillet and aiming to the center of zone of protection of each nozzle.

**Elan Alchalel**

**System Designing & Integration Manager**

Mobile. +972-52-373 6110|   Email: elan-a@lehavot.com

Tel. +972-4-6952197  | Fax. +972-4-6952119

Lehavot Habashan ISRAEL 1212500