Drinking Water Quality and Compliance

Town Short Form – A Template for Annual Notice to Consumers

(Note:  This short form may be used for communities or waterworks serving a population of less than 5000).

2022 REPORT-RM 241

Introduction

The Water Security Agency and the Ministry of Environment requires that at least once each year waterworks owners provide notification to consumers of the quality of water produced and supplied as well as information on the performance of the waterworks in submitting samples as required by a Minister’s Order or Permit to operate a waterworks.  The following is a summary of the WROXTON water quality and sample submission compliance record for the 2022 time period.  This report was completed on March 21st, 2023 Readers should refer to Water Security Agency’s Municipal Drinking Water Quality Monitoring Guidelines, June 2015, EPB 502 for more information on minimum sample submission requirements and the meaning of type of sample.  Permit requirements for a specific waterworks may require more sampling than outlined in the department’s monitoring guidelines.  If consumers need more information on the nature and significance of specific water tests, for example, “what is the significance of Selenium in a water supply”, more detailed information is available from:  http://www.hc-sc.gc.ca/ewh-semt/pubs/water-eau/index_e.html .

## Water Quality Standards

# Bacteriological Quality

Regular Samples	Regular Samples	  # of Positive Regular

Parameter/Location	Limit			Required		Submitted	  Submitted (%)

Total Coliform 		0 Organisms/100 mL	__12_________	__12_________     _ ___0___________

E. coli			0 Organisms/100 mL	__12__________	__12_________      _    _0_______________

Background Bacteria	Less than 200/100 mL	______________	_______________  __________________

Water Disinfection –

Chlorine Residual in Distribution System for Test Results Submitted with Bacteriological Samples

Minimum	Total Chlorine	Free Chlorine	# Tests	# Tests	# Adequate

Parameter	Limit	Residual Range	Residual Range	Required	Submitted	Chlorine (%)

Chlorine	0.1 mg/L free OR	  0.75 – 1.86	  0.28 -1.58	12	12		100%

Residual	0.5 mg/L total	_____________	_____________	________	_________	_____________

Water Disinfection - Free Chlorine Residual for Water Entering Distribution System from Waterworks Records-From Water Treatment Plant Records

Test Level	# Tests                # Tests Not Meeting

Parameter	Limit (mg/L)	Range	Performed          Requirements

Free Chlorine Residual	at least 0.1	_0.19 – 1.88	_365_____                    0

A minimum of 0.1 milligrams per litre (mg/L) free chlorine residual is required for water entering the distribution system.  Tests are normally performed on a daily basis by the waterworks operator and are to be recorded in operation records.  This data includes the number of free chlorine residual tests performed, the overall range of free chlorine residual (highest and lowest recorded values) and the number of tests and percentage of results not meeting the minimum requirement of 0.1 mg/L free chlorine residual.

Turbidity – From Water Treatment Plant Records

Parameter	Limit	Test Level	# Tests Not Meeting	Maximum	# Tests           # Tests		# Tests

(NTU) 	Range	Requirements	Turbidity (NTU)	Required        Performed	Performed

Turbidity	_1.0___	_0.13 – 0.99	   __0     	0.99_	__365___       _365______	____________

Chemical – Health Category

All waterworks serving less than 5000 persons are required to submit water samples for SE’s Chemical Health category once every 2 years.  The Chemical Health category includes analysis for arsenic, barium, boron, cadmium, chromium, fluoride, lead, nitrate, selenium and uranium.

The last sample for Chemical Health analysis was submitted on April 4, 2022.  Sample results indicated that the provincial drinking water quality standards were not exceeded.  (Use this one if review indicates that there were no exceedences).  (OR)  Samples exceeded provincial water quality standards for the following parameters:  (Use only the applicable portions of table below for which values have been exceeded).

| Parameter | Limit MAC Sask . Guideline | Limit IMAC (mg/L) | Sample Result(s) |  | # Samples Exceeding Limit | *Results expressed as average values for communities or waterworks that fluoridate drinking water supplies or those with elevated concentrations of fluoride or nitrates. |
| --- | --- | --- | --- | --- | --- | --- |
| Arsenic Aluminum | 10 No Guideline |  | 0.60 <6.96 | Ug/L Ug/L | 0 0 |  |
| Antimony Barium | No Guideline 1000 |  | <0.16 12.7 | Ug/L Ug/L | 0 0 |  |
| Boron | 5.0 |  | 0.2 | Mg/L | 0 |  |
| Cadmium | 5 |  | <0.15 | Ug/L | 0 |  |
| Chromium | 50 |  | <0.19 | Ug/L | 0 |  |
| Copper | 1000 |  | 31.4 | Ug/L | 0 |  |
| Lead | 10 |  | 0.20 | Ug/L | 0 |  |
| Selenium Silver | 10 No Guideline |  | <1.13 <.20 | Ug/L Ug/L | 0 0 |  |
| Uranium Zinc | 20 5000 |  | 1.4 8.5 | Ug/L Ug/L | 0 0 |  |

Chemical – Trihalomethanes (THMs)and Haloacetic Acids (HAAs)

| Parameter | THMs Limit (mg/L) | Sample Result (average) | # Samples Required | # Samples Submitted |
| --- | --- | --- | --- | --- |
| Trihalomethanes | 0.10 |  | 4 (1 every 3 months) | 0 |
| Haloacetic Acids | 0.08 |  | 4 (1 every 3 months) | 0 |

Note:  Only water supplies derived from surface water or groundwater under the influence of surface water are required to monitor for THMs and HAAs.  Waterworks using groundwater sources beyond the influence of surface water do not need to report THMs or HAAs since sampling/analysis will not likely have been performed unless otherwise noted in the waterworks permit to operate

# General Chemical

| Parameter | Saskatchewan Guidelines *(mg/L) | Sample Results (Average) |  | # Samples Required | # Samples Submitted |
| --- | --- | --- | --- | --- | --- |
| Alkalinity | <500 | 484 | Mg/L | 0 | 1 |
| Bicarbonate | No Objective | 590 | Mg/L | 0 | 1 |
| Calcium | No Objective | 162 | Mg/L | 0 | 1 |
| Carbonate | No Objective | 0 | Mg/L | 0 | 1 |
| Chloride Dissolved | <250 | 31.6 | Mg/L | 0 | 1 |
| Conductivity | <2300 | 1312 | US/cm | 0 | 1 |
| Fluoride Dissolved Nitrate Dissolved Hardness Iron Manganese Magnesium Potassium | <1.5 <45 <800 <0.3 <0.05 200 No Guideline | 0.26 0.2 639 0.1 0.01 57 10.0 | Mg/L Mg/L Mg/L Mg/L Mg/L Mg/L Mg/L | 0 0 0 0 0 | 1 1 1 1 1 |
| PH | 7.0-10.5 | 7.5 | PH units | 0 | 1 |
| Sodium | <300 | 68 | Mg/L | 0 | 1 |
| Sulphate Dissolved | <500 | 232.0 | Mg/L | 0 | 1 |
| Total Dissolved Solids | <1500 | 1151 | Mg/L | 0 | 1 |

All waterworks serving less than 5000 persons are required to submit water samples for SE’s General Chemical category once every two years if a ground water source and once per three months every second year if a surface water or blended surface/groundwater source.  The General Chemical category includes analysis for alkalinity, bicarbonate, calcium, carbonate, chloride, conductivity, hardness (as CaCO3), magnesium, sodium, sulphate and total dissolved solids.

The last sample for General Chemical analysis was required in 2022 and submitted on  April 4, 2022 ;

More information on water quality and sample submission performance may be obtained from:

Rural Municipality of Calder No. 241

PO Box 10, Wroxton, Sask. S0A 4S0

Telephone Number 306-742-4233 / Facsimile Number 306-742-4559

E-mail address calderrm@sasktel.net