## STARS Cat
Pratt Institute - AASHE STARS - Sustainability Indicators
Institutional Characteristics
Operational Characteristics
Academics
Demographics
Academics
Campus Engagement
Public Engagement
Operations
|  | Air and Climate | GHG
|  |  | air emissions |  |  | 25000
|  |  | outdoor air quality |  |  | 15000
75000
|  | Buildings | Bldg Operation & Maintenance |  |  | 115000
|  |  | Bldg Design & Construction |  |  | in the last 5 years NC Maj Reno - PMC - 25,000 sf, Des ctr 15,000, res hall 75,000
Designed and built to LEEG certified equivalent
|  | Energy | Bldg Energy Consumption
|  |  | Clean & Renewable Energy |  |  | 23,500 Kwhrs on site
[6 empty] | 102,000 MM btu, NG; 27,000 MM btu oil = |  | 102000 | oil - % | NG - %
[6 empty] | 158.41 Kbtu/sf |  | 27000 | 27000 | 102000
[8 empty] | 129000 | 0.2093 | 0.7907
|  |  | Thermal | MM btu
|  | Food & Dining | Food & Beverage Purchasing
Sustainable Dining
|  | Grounds | Landscape Mgmt |  | Pratt's 25 acres campus is managed sustainably. No inorganic fertilizers, pesticides used. Organic topsoil added to lawns and beds annually. Leaves and grass clippings composted offsite.
Biodiversity
|  | Purchasing | Sustainable Procurement |  | Pratt IT Dept tries to purchase EPEAT computers and energy star whenever available.
Electronics
Cleaning & Janitorial
|  |  | Cat |  | % Green
|  |  | OP 13 | Cleaning & Janitorial |  | 175000
|  |  |  | Approx 50/50 split | 50% | total $ on Cleaning | $ green cleaning
[6 empty] | 87500 | 43750
[5 empty] | 90% | $ paper Products | $ green paper
[6 empty] | 87500 | 78750
|  |  |  | time period |  | annual 2018
about 50% janitorial and 50% paper
toilet tissue - all 100% recycled
roll towels all 100% recycled
hand soap - allGreen seal
trash bag liners approx 10%Ecologo
all buildings - gen'l purpose cleaner 100% Green seal
|  |  | Office Paper | We purchase Boise Paper. Boise has certificate in, FSC Chain of Custody, PERC Chain of Custody, and SF1 Certified Sourcing certificates for their products.
|  | Transportation | Campus Fleet |  | Fleet = 5 trucks, 3 sec cars, 1 mail car, 1 elect truck = 10
|  |  | Student Commute Modal Split |  |  |  | Pratt enourages students to live on campus by providing dorm spae
|  |  | Employee Commute Modal Split |  |  |  | Employees are enouraged to use Mass Transit
|  |  | Support for Sustainable Transit |  |  |  | Employees can purchase pre-tax mass transit the the Beniversal Program
|  | Waste | Waste Minimization & Diversion |  |  |  | Pratt changed Carters from 5 Star to RTS. Also went from single stream to single stream recyling. We are evaluating this change.
|  |  | Construction & Demolition Waste |  |  |  | C&D waste picked up separately. Steel, plastic, and masonry recovered Approx %75
|  |  | Hazardous Waste Mgmt |  |  |  | Pratt handles all waste according to Federal, State and local regs. Toxic product us is minimized by banning some mat'ls and finding alternatives for other mat'ls. Specialty vendors pickup, reuse and recycle electronic goods and other recoverable products.
|  | Water | Water Use
|  |  | Rainwater Mgmt. |  |  |  | Rainwater is managed via permeable surfaces. When we design landscape project we attempt to have 100% retention. We have completed a 100% retention parking lot and our Townhouses were converted to 100 % retention on the campus side, grounds not roofs.
Planning & Administration
|  | Coordination & Planning | Sustainability Coordination
Sustainability Planning
Particapatory Governance
|  | Diversity & Affordability | Diversity & Equity Coordination
Assessing D&E
Support for Underrepreented Groups
Affordability & Access

## Util Sum 18
Pratt Institute - Utility Data Summary - 2018 - April 29, 2019 | [17 empty] | 2016 - sf - 1,811,725 |  |  |  |  | 2015 - sf - |  |  |  |  | 2014 - sf - 1,627,500 |  |  |  | Pratt Institute - Utility Data Summary - Older
|  |  |  | 2018 | [5 empty] | 2017 | [6 empty] | 2016 |  |  |  | 2016 | 2015 | 2015 |  | 2015 | 2015 | 2014 |  |  | 2014 | Fleet |  |  |  |  | 2013 | 2013 |  |  |  | 2012 | Steam
Name | address | Con Ed Acct #'s |  | KW Hr | Nat Gas Acc't | Nat Gas | oil | Fleet | Tot therm | KW Hr | Nat Gas Acc't | Nat Gas | oil | Steam | Fleet |  | KW Hr | Nat Gas | oil | Steam | Fleet | KW Hr | Therms | oil | steam | Fleet | Kw Hr | therms | oil | Steam | Gals | Name | address | Con Ed Acct #'s |  | Therms | oil | Steam | Fleet | Therms | Oil Gal | Tot Therms | Therms | Therms 2011 | Oil Gal | KwHr - Meter | Kw-Hr - Bldg | KW Hr - Bldg | Kw Hr Acct
[6 empty] | Therms | gals | Gals | 503506 |  |  | Therms | gals |  | Gals |  |  | Therms | gals |  | Gals |  |  |  | therms |  |  |  | Gallons | Therms | [5 empty] | 2013 | 2013 | 2013 | Gal | 2012 | 2012 | 2012 Plant | 2011 | Steam - Plant | 2011 | 2011 | 2011 | 2012 | 2013
heating plant | 200 Willoughby Ave |  |  |  | 012 452 9810 | 503506 | 194258 |  | 26807604 |  | 012 452 9810 | 847587 | 54800 |  |  |  |  | 434216 | 0 | 452216 |  |  | 20082 | 0 | 20082 |  |  | 415420 | 30860 | 452455 |  | heating plant | 200 Willoughby Ave |  |  | 852044 | 54026 | 0il + gas |  | 783031 | 50741 | includes oil | 926143 | includes oil | 15458
"main meter" *** | 193 Ryerson St |  | sf - 2018 | 4888560 |  |  |  |  | 27311110 | 4487240 |  |  |  | included in Nat Gas |  |  | 4523640 |  | 18000 |  |  | 4689360 |  | 0 |  |  | 4546560 |  |  |  |  | "main meter" *** | 193 Ryerson St |  | sf | [6 empty] | 843920 |  | 944693 |  | 4694800 |  | 4707400 | 4391360
69-6031-1016-0200-5 | [31 empty] | 69-6031-1016-0200-5 | [9 empty] | per bldg
chemistry bldg |  | "main meter" | 27024 |  | 012-484-2150 | 742 |  | 6500 |  |  | 012-484-2150 | 742 |  | Facil, Sec. | 6548 | Facil, Sec, Mail | 243664 | 1941 |  | 11417 |  | 252588 | 1500 |  | 509 |  | 244896.674 | 1596 |  | 11461 |  | chemistry bldg |  | "main meter" | 23000 | 1800 |  |  |  | 1688 |  | 21376 |  | 23929 |  |  | 211057 | 214369
dekalb hall |  | "main meter" | 24058 |  |  | na |  | 2000 |  |  |  | na |  | bus | 2065 | Bus Svc | 275444 | na |  | 12906 |  | 285535 | na |  | 575 |  | 276839.719 | na |  | 12956 |  | dekalb hall |  | "main meter" | 26000 | [6 empty] | 24164 |  | 27050 |  | 94320 | 94320 | 91960
East bldg |  | "main meter" | 53865 |  |  | central Pl | [5 empty] | central Pl |  |  |  |  | 423760 | central Pl |  | 19856 |  | 439284 | central pl |  | 885 |  | 425907.26 | central |  | 19932 |  | East bldg |  | "main meter" | 40000 | [6 empty] | 37176 |  | 40616 |  |  | 529000 | 540634
Esther Jones | 243 Ryerson St | "main meter" | 44801 |  |  | 8285 | [5 empty] | 6221 |  |  |  |  | 413166 | 5936 |  | 19359 |  | 428302 | 6588 |  | 863 |  | 415259.578 | 7012 |  | 19434 |  | Esther Jones | 243 Ryerson St | "main meter" | 39000 | 5990 |  |  |  | 5026 |  | 36247 | 4902 | 40020 |  | 208560 | 173105 | 162282
Engineering Bldg |  | "main meter" | 58716 |  |  | na | [5 empty] | na |  |  |  |  | 603858 | na |  | 28295 |  | 625980 | na |  | 1261 |  | 606917.845 | na |  | 28403 |  | Engineering Bldg |  | "main meter" | 57000 | [6 empty] | 52976 |  | 55303 |  |  | 524074 | 532298
ISC Bldg |  | "main meter" | 26314 |  |  | na | [5 empty] | na |  |  |  |  | 296632 | na |  | 13899 |  | 307499 | na |  | 619 |  | 298135.082 | na |  | 13952 |  | ISC Bldg |  | "main meter" | 28000 | [6 empty] | 26023 |  | 29131 |  | 255680 | 255680 | 241440
Machinery |  | "main meter" | 36439 |  |  | chem | [5 empty] | chem |  |  |  |  | 328414 | chem |  | 15388 |  | 340445 | chem |  | 686 |  | 330078.126 | chem |  | 15447 |  | Machinery |  | "main meter" | 31000 | [6 empty] | 28811 |  | 32252 |  | 1019600 | 284468 | 288932
Main Bldg |  | "main meter" | 52880 |  |  | na | [5 empty] | na |  |  |  |  | 455542 | na |  | 21345 |  | 472231 | na |  | 951 |  | 457850.304 | na |  | 21427 |  | Main Bldg |  | "main meter" | 43000 | [6 empty] | 39964 |  | 43737 |  |  | 570000 | 582221
Memorial Hall |  | "main meter" | 18524 |  |  | na | [5 empty] | na |  |  |  |  | 180098 | na |  | 8439 |  | 186696 | na |  | 376 |  | 181010.585 | na |  | 8471 |  | Memorial Hall |  | "main meter" | 17000 | [6 empty] | 15800 |  | 17687 |  |  | 223000 | 228730
Library |  | "main meter" | 56839 |  |  | na | [5 empty] | na |  |  |  | 37206 | 466136 | na |  | 21841 |  | 483213 | na |  | 973 |  | 468497.986 | na |  | 21925 |  | Library |  | "main meter" | 44000 | [6 empty] | 40894 |  | 45778 |  | 854240 | 854240 | 832480
North Hall |  | "main meter" | 67026 |  | 012-480-6001 | 12990 |  |  |  |  | 012-480-6001 | 11911 |  |  |  | 41400 | 497918 | 11904 |  | 24821 |  | 516169 | 11640 |  | 1040 |  | 500441.03 | 10799 |  | 23420 |  | North Hall |  | "main meter" | 47000 | 11223 |  |  |  | 11593 |  | 43682 | 11535 | 47899 |  | 2262400 | 622000 | 635360
South Hall |  | "main meter" | 16021 |  |  | na | [5 empty] | na |  |  |  | 1080 | 148316 | na |  | 6950 |  | 153750 | na |  | 310 |  | 149067.541 | na |  | 6976 |  | South Hall |  | "main meter" | 14000 | [6 empty] | 13012 |  | 14566 |  |  | 185000 | 189453
Student Union |  | "main meter" | 11729 |  |  | see * | [5 empty] | tba |  |  |  | 79686 | 105940 | tba |  | 4964 |  | 109821 | na |  | 221 |  | 106476.815 | tba |  | 4983 |  | Student Union |  | "main meter" | 10000 | [6 empty] | 9294 |  | 10404 |  |  | 133400 | 134002
Thrift Hall |  | "main meter" | 9110 |  |  | na | [5 empty] | na |  |  |  |  | 84752 | na |  | 3971 |  | 87857 | na |  | 177 |  | 85181.452 | 0 |  | 3986 |  | Thrift Hall |  | "main meter" | 8000 | 0 |  |  |  | 0 |  | 7458 | 0 | 8323 |  |  | 35455 | 33238
Arc | 395 Dekalb Ave | 69-6031- 1016 0100-7 | 114452 | 1929600 |  | 9168 |  |  |  | 2016000 | 012 480 5001, 5310 | 6992 |  |  |  |  | 2003200 | 7586 |  | 54107 |  | 1940000 | 7197 |  | 2411 |  | 2089600 | 10342 |  | 54315 |  | Arc | 395 Dekalb Ave | 69-6031- 1016 0100-7 | 109000 | 7877 |  |  |  | 5957 |  | 101305 | 5960 | 111403 |  |  | 1880000 | 2016000 | 2208800
Cct | 280 - 296 Classon Ave | 69-6031-1017-0000-7 | 29259 | 280500 |  | 12000 |  |  |  | 315240 | 012 48 7400 | 12343 |  |  |  |  | 320880 | 11961 |  |  |  | 322200 | 15184 |  |  |  | 288360 | 13863 |  | na |  | Cct | 280 - 296 Classon Ave | 69-6031-1017-0000-7 | 29000 | 11923 |  |  |  | 9670 |  | 0 | 13226 | NA |  |  | 291840 | 306480 | 297720
Grand Ave Res Hall | 100 Grand Ave | PLP |  |  |  | 5367 |  |  |  |  | 5112 | 10966 | [5 empty] | 11836 | 668 |  |  |  | 10000 | 750 |  |  | NA | 10000 | 750 | na |  | Grand Ave Res Hall | 100 Grand Ave | HH |  | 7500 |  |  |  | 7451 |  | 0 | 7716 | NA |  |  | 68077 | 83256 | 80000
| 100 Grand | HCM |  |  | 012-482-5122 | [5 empty] | 012-482-5122 | 6719 | [5 empty] | 6802 |  |  |  |  | 6600 |  |  |  |  | 7000 |  |  |  |  | 100 Grand | HCM
sign
Grand Ave Res Hall |  | Total | 27053 | 150455 |  |  | 500 |  |  | 102951 |  |  | 500 |  |  |  | 145680 |  |  |  |  | 145000 |  |  |  |  | 150000 |  |  |  |  | Grand Ave Res Hall |  | Total | 21000
Higgins Hall | 282 Lafayette Ave | 69-6031-1019-0200-9 | 138349 | 1164000 | 024-172-7770 | 62169 | 2500 |  |  | 1187200 | 024-172-7770 | 73821 | 2500 |  |  |  | 1272800 | 67836 | 6547 |  |  | 1253600 | 70699 | 7000 |  |  | 1443200 | 70325 | 4501 | na |  | Higgins Hall | 282 Lafayette Ave | 69-6031-1019-0200-9 | 136000 | 50719 | 2000 |  |  | 49361 |  | 0 | 49823 | NA |  |  | 1095200 | 1198400 | 1305600
Leo J Pantas | 224 Grand Ave | 69-6031-1017-0100-5 | 66590 | 571200 | 012-480-6500 | 4500 |  |  |  | 539200 | 012-480-6500 | 8584 |  |  |  |  | 593280 | 8790 |  | 29287 |  | 610880 | 9608 |  | 1305 |  | 550400 | 10786 |  | 29400 |  | Leo J Pantas | 224 Grand Ave | 69-6031-1017-0100-5 | 59000 | 9848 |  |  |  | 9740 |  | 54835 | 10036 | 60384 |  |  | 601280 | 578560 | 588160
513 Myrtle Ave | 513 Myrtle Ave | 62-2038-1215-0000-1 | na | na | na | na |  |  |  | na | na | na |  |  |  |  | na | na? |  |  |  | na | na |  |  |  | NA | NA |  | na |  | 513 Myrtle Ave | 513 Myrtle Ave | 62-2038-1215-0000-1 | [7 empty] | 0 |  | NA |  |  | 59 | 2648 | 2500
Myrtle Hall | 536 Myrtle Ave | 62-2038-0702-0000-9 | 133424 | 2053600 |  | 75064 |  |  |  | 2065600 |  | 78052 |  |  |  |  | 2085600 | 67194 |  |  |  | 1932000 | 70000 |  |  |  | 2044800 | 67427 |  | na |  | Myrtle Hall | 536 Myrtle Ave | 62-2038-0702-0000-9 | 120000 | 50,000 est |  |  |  | 44855 |  | 0 | 68568 | NA |  |  | 2298720 | 2068800 | 2210000
Pratt Hse | 229 Clinton Ave | 69-6031-1018-0100-3 | 19784 | 37296 | 012-450-3011 | 12568 |  |  |  | 26694 | 012-450-3011 | 14753 |  |  |  |  | 30726 | 11749 |  |  |  |  | 13868 |  |  |  | 12000 | 13472 |  | na |  | Pratt Hse | 229 Clinton Ave | 69-6031-1018-0100-3 | 16000 | 10000 |  |  |  | 9371 |  | 0 | 10419 | NA |  |  | 39708 | 36081 | 30141
Pratt Manhattan Ent | 142 144 W 14th ST | 43-1011-0680-0007-0 | 96382 | inc |  | inc |  |  |  | 1250800 | [6 empty] | 1339200 | 21999 | 0 |  |  | 1485600 | 26575 |  |  |  | 1403600 | tba |  | na |  | Pratt Manhattan | 142 144 W 14th ST | 43-1011-0680-0007-0 | 75000 | 23876 | 500 |  |  | 31080 |  | 0 | 15997 | NA |  |  | 1342400 | 1467600 | 1597820
PMC base |  |  | inc | inc |  | inc |  |  |  | 24849 |  | 60053 |  |  |  |  | 32508 | 9698 |  |  |  | na | na | [6 empty] | na |  | PMC base
PMC 2 Sto |  |  |  | inc |  | inc |  |  |  | 35520
PMC All |  |  |  | 1284570 |  | 50000
Pratt Studios | 369 Dekalb Ave | 69-6031-1018-0000-5 | 74532 | 479840 |  | 1748 |  |  |  | 489280 |  | 1748 |  |  |  |  | 531840 | 1105 |  | 34251 |  | 563200 | 1500 |  | 1526 |  | 556480 | 1573 |  | 34383 |  | Pratt Studios | 369 Dekalb Ave | 69-6031-1018-0000-5 | 66000 | 1686 |  |  |  | 1591 |  | 64129 | 1540 | 70788 |  |  | 533600 | 558880 | 586560
Des Ctr - included in Pratt Studios |  |  | 5000 |  |  | na | [5 empty] | na | [5 empty] | na | [9 empty] | na |  |  |  | Des Ctr - included in Pratt Studios |  |  | 3000
Film&Video | 550 Myrtle Ave | 62-2038-0705-0000-2 | 15479 | 314720 |  | 10700 |  |  |  | 302400 |  | 8341 |  |  |  |  | 269280 | 7851 |  |  |  | 261280 | 7000 |  |  |  | 71920 | 6467 |  |  |  | Film&Video | 550 Myrtle Ave | 62-2038-0705-0000-2 | 15000 | 3207 |  |  |  | 2659 |  | 0 | 3510 | NA |  |  | 164960 | 146400 | 109760
Stabile Hall | 240 Will Ave | 69-6031-1017-0300-1 | 79756 | 832400 | 012-452-9800 | 4537 |  |  |  | 876000 | 012-452-9800 | 4429 |  |  |  |  | 925600 | 4919 |  | 37230 |  | 944800 | 6906 |  | 1659 |  | 926400 | 7373 |  | 37373 |  | Stabile Hall | 240 Will Ave | 69-6031-1017-0300-1 | 75000 | 7394 |  |  |  | 6479 |  | 69705 | 7262 | 77030 |  |  | 1003200 | 1030800 | 989200
Steuben Hall | 379 Dekalb Ave | 69-6031-1016-0000-9 | 114000 | 958000 |  | na |  |  |  | 900400 |  | na |  |  |  |  | 952800 | na |  | 56589 |  | 938400 | na |  | 2521 |  | 932000 | 0 |  | 56806 |  | Steuben Hall | 379 Dekalb Ave | 69-6031-1016-0000-9 | 114000 | [6 empty] | 105952 |  | 116605 |  |  | 754800 | 881600 | 886000
Tnhses - Emerson PL |  |  | 28048 | 57640 |  | 2226 |  |  |  | 54880 |  | 2166 |  |  |  |  | 71640 | 1801 |  | 8089 |  | 96000 | 2400 |  | 360 |  | 62960 | 2493 |  | 8120 |  | Tnhses - Emerson PL |  |  | 55000 | 515 |  |  |  | 458 |  | 15146 | [5 empty] | 61240 | 36240
Tnhses - Steuben |  | 622110033200010 | 28048 | 59440 |  | 1024 |  |  |  | 49080 |  | 2166 |  |  |  |  | 50800 | 982 |  | 8089 |  | 95000 | 2400 |  | 360 |  | 42043 | 1256 |  | 8120 |  | Tnhses - Steuben |  | 622110033200010 |  | 44 |  |  |  | 44 |  | 15146 |  |  |  | 8490 kwhr |  | 4051 | 18786
Tnhses - Will Ave |  |  | 28048 | 37360 |  | 216 |  |  |  | 33612 |  | 2166 |  |  |  |  | 10570 | 1142 |  | 11123 |  | 105000 | 2400 |  | 495 |  | 0 | 1636 |  | 11165 |  | Tnhses - Will Ave |  |  |  | 100 |  |  |  | 250 |  | 20825 |  |  |  | 11329 kwhr |  | 8830 | 9470
Willoughby Hall | 215 Willoughby Ave | 69-6031-1017-0200-3 | 289258 | 1290000 | 012-480-4020 | 226356 |  |  |  | 1398800 | 012-480-4020 | 175868 |  |  |  |  | 1373200 | 182536 |  |  |  | 1335200 | 210677 |  |  |  | 1302400 | 182469 |  | na |  | Willoughby Hall | 215 Willoughby Ave | 69-6031-1017-0200-3 | 283000 | 196312 |  |  |  | 175699 |  | na | 185870 | NA |  |  | 1414400 | 1320800 | 1368400
WRH | Kitchens |  |  | na | 012-480-4000 | inc |  |  |  | na | 012-480-4000 | 5671
248 Flushing Ave * |  | 62 2144 5251 0100 6 | 0 | na | na | na |  |  |  | na | na | na |  |  |  |  | 21852 | 2146 |  |  |  | 29000 | 2150 |  |  |  | 25000 | 2150 |  | na |  | 248 Flushing Ave * |  | 62 2144 5251 0100 6 | 11000 | 14000 |  |  |  | 2177 |  | na | 11444 | NA |  | 11000 | 45240 | 44800 | 43360
123 W 18th St |  | 43 4135 1710 0801 4 | 10430 | 54120 | na | 6500 |  |  |  | 107920 | na | 6571 |  |  |  |  | 154120 | na |  |  |  | 150000 | [9 empty] | 123 W 18th St |  | 43 4135 1710 0801 4 | 12000 | 11000 | [5 empty] | na |  | NA |  | 12000 | 151280 | 165000 | 165040
Pfizer |  |  | 26000 | 344705 |  | 10209 |  |  |  | 338000 |  | 16380 | [19 empty] | Pfizer |  |  | 26000
Totals |  |  | 1827238 | 16788006 |  | 1019875 | 197258 | 8500 |  | 16601666 |  | 1364250 | 57800 | see gas, oil | 8613 |  | 16709216 | 881930 | 25215 |  | 6548 | 16896530 | 504974 | 7750 |  | 5750 | 16447722.997 | 843459 | 36111 |  | 5000 | Totals |  |  | 1652000 | 1227058 | 56526 |  | 5000 |  |  | 843920 | 1333951 | 872905 | 15458 |  | 16379563 | 16687625 | 16924917
|  |  | sf - 2018 | KW HR | NG Acc't # | Therms | #2 oil, gal | Fleet Gal |  | KW HR | NG Acc't # | Therms | #2 oil | Steam | Fleet Gal |  | KW HR | Therms | Gal Heat | Steam | Fleet Gal | KwHr | Therms | Gal heat |  | Fleet Gal | Kw Hr | Therms | Heat oil |  | Fleet gal |  |  |  | SF
2016
Pfizer estimated - similar usage to PMC
123 W18 NG estimated similar to PMC |  |  |  |  | 58,550 X 125,000 Btu/gal/100,000 = 73,188 therms | [5 empty] | 58,550 X 125,000 Btu/gal/100,000 = 73,188 therms
302932 MM BTU
Notes Pantas dec - add electric DHW
Pfizer - sf estimates |  |  | MM btu/yr for 2018 = 1,019,875,000 +
123 W 18 gas sf est - no meters
Cct - NG - est readings very low |  |  | 197,258 x120,000 = 23,670,000,000
24,619 MM btu/yr thermal

## NYC GHG 07 - 18
Pratt Institute - Carbon/GHG - Draft - 6/18/19 - Bldgs, Fleet, Pratt owned - Revised 2/2020
| Year | Carbon #/sf | Elec | CDD | HDD | NG | Oil | SF | MT CO2e | # Carbon/sf | # C/ sf |  |  |  |  | GHG |  |  |  | Elec, NG, Oil |  |  | On site | EUI | CDD | HDD | MM BTU
|  | % Reduction | kwhrs |  |  | therms | gal |  |  |  | # C NG | #C Oil | #c fleet | # C Elec |  | C Elec | C NG | Oil | NG&Oil |  | tC Fleet | t SW | Kw Hr | Kbtu/sf/yr |  |  | Thermal
| 2007 | Base Yr | 14380326 | 1346 | 4777 | 1087149 | 190144 | 1595000 | 13887.5925 | 19.1553 | 7.9898 | 2.705 | 0.0586 | 8.402 | t | 6079 | 5780 | 1957 | 7737 | 13816 | 42 |  |  | 170.68 |  |  | 108715
5526.4189 | MT | [12 empty] | MT | MT | 5526.4189 | 5254.598 | 1779.1087 | 7033.7067 | 12560.1256 | 38.1822 | 2292 |  |  |  |  | 26240
| 2008 | 3.85 | 14307089 | 1142 | 4426 | 1280833 | 42388 | 1595000 | 14422.57 | 19.8932 | [13 empty] | 183.02 |  |  | 134955
| 2009 | 2,14 | 13519178 | 1041 | 4647 | 1243833 | 72535 | 1595000 | 14185.205 | 19.5658 | [13 empty] | 178.25
| 2010 | -9.85 | 14155738 | 1712 | 4227 | 1164674 | 25.946 | 1595000 | 12519.8075 | 17.2687 | [13 empty] | 160.09
| 2011 | 1.39 | 16590076 | 1363 | 4288 | 1333951 | 15458 | 1624000 | 14336.8935 | 19.4219 | [13 empty] | 180.97
| 2012 | 2.03 | 16678625 | 1503 | 3792 | 1167874 | 50741 | 1624000 | 13853.4582 | 18.767 | [13 empty] | 174.25
| 2013 | 0.96 | 16924917 | 1388 | 4609 | 1227058 | 54026 | 1627500 | 14306.7607 | 19.3394 | [13 empty] | 179.25
| 2014 | 16.19 | 16447723 | 1183 | 4938 | 843459 | 36111 | 1627500 | 11876.1634 | 16.0538 | [13 empty] | 151.36
| 2015 | 29.6 | 16896530 | 1544 | 4496 | 504974 | 7750 | 1627500 | 9976.649 | 13.4861 | [13 empty] | 130.79
| 2016 | 23.34 | 16709216 | 1732 | 3978 | 881930 | 25215 | 1811725 | 12092.6879 | 14.6843 | [13 empty] | 138.64
| 2017 | 3.38 | 16601666 | 1429 | 3996 | 1364250 | 57800 | 1827238 | 15372.6364 | 18.5087 | [13 empty] | 165.79
| 2018 | 4.58 | 16788006 | 1688 | 4511 | 1019875 | 197 258 | 1827238 | 15180.5272 | 18.2774 | 6.5427 |  | 0.088 | 8.562 | t | 7096 | 5423 | 1917 | 7340 | 9013 | 73 | 640 |  | 158.41 | 1688 | 4511
| MT | [12 empty] | MT | MT | 6450.9736 | 4930.0493 | 1742.7447 | 6672.794 | 8193.7183 | 66.3643 | 581.824
| Notes | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | [13 empty] | 10
129111
|  | MM BTU - Thermal |  | 70.659 *1,827,238 *1000/1000/1000 = 129,111 MM btu
| 1 | Carbon reductions from the base year, 2007, %, (# carbon/sf/yr)
[16 empty] | 4930 | 1743 | 6673
| 2 | Electricity is used for lighting, fairly constant year to year, fans, cooling and plug load. Cooling should correspond to CDD, cooling degree days, which increases compressor usage. Fans fairly constant. Plug load, mainly computers, printing and 3D printing has been increasing year to year.lug load, Overall electricity use has been increasing.
| 3 | CDD, cooling degree days are from NYSERDA at LaGuardia Airport. Trend is greater CDD per year re climate change and more variability.
| 4 | HDD, heating degree days are from NYSERDA at LaGuardia Airport. Trend should be decreasing re climate change, also more variable.
| 5 | Natural gas usage in therms from the utility bills Pratt receives from Nat'l Grid for Bklyn and Con Ed for Manhattan. Natural gas is primarily used for space heating and domestic hot water as well as for cooking in the cafeteria and Willoughby Residence Hall. Changes in the use of natural gas are primarily driven by the fuel used in central plant for producing steam for the campus. In 2014/15, #3 boiler came back on line with a new burner fitted for natural gas. The usage appeared to drop significantly. We asked Nat'l Grid to check the meter and they replaced the meter. Nat gas generates significantly less carbon per energy unit than #2 oil.
| 6 | Fuel Oil, #6, #2 - Fuel oil is used primarily in Central Plant to produce steam for tne campus. Fuel oil was originally # 6 oil with no natural gas. We added natural gas and converted boilers #1 and 2 to natural gas and # 6 oil in approximately 2000. In approximately 2015, # 3 boiler was converted to natural gas and NYC law required all boilers to be converted to # 2 oil. We try to run natural gas as the primary fuel as the carbon emissions are less than oil and gas has been less expensive than oil. After about 1 year of usage on # 3 boiler, the tubes began leaking and the boiler has been out of service. As a result in 2015 we rented an all oil,#2 boiler, which has become the main source of steam for the campus. #2 fuel usage has increased as a replacement for natural gas because of the failure of #3 boiler.
| 7 | Square Feet
| 8 | GHG - MTCO2e - Metric Tonnes of Carbon Dioxide equivalent for electricity, nat gas, fuel oil and Pratt vehicles
| 9 | Carbon Intensity - # of carbon/sf/yr
Energy Intensity - Btu/sf/yr
10

## SW 18
Pratt Institute - Solid waste data estimates for 2018 - Draft, 6/12/19
Mo | All (tons) | Recycle P,M,G | Paper, Cardboard | Subtot Recycled | Recycled x 100 = % | Waste to Energy * | Landfill 5 - 10 % (tons) ** | C&D tot | C&D % recover | Compost
Jan | 90 | 22 | 22 | 44 | 0.48889 | 55 | 9 | 17
Feb | 89 | 20 | 16 | 36 | 0.40449 | 62 | 9 | 18
Mar | 93 | 21 | 15 | 36 | 0.3871 | 66 | 9 | 14
April | 83 | 19 | 12 | 31 | 0.37349 | 61 | 9 | 12
May | 77 | 17 | 15 | 32 | 0.41558 | 52.5 | 7.5 | 103
June | 58 | 9 | 9 | 18 | 0.31034 | 46 | 6 | 9
July | 58 | 9 | 7 | 16 | 0.27586 | 48 | 6 | 31
Aug | 118 |  |  | 39 | 0.33051 | 0 | 79 | 8
Sept | 83 |  |  | 29 | 0.3494 | 0 | 54 | 7
Oct | 100 |  |  | 28 | 0.28 | 0 | 72 | 7
Nov | 102 |  |  | 29 | 0.28431 | 0 | 73 | 8
Dec | 105 |  |  | 29 | 0.27619 | 0 | 76 | 9
Tot | 1056 |  |  | 367 | 0.34754 | 390.5 | 409.5 | 243 | 182.25
Yard | 30 | [8 empty] | 30
1086
Give Take | 8 |  |  |  | 8
***Bulk/Constrution - Mat'l very variable - steel, plasti, masonry recovered - approx 75% recovered
Totals 2018 All Pratt - Solid Waste
| Tot Tons | Diverted | % Diverted
| 548 | 405
| 508 | 152
| 1056 | 557 | 53%
xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx
Pratt Institute - Solid waste data estimates for 2017 - Draft, 2/13/2018
Mo | All (tons) | Recycle P,M,G | Paper, Cardboard | Subtot Recycled | Recycled x 100 = % | Waste to Energy * | Landfill 5 - 10 % (tons) ** | Bulk***
Jan | 90 | 22 | 22 | 44 | 0.48889 | 55 | 9 | 17
Feb | 89 | 20 | 16 | 36 | 0.40449 | 62 | 9 | 18
Mar | 93 | 21 | 15 | 36 | 0.3871 | 66 | 9 | 14
April | 83 | 19 | 12 | 31 | 0.37349 | 61 | 9 | 12
May | 77 | 17 | 15 | 32 | 0.41558 | 52.5 | 7.5 | 103
June | 58 | 9 | 9 | 18 | 0.31034 | 46 | 6 | 9
July | 58 | 9 | 7 | 16 | 0.27586 | 48 | 6 | 31
Aug | 80 | 16 | 19 | 35 | 0.4375 | 53 | 8 | 99
Sept | 74 | 15 | 14 | 29 | 0.39189 | 52 | 7 | 16
Oct | 67 | 11 | 12 | 23 | 0.34328 | 51 | 7 | 11
Nov | 81 | 12 | 6 | 18 | 0.22222 | 71 | 8 | 15
Dec | 93 | 12 | 13 | 25 | 0.26882 | 77 | 9 | 9
Total | 943 | 183 | 160 | 343 | 0.36373 | 694.5 | 94.5 | 354
* all mat'l that is not recycled goes to a 'waste to energy' plant to produce energy
** Waste to energy plant, non burnable for energy, from 5-10% goes to landfill
*** bulk mat'ls are picked up in 30 or 40 yard containers, on a call basis. This mat'l is very variable.
The GiveTake Program removed 9095 pounds of mat'ls and gives back to students 16/17.
The GiveTake Program removed 8900 pounds of mat'ls and gives back to students 17/18 to date.

## Transport
Transport - Students & Fac Staff
2018 | Students |  | Fac/Staff
FTE students | 4829 |  | 1096
Res Hall Students | 1783 |  | 11
Parking Passes Stud | 162 |  | 401
Students Driving and not parking on campus - very little off campus parking | 10% | 304.6 | 1096 - 11= 1085 | 401+
cars to school - 162 +304 =466 |  |  | 1085-401=684 | 469 | Drive
4829 - 466 = 4363 |  |  | 684*.1=68
% sustainable is 466/4829 students | 96.5
Fac staff
% sustainable -1096 - 469 = 627 green |  |  | 1085-401-68/1096 |  | 57%
627/1096=57% |  |  | 616/1096

## GHG 17
Pratt Institute - GHG Inventory 2017 Climate Change - Feb, 2019
Scope 1, 2 and solid waste from NYC Carbon Challenge - Mayor's Ofc of Sustainability
Category |  | T CO2e | Mult | MTCO2e
1.1
Fuel | Nat gas | 7254 |  | 7979
| oil B5 | 562 |  | 618
Electricity | elec | 7018 |  | 7720
Solid Waste |  | 431 |  | 474
Pratt Fleet |  | 77 |  | 85
commuting |  |  |  | 1095
air travel |  |  |  | 1170
GHG 2017 - MTCO2e |  |  |  | 19141