## Sheets Description
OP 5 : Building Energy Efficiency
Sheets description
Score Part 1 | This sheet details the input values required in the criterion. The inputs are specified in accordance with their nomination in the STARS technical manual formula and the information are related to the performance year 2019. Each value in the 5th column is the sum of the three values related to the three parts of the campus scope (UM6P, Experimental Farm and the Green Energy park). Imported electricity of UM6P is calculated based on the electrical billing during the three year period (2017-2019) detailed in the sheet "Purchased electricity" where only data of 2018 and 2019 is considerated. Renewable energy in campus is detailed in the sheet "Data Energy Campus". Stationary fuels used on site to generate electricty concerns the electricity produced by the generators on site which the energy genereted is calculated in the sheet " ". The value is given in KWH so it has been multiplied by 0,0032 in the formula of The total energy comsumption.
Score Part 2 | This sheet details the input values required in the criterion. The inputs are specified in accordance with their nomination in the technical manual formula. Each value in the 5th column is the sum of the three values related to the three parts of the campus scope (UM6P, Experimental Farm and the Green Energy park). The values of the baseline year are related to 2018. The total gross floor area of the campus has not changed from 2018 to 2019. Concerning the imported electricity, we have considerated 66% of the total purchased energy that is resulted from primary sources. While the 34% remain value is added to the renewable energy on site because according to the national ministry of mine and energy, 34% of the energy distributed around the country results from clean and renewble energy (Solar, Eolen, Hydraulics). Find the info in the following link https://www.mem.gov.ma/Pages/secteur.aspx?e=2. The Source-site ratio for grid Purchased electricity (B) chosen is 2,5 according to the STARS technical manual.
Data Energy Campus | This sheet is a sum up of the input data related to energy consumption in each part of the campus scope (UM6P, Experimental Farm and the Green Energy Park) during both the performance and the baseline year. The on site renewbale energy is genereted by photovoltaic panels in the campus.
Energy Experimental Farm | This sheet details the purchased energy according to the monthual billing of 2018 and 2019, in addition to the renewable energy produced on site by the photovoltaic panels in the farm. This energy used is split on two parts (On Grid and Off Grid energy).
Renewbale energy UM6P | This sheet describes the thermoelectrical energy generated by the photovoltaic panels that are installed on the roof of the detailed buildings. In the first step, we have calculated the electrical power of each installation multiplied by the functionning duration which split on two period (Heat and cold). During the heat period (4 months), the panels function 0,5 H/day. During the cold period (7 months), they function 5 hours/day. The panels don't function the month of August.
Purchased electricity UM6P | This sheet visualizes data of purchased energy consolidated after collecting electrical bills from the general administration of the university during the 3 year period 2017-2019. Only data of 2018 and 2019 is considerated in order to be in harmony with other available data (Gross Floor area, Renewbale energy ...)
Total Degree days | This sheet is generated from the online simulation https://www.degreedays.net/ generate of the average heating and cooling degree days of Benguerir City. It's Celsius-based 2-year-average (2018 to 2019) cooling and heating degree days with a base temperature of 19 C.
Energy generators UM6P | This sheet describes the electrical energy generated by the generators on site. They were mainly used during electrical blackouts that took place in 2019 and 2018. In the first step, we have calculated the electrical power of each generator multiplied by the functionning duration wich is the duration of the blackouts, vacuum tests and annual maintenance.

## Score Part 1
Sheets description
Part 1 : Site energy use per unit of floor area
Inputs | UM6P | GEP | Experimental Farm | Total Campus
A : Gross floor Area of Building Space (Square Feet) | 1144848.276 | 77479.272 | 18298.8 | 1240626.348
B : Floor Area of Laboratory (Square Feet) | 15338.7 | 3527.3628 | 13691.808 | 32557.8708
C : Floor Area of healthcare space (Square Feet) | 1278.7632 | 0 | 0 | 1278.7632
D : Floor Area of other energy intensive space (Square Feet) | 111598.9992 | 613.548 | 0 | 112212.5472
Campus EUI-Adjusted Floor Area (Square meter) |  |  |  | 1420512.1632
A : Imported electricity, Performance year (KWH) | 5134800 | 145062.06 | 45732.72 | 5325594.78
B : Electricity from on-site, non-combustion facilities/Devices (Renewable Energy), Performance year (KWH) | 2879260 | 230300.84 | 55408.68 | 3164969.52
C : Stationary fuels used on site to generate electricty and thermal energy (KWH) | 26197 | 0 | 0 | 26197
D : Imported steam, hot water, performance year (MMBtu) | 0 | 0 | 0 | 0
Total Degree days Performance year (°F) | 4299 | 4299 | 4299 | 4299
Total energy consumption (site energy), performance year (MMBtu) |  |  |  | 29059.1896

## Score Part 2
Sheets description
Part 1 : Site energy use per unit of floor area
Inputs | UM6P | GEP | Experimental Farm | Total Campus
A : Imported electricity, Performance year (KWH) | 5134800 | 145062.06 | 45732.72 | 5325594.78
B : Source-site ratio for grid Purchased electricity | 2.5 | 2.5 | 2.5 | 2.5
C : Electricity from on-site, non-combustion facilities/Devices (Renewable Energy), Performance year (KWH) | 2879260 | 230300.84 | 55408.68 | 3164969.52
D : Stationary fuels used on site to generate electricty and thermal energy. Performance year (KWH) | 26197 | 0 | 0 | 26197
E : Imported steam, hot water, performance year (MMBtu) | 0 | 0 | 0 | 0
A : Imported electricity, Baseline year(KWH) | 4417385.94 | 152073.24 | 10382.46 | 4579841.64
B : Source-site ratio for grid Purchased electricity | 2.5 | 2.5 | 2.5 | 2.5
C : Electricity from on-site, non-combustion facilities/Devices (Renewable Energy), Baseline year(KWH) | 2509683.06 | 219769.76 | 5348.54 | 2734801.36
D : Stationary fuels used on site to generate electricty and thermal energy. Baseline year (KWH) | 10000 | 0 | 0 | 10000
E : Imported steam, hot water, Baseline year (MMBtu) | 0 | 0 | 0 | 0
B : Gross floor Area of Building Space (Square feet), Baseline year | 1144848.276 | 77479.272 | 18298.8 | 1240626.348
D : Gross floor Area of Building Space (Square feet), Baseline year | 1144848.276 | 77479.272 | 18298.8 | 1240626.348

## Data Energy Campus
Sheets description
| UM6P | GEP | Experimental Farm
Solar energy generated on site, 2019 (KWH) | 234060 | 155571.9 | 31849.4
Total Puchased Electricity from ONEE, 2019 (KWH) | 7780000 | 219791 | 69292
Solar energy generated on site, 2018 (KWH) | 234060 | 141429 | 0
Total Puchased Electricity from ONEE, 2018 (KWH) | 6693009 | 230414 | 15731
Electricity produced from electrogen group, 2019 (KWH) | 26197 | 0 | 0
Electricity produced from electrogen group, 2018 (KWH) | 10000 | 0 | 0

## Energy Experimental farm
Input data experimental farm
Production Solar Enegry 2019
Étiquettes de lignes | 2019-06-01 | 2019-07-01 | 2019-08-01 | 2019-09-01 | 2019-10-01 | 2019-11-01 | 2019-12-01
Somme de KW/JOUR/ON GRID | 4125.9 | 4245.2 | 4269.8 | 4055.2 | 3887.7 | 3625.6 | 3547.5
Somme de KW/JOUR/ OFF GRID | 611.7 | 617.8 | 632.9 | 607.5 | 564.8 | 532.7 | 525.1
Total Solar Energy Produced | bar: 2019-06-01
Total energy on Grid 2019 (KWH) | 2019-06-01: 27756.9
Total energy off Grid 2019 (KWH) | 2019-06-01: 4092.5; 2019-10-01: Sheets description
Total Energy Purchased | bar: 2019-06-01
Total Purchased energy 2018 (KWH) | 2019-06-01: 15731
Total Purchased energy 2019 (KWH) | 2019-06-01: 69292

## Renewbale Energy UM6P
Sheets description
Thermo electrical energy in the UM6P
Localisation | Nombre de ballon auxiliaire | Capacite de ballon en L | Puissance resistance d'appui / ballon ECS (KW) | Puissance globale / localisation (KW) | Energie consommee en periode froide (KWh) | Energie consommee en periode chaude (KWh)
HG1 | 7 | 800 | 5 | 35 | 21000 | 3675
HG3 | 7 | 800 | 5 | 35 | 21000 | 3675
Batiment sportif | 2 | 2000 | 10 | 20 | 12000 | 2100
batiment d'enseignement | 1 | 2000 | 10 | 10 | 6000 | 1050
Restaurant universite | 1 | 5000 | 72 | 72 | 43200 | 7560
HG2 | 16 | 400 | 5 | 80 | 48000 | 8400
HG4 | 16 | 400 | 5 | 80 | 48000 | 8400
Total |  |  |  |  | 199200 | 34860
Total annuel |  |  |  |  | 234060

## Purchased Electricity UM6P
Energie electrique achetée en KWH
| 2017 | 2018 | 2019 | Moyenne
Jan | 700000 | 628042 | 650000 | 659347.3333
Fev | 660000 | 619105 | 623000 | 634035
Mars | 648667 | 606771 | 613000 | 622812.6667
Avr | 515933 | 526346 | 586000 | 542759.6667
Mai | 615000 | 467028 | 576000 | 552676
Juin | 517570 | 432439 | 574000 | 508003
Juil | 613036 | 500902 | 623000 | 578979.3333
Aout | 594805 | 488436 | 590000 | 557747
Sep | 610911 | 545508 | 689000 | 615139.6667
Oct | 657826 | 593005 | 669000 | 639943.6667 | Sheets description
Nov | 531091 | 635427 | 670000 | 612172.6667
Dec | 564132 | 650000 | 917000 | 710377.3333
Total | 7228971 | 6693009 | 7780000 | 602832.7778

## Energy Generators UM6P
Sheets description
Type par reservoir interne | puissance (kW) | Energie generée (kWh) |  |  | Quantité | Total (kWh)
|  | Coupures electriques 6h | testes à vide 15min/sem =13h/an | Entretien 4h/an
GE de 200L | 90 | 540 | 1170 | 360 | 7 | 14490
GE de 150L | 51 | 306 | 663 | 204 | 2 | 2346
GE de 1500L | 407 | 2442 | 5291 | 1628 | 1 | 9361
Total (KWh) |  | 3288 | 7124 | 2192 | 10 | 26197

## Total Degree Days
Description: | Celsius-based 2-year-average (2018 to 2019) cooling and heating degree days with a base temperature of 19 C
Source: | www.degreedays.net
Accuracy: | Estimates were made to account for missing data: the "% Estimated" column shows how much each figure was affected (0% is best, 100% is worst)
Station: | Marrakech, MA (8.04W,31.61N)
Station ID: | GMMX
|  | HDD 19 | % Estimated |  | CDD 19 | % Estimated
| Jan | 238 | 0.1 | Jan | 6 | 0.1
| Feb | 171 | 0.02 | Feb | 21 | 0.02
| Mar | 110 | 0.02 | Mar | 40 | 0.02
| Apr | 93 | 0.1 | Apr | 50 | 0.1
| May | 42 | 0.03 | May | 137 | 0.03
| Jun | 16 | 0 | Jun | 151 | 0
| Jul | 2 | 0.1 | Jul | 247 | 0.1
| Aug | 0 | 0.02 | Aug | 329 | 0.02
| Sep | 2 | 0 | Sep | 216 | 0
| Oct | 30 | 0 | Oct | 129 | 0
| Nov | 112 | 0.07 | Nov | 22 | 0.07
| Dec | 167 | 0.02 | Dec | 22 | 0.02
| Total | 983 | 0.04 | Total | 1370 | 0.04