## Building
Building Energy Use (Excluding Central Utility Plant)
(Includes only energy used at the building, does not include energy used on behalf of the building by the central plant) |  |  |  |  | 2020 Fiscal Year | [8 empty] | 2021 Fiscal Year
|  |  | Square Feet |  | kBTU | kBTU | kWh | kWh | kBTU | kBTU | US gal | kBTU | kBTU/SF/y | kBTU | kBTU | kWh | kWh | kBTU | kBTU | US gal | kBTU | kBTU/SF/y
Campus | Building Number | Building Name | Area | UR Electric | Hot Water | Chilled Water | Electricity | Imported Electric | Gas | Steam | Water | Total Energy Use | Site Energy Use Index | Hot Water | Chilled Water | Electricity | Imported Electric | Gas | Steam | Water | Total Energy Use | Site Energy Use Index
ESM | 400 | Eastman School Of Music | 406610 | No |  |  | 3525706 | 3525706 |  |  | 12660000 | 12029708.872 | 29.5854 |  |  | 3383067 | 3383067 |  |  | 8692000 | 11543024.604 | 28.3884
ESM | 402 | Eastman Commons | 145966.9 | No |  |  | 1697000 | 1697000 | 10773867.9281 |  | 2750000 | 16564031.9281 | 113.478 |  |  | 1496591 | 1496591 | 10125638.5451 |  | 2170000 | 15232007.0371 | 104.3525
ESM | 406 | Messinger Hall | 32699 | No |  |  | 270260 | 270260 |  |  | 830000 | 922127.12 | 28.2005 |  |  | 202275 | 202275 |  |  | 376000 | 690162.3 | 21.1065
ESM | 1344 | 1344 University Avenue |  | No |  |  |  | 0 | [7 empty] | 8400 | 8400 | 569560.9143 |  |  | 598221.7143
MAG | 414 | Memorial Art Gallery | 134047 | No |  |  | 1489036 | 1489036 | 10150113.6245 |  | 1356000 | 15230704.4565 | 113.6221 |  |  | 1557276 | 1557276 | 9200308.4365 |  | 1029000 | 14513734.1485 | 108.2735
MC | 101 | Golisano Childrens Hospital at Strong-GCHaS | 271860.7 | Yes | 34519725.45 | 19937450.8634 | 5814168.984 |  |  | 2765353.1482 | 9004041.4823 | 77060474.0351 | 283.4557 | 32160994.9634 | 21474136.5877 | 6084033.479 |  |  | 1855077.817 | 7112326.8498 | 76248931.5986 | 280.4706
MC | 102 | Medical Center Annex | 79098.9 | Yes |  | 2779870.9671 | 1520841.235 |  |  | 12195705.2696 |  | 20164686.5304 | 254.93 |  | 2733071.2835 | 1531109.3955 |  |  | 6471352.7624 |  | 14428569.3036 | 182.4118
MC | 104 | School of Medicine and Dentistry | 1169321.9 | Yes | 35657289.6743 | 82862072.9537 | 16666662.3519 |  | 1409178.2141 | 163369522.3556 | 65016043.4249 | 340164715.1424 | 290.9077 | 46816591.1426 | 77286506.2135 | 15730478.322 |  | 1441237.9665 | 87491308.2745 | 43394894.299 | 266708035.6319 | 228.0878
MC | 105 | Strong Memorial Hospital | 1030970 | Yes | 58108205.7607 | 154660237.5368 | 23431876.5211 |  |  | 72013016.7638 | 9862643.1788 | 364731022.7511 | 353.7746 | 51527305.6357 | 173139414.4779 | 24317429.1154 |  |  | 72013016.7638 | 8210825.7725 | 379650805.0193 | 368.2462
MC | 106 | R-Wing-Psychiatry | 175564.8 | Yes | 11796322.1307 | 13261384.8919 | 2223567.4714 |  |  | 1479028.8999 | 6607103.8306 | 34123548.1349 | 194.3644 | 11286130.2459 | 12159382.9782 | 2063762.1947 |  |  | 96563.7437 | 10335685.8356 | 30583633.576 | 174.2014
MC | 107 | SGG-Wing | 472082.5 | Yes | 44252254.7091 | 51535383.694 | 12275466.8748 |  | 1862207.3315 | 124985212.3294 | 13544449.9328 | 264518951.0408 | 560.3236 | 41743336.4697 | 50436815.4403 | 12260293.1036 |  | 1966441.5517 | 117065053.7692 | 0 | 253043767.3003 | 536.016
MC | 110 | Parking Garage | 654696.4 | Yes |  |  | 673959.7357 |  |  |  | 76987.3091 | 2299550.6181 | 3.5124 |  |  | 662714.2277 |  |  |  | 50433.9845 | 2261180.945 | 3.4538
MC | 111 | Kornberg Medical Research Building | 235913.8 | Yes | 14737627.11 | 27218762.2552 | 9470442.5652 |  | 22683.9759 | 47517247.4867 | 8848000 | 121809470.8603 | 516.3304 | 16248418.36 | 29757341.5989 | 9567373.7161 |  | 15799.7344 | 50840794.209 | 9358000 | 129506233.0215 | 548.9557
MC | 112 | Eastman Dental Center | 92028.9 | No |  | 6850591.0526 | 1499507.9594 | 1499507.9594 | -310.1911 | 8288975.425 | 2536022.9433 | 20255577.4441 | 220.1002 |  | 7160674.1592 | 1602154.9194 | 1602154.9194 | 0 | 5974013.674 | 2707465.0699 | 18601240.418 | 202.1239
MC | 113 | Levine Pavilion | 66516.9 | Yes | 3321360.4881 | 4379477.7691 | 1071693.5273 |  |  | 588569.2353 |  | 11946025.8076 | 179.5938 | 4468164.518 | 5993647.8954 | 1084703.2075 |  |  | 547405.4658 |  | 14710225.2231 | 221.1502
MC | 114 | Autoclave Building | 5618 | Yes |  |  | 339067.6677 |  |  | 1833666.6662 | 3116693.9358 | 2990565.5484 | 532.3185 |  |  | 440948.1993 |  |  | 1833666.6662 | 2432956.5761 | 3338181.9223 | 594.194
MC | 115 | Del Monte Institute | 152226.9 | Yes | 16185547.4915 | 17066812.5029 | 5413170.1903 |  |  | 22356997.5167 | 5107926.1237 | 74079094.2003 | 486.636 | 15477994.0378 | 17464662.5629 | 5289890.3205 |  |  | 22337142.7288 | 4607712.5711 | 73328905.1029 | 481.7079
MC | 116 | Emergency Department | 175847.8 | Yes | 18858336.5744 | 10233336.8332 | 5619363.3668 |  |  | 12696459.3346 | 4354698.2527 | 60961400.5496 | 346.6714 | 19447992.7715 | 11415749.638 | 5437048.091 |  |  | 14783856.3321 | 1133112 | 64198806.8281 | 365.0817
MC | 119 | Wilmot Cancer Center | 1102144 | Yes | 18472689.673 | 23641182.8894 | 5975260.4583 |  |  | 15048591.3279 | 6519454.9553 | 77550052.5741 | 70.3629 | 18915482.533 | 24330392.1531 | 6115520.6 |  |  | 28074775.0773 | 8424347.0944 | 92186806.0507 | 83.6432
MC | 108-109 | Access Center and Ambulatory Care Facility | 279166.7 | Yes | 338999.7559 | 14499518.4686 | 4647770 |  |  | 26258826.5231 | 5497359.3548 | 56955535.9876 | 204.0198 | 264737.4658 | 16075184.7245 | 4509533 |  |  | 27287453.642 | 911074.8387 | 59013902.4283 | 211.3931
Mid | 103 | Helen Wood Hall | 119063.9 | Yes | 5489923.1172 | 4612406.5359 | 839632.007 |  |  |  | 1414758.205 | 12967154.0609 | 108.9092 | 5159065.7552 | 4235173.919 | 761039.4808 |  |  |  | 483920.9203 | 11990906.3826 | 100.7098
Mid | 118 | Childrens School at URMC | 7898 | No |  |  | 73200 | 73200 | 313433.1104 |  | 392000 | 563191.5104 | 71.3081 |  |  | 68120 | 68120 | 215442.7372 |  | 253000 | 447868.1772 | 56.7065
Mid | 120 | Saunders Research Building | 194522.8 | Yes | 9012037.1376 | 5263623.0487 | 1254616.5833 |  |  |  | 1052020.8726 | 18556411.9687 | 95.3945 | 13457253.6309 | 6020558.1558 | 1208392.5338 |  |  |  | 1754632136.1747 | 23600847.1121 | 121.3269
Mid | 144 | Valentine Tower | 57427.9 | No |  |  | 466482.8 | 466482.8 |  |  |  | 1591639.3136 | 27.7154 |  |  | 397010.579 | 397010.579 |  |  |  | 1354600.0955 | 23.5878
Mid | 147 | De Kewiet Tower | 57427.9 | No |  |  | 403110 | 403110 |  |  |  | 1375411.32 | 23.9502 |  |  | 370559.9444 | 370559.9444 |  |  |  | 1264350.5304 | 22.0163
Mid | 514 | 514 Intercampus Drive-UFC Annex | 3421 | No |  |  | 28642 | 28642 | 120438.4383 |  |  | 218164.9423 | 63.7723 |  |  | 24904 | 24904 | 109056.2617 |  |  | 194028.7097 | 56.717
Mid | 141-149 | Southside Living Center | 131672.9 | No |  |  |  | 0 | 11662005.1216 |  | 9041000 | 11662005.1216 | 88.568 |  |  |  | 0 | 10745969.7397 |  | 15038000 | 10745969.7397 | 81.6111
Mid | 151-159 | University Park | 232323.8 | No |  |  | 617707 | 617707 | 14291074.9277 |  | 6633000 | 16398691.2117 | 70.5855 |  |  | 600696 | 600696 | 13434897.425 |  | 6360000 | 15484472.177 | 66.6504
Mid | N/A | 520 Intercampus Drive-EHS | 4316 | No |  |  | 131402 | 131402 | 459442.5495 |  | 28372.8279 | 907786.1735 | 210.3304 |  |  | 119709 | 119709 | 488868.7365 |  | 25634.4081 | 897315.8445 | 207.9045
Off | 61 | 575 Mount Hope Avenue | 11128 | No |  |  | 63132 | 63132 | 505971.7361 |  | 16000 | 721378.1201 | 64.8255 |  |  | 48024 | 48024 | 406940.7218 |  | 1000 | 570798.6098 | 51.2939
Off | 62 | 590 Mount Hope Avenue | 7116 | No |  |  | 31008 | 31008 | 327191.5872 |  | 21000 | 432990.8832 | 60.8475 |  |  | 24825 | 24825 | 291629.6771 |  | 10000 | 376332.5771 | 52.8854
Off | 63 | 668 Mount Hope Avenue | 4356 | No |  |  | 27208 | 27208 | 268115.1895 |  | 57000 | 360948.8855 | 82.8625 |  |  | 18112 | 18112 | 194800.019 |  | 41000 | 256598.163 | 58.9068
Off | 64 | 685 Mount Hope Avenue-Fairbank | 10379 | No |  |  | 62393 | 62393 | 367556.4566 |  | 77000 | 580441.3726 | 55.9246 |  |  | 39604 | 39604 | 362863.5652 |  | 38000 | 497992.4132 | 47.9808
Off | 65 | 692 Mount Hope Avenue | 10464 | No |  |  | 54409 | 54409 | 677717.5511 |  | 79000 | 863361.0591 | 82.5077 |  |  | 54311 | 54311 | 611516.7639 |  | 61000 | 796825.8959 | 76.1493
Off | 66 | 630 Mount Hope Avenue | 13319 | No |  |  | 71246 | 71246 | 523942.8084 |  | 180000 | 767034.1604 | 57.5895 |  |  | 34556 | 34556 | 432026.1773 |  | 90000 | 549931.2493 | 41.2892
Off | 201 | Aab Cardiovascular Research Institute | 110746.9 | No |  |  | 6232523 | 6232523 | 27883609.475 |  | 8554000 | 49148977.951 | 443.7955 |  |  | 6881019 | 6881019 | 34727205.9089 |  | 11316000 | 58205242.7369 | 525.57
Off | 521 | 300 Science Parkway-PDC | 41965 | No |  |  | 7423389 | 7423389 | 282063.7834 |  | 2984000 | 25610667.0514 | 610.2864 |  |  | 7495012 | 7495012 | 328042.1113 |  | 3236000 | 25901023.0553 | 617.2054
Off | 522 | 315 Science Parkway | 29873 | No |  |  | 389520 | 389520 | 1423467.0176 |  | 211000 | 2752509.2576 | 92.1404 |  |  | 344000 | 344000 | 1688780.4809 |  | 105000 | 2862508.4809 | 95.8226
Off | 523 | University Farmington Data Center | 19009 | No |  |  | 2389000 | 2389000 |  |  |  | 8151268 | 428.811 |  |  | 2337000 | 2337000 |  |  |  | 7973844 | 419.4773
Off | 561 | 110 Office Park Way | 9000 | No |  |  | 71460 | 71460 | 832492.9103 |  | 17000 | 1076314.4303 | 119.5905 |  |  | 57900 | 57900 | 756666.1924 |  | 7000 | 954220.9924 | 106.0246
RC | 1 | Hutchison Hall | 313147.7 | Yes | 57370305.304 | 36448359.536 | 9091619.9841 |  | 44547.4463 | 12476829.966 | 4845134 | 137360649.6379 | 438.6449 | 59448333.186 | 44701012.3517 | 9268084.2844 |  | 42306.0653 | 17096152.7675 | 4816323.464 | 152910507.9488 | 488.3016
RC | 2 | Computer Studies Building | 108964.9 | Yes | 5598888.6585 | 5927681.4085 | 1702620.5827 |  |  |  | 516346.4754 | 17335911.4952 | 159.0963 | 5427461.9895 | 5859503.6931 | 1632340.4185 |  |  |  | 143696.7928 | 16856511.1906 | 154.6967
RC | 3 | Wegmans Hall | 60975.9 | Yes | 1144000 | 2334535.8312 | 821481.0001 |  |  |  | 249981.1644 | 6281429.0034 | 103.0149 | 1747536.152 | 2352850.762 | 812811.1749 |  |  |  | 170305.7581 | 6873698.6428 | 112.7281
RC | 5 | Wilmot Hall | 47286 | Yes | 5293707.0203 | 5146424.7432 | 1068116.2 |  |  |  | 784133.7271 | 14084544.238 | 297.8587 | 4396550.2489 | 8795623.9931 | 980608.9333 |  |  |  | 108608.3392 | 16538011.9225 | 349.7444
RC | 6 | NYS Optics Institute | 4383 | Yes | 646999.0605 | 587160.8497 | 107300.0898 |  |  |  | 2192.9881 | 1600267.8167 | 365.1079 | 589035.1116 | 508836.9857 | 107159.8378 |  |  |  | 1663.0812 | 1463501.4638 | 333.9041
RC | 7 | Hylan Hall | 59913.9 | Yes | 3846233.4429 | 4277585.9348 | 496685.505 |  |  |  | 292866 | 9818510.3207 | 163.877 | 3886822.9329 | 4391994.9105 | 486218.9581 |  |  |  | 291124.536 | 9937796.9284 | 165.868
RC | 8 | Goergen Hall | 113426.9 | Yes | 16694316.2616 | 8123208.0303 | 2559395.1983 |  |  | 288399.2808 | 1793845.6019 | 33838579.9894 | 298.3294 | 18007008.7384 | 7468152.2377 | 2740719.3729 |  |  | 761295.74 | 1290886.8312 | 35587791.2164 | 313.7509
RC | 10 | Interfaith Chapel | 29283 | Yes | 2181120.3963 | 443183.9438 | 212970.7858 |  |  |  | 75206.1069 | 3350960.6614 | 114.4337 | 2336023.3618 | 405306.4622 | 238113.7668 |  |  |  | -96265.9489 | 3553773.9963 | 121.3596
RC | 11 | Wallis Hall | 49598 | Yes | 1225845.6672 | 980171.0318 | 377665.1918 |  |  | 1435084.7233 | 1024812.5665 | 4929695.0567 | 99.393 | 1252624.1688 | 933415.0046 | 315502.3343 |  |  | 1425782.2794 | 599407.5402 | 4688315.4175 | 94.5263
RC | 12 | Dewey Hall | 122889.9 | Yes |  | 3062191.5723 | 925762.9429 |  |  | 4157621.9462 | 438672.911 | 10378516.6795 | 84.4538 |  | 2522493.4243 | 876978.4667 |  |  | 8758315.4237 | 149175.6755 | 14273059.3763 | 116.1451
RC | 13 | Hopeman Engineering Building | 72251.9 | Yes | 3108179.0841 | 1973871.0869 | 557879.826 |  |  |  | 1335284.7975 | 6985536.1373 | 96.6831 | 3005270.5291 | 1546020.3975 | 536388.3088 |  |  |  | 1457832.2447 | 6381447.8361 | 88.3222
RC | 14 | Hoyt Hall | 19940 | Yes |  | 885654.0252 | 202454.4444 |  |  | 2010889.9524 |  | 3587318.5419 | 179.9056 |  | 715782.3244 | 217436.7021 |  |  | 2385669.7884 |  | 3843346.1403 | 192.7455
RC | 15 | Gavett Hall | 79684.9 | Yes |  | 5601031.3782 | 1293554.9944 |  |  | 10067441.2095 | 1479724.7607 | 20082082.2286 | 252.0187 |  | 5482939.7026 | 1229757.2151 |  |  | 9786527.1407 | 674916.3068 | 19465398.4614 | 244.2796
RC | 16 | Taylor Hall | 11739 | Yes |  | 439272.9369 | 219571.2011 |  |  | 2727783.1858 | 10633.991 | 3916233.061 | 333.6087 |  | 1099446.5897 | 184449.2842 |  |  | 2983375.1644 | 2314.6305 | 4712162.7119 | 401.4109
RC | 17 | Bausch and Lomb Hall | 114227.9 | Yes |  | 5305715.7892 | 1975159.1798 |  |  | 9439993.8538 | 61150.123 | 21484952.7644 | 188.0885 |  | 6207963.3777 | 1875472.3801 |  |  | 7414000.7267 | 55402.8866 | 20021075.8654 | 175.2731
RC | 18 | Meliora Hall | 130969.9 | Yes | 10797333.242 | 6513998.5422 | 1902332.2352 |  |  | 8631344.8915 | 579298.6979 | 32433434.2624 | 247.6404 | 10666015.0932 | 7037375.6703 | 1902597.5992 |  |  | 9060706.4532 | 485745.0511 | 33255760.2251 | 253.9191
RC | 19 | Harkness Hall | 61989.9 | Yes | 1331916.7168 | 761185.0027 | 335558.6457 |  |  | 1805372.2466 | 290019.4716 | 5043400.0654 | 81.3584 | 1299946.8407 | 794737.0469 | 333912.341 |  |  | 28386.3953 | 281905.7854 | 3262379.1905 | 52.6276
RC | 20 | Gleason Hall | 41698 | Yes | 1166495.7987 | 519948.4576 | 272053 |  |  | 61735.6303 | 154894.9917 | 2676424.7227 | 64.1859 | 1740154.4723 | 763807.5431 | 293810 |  |  | 0 | 171326.3767 | 3506441.7354 | 84.0914
RC | 20 | Schlegel Hall | 73180 | Yes | 1373133.4329 | 1109077.4921 | 994712.3532 |  |  |  | 484765.8229 | 5876169.4743 | 80.2975 | 1864767.0138 | 1237473.3999 | 1073331.7468 |  |  |  | 122906.8908 | 6764448.3338 | 92.4358
RC | 21 | Todd Union | 54306.9 | Yes |  | 222203.9621 | 188678.9189 |  |  | 2148568.0539 | 123474 | 3014544.4872 | 55.5094 |  | 276626.6636 | 225963.9211 |  |  | 1686506.3701 | 80514.6693 | 2734121.9325 | 50.3458
RC | 22 | Strong Auditorium | 43131 | Yes |  |  | 40429.2471 |  |  | 2488768.1741 | 387211.2653 | 2626712.7652 | 60.9008 |  |  | 71401.7667 |  |  | 2649174.4976 | 402148.2503 | 2892797.3255 | 67.07
RC | 23 | Lattimore Hall | 81123.9 | Yes | 5875309.9243 | 3510361.5332 | 974266.4869 |  |  |  | 600016.1778 | 12709868.7109 | 156.6723 | 8028378.2287 | 5714760.0093 | 1118909.4461 |  |  |  | 614870.4661 | 17560857.2682 | 216.4696
RC | 24 | LeChase Hall | 79566.9 | Yes | 1729514.1356 | 1751223.0761 | 533408.9907 |  |  |  | 138481.4421 | 5300728.6881 | 66.6198 | 1396796.9874 | 1449300.6591 | 535243.6015 |  |  |  | 42225.0411 | 4672348.815 | 58.7223
RC | 25 | Morey Hall | 59680.9 | Yes | 1207163.46 | 3357972.0317 | 218210.626 |  |  | 2924374.0581 | 304964.0644 | 8234044.2057 | 137.9678 | 1286811.0192 | 5193287.9033 | 223999.8221 |  |  | 2901809.7463 | 204811.1976 | 10146196.0617 | 170.0074
RC | 26 | Frederick Douglass Commons | 89150.9 | Yes | 9289003.4173 | 4283496.6504 | 1564788.4589 |  | 935917.0685 |  | 4679000 | 19847475.3579 | 222.6279 | 9786651.8019 | 4236107.8729 | 1625493.4022 |  | 934557.3908 |  | 2594579.2571 | 20503500.554 | 229.9865
RC | 27 | Rush Rhees Library | 349283.7 | Yes |  | 8575920.662 | 2003661.8987 |  |  | 21351017.6516 | 2057204.3669 | 36763432.7121 | 105.2538 |  | 6000529.1442 | 1850607.2068 |  |  | 21225065.9424 | 1050880.7888 | 33539866.8763 | 96.0247
RC | 28 | Wilson Commons | 104337.9 | Yes |  | 5131702.3087 | 2035435.102 |  |  | 6258924.3845 | 4089000 | 18335531.2612 | 175.7322 |  | 4983913.8617 | 2059215.4666 |  |  | 5494633.2574 | 5400644.4444 | 17504590.2912 | 167.7683
RC | 29 | Rettner Hall | 20605 | Yes | 935275.754 | 1605245.9595 | 337536.4768 |  |  |  |  | 3692196.1723 | 179.1893 | 787753.289 | 1511699.2966 | 379336.1717 |  |  |  |  | 3593747.6033 | 174.4114
RC | 31 | Tiernan Hall | 40950 | Yes | 2279284.1035 |  | 196456.5201 |  |  |  | 429796.6144 | 2949593.7501 | 72.0292 | 2096492.3653 |  | 197485.9308 |  |  |  | 242769.4541 | 2770314.3612 | 67.6511
RC | 32 | Lovejoy Hall | 42622 | Yes | 1912556.0324 |  | 261947.4594 |  |  |  | 1092758.7763 | 2806320.7641 | 65.8421 | 1927966.3353 |  | 258415.3137 |  |  |  | 742401.2606 | 2809679.3856 | 65.9209
RC | 33 | Burton Hall | 33449 | Yes | 1646981.1729 |  | 168537.6112 |  |  |  | 699203.6201 | 2222031.5025 | 66.4304 | 1693687.5703 |  | 168543.7326 |  |  |  | 573207.987 | 2268758.7858 | 67.8274
RC | 34 | Gilbert Hall | 72774.9 | Yes | 2838059.5019 |  | 391743.1708 |  |  |  | 764082.8701 | 4174687.2008 | 57.3644 | 3186365.7281 |  | 377134.5051 |  |  |  | 431590.1405 | 4473148.6596 | 61.4655
RC | 35 | Hoeing Hall | 43377 | Yes | 2614978.9548 |  | 150208.424 |  |  |  | 1112117.5908 | 3127490.0975 | 72.1002 | 2631921.2261 |  | 150545.2293 |  |  |  | 755553.3016 | 3145581.5486 | 72.5173
RC | 36 | Crosby Hall | 32247 | Yes | 1887405.1781 |  | 123453.0022 |  |  |  | 701181.5249 | 2308626.8217 | 71.592 | 1804921.101 |  | 123002.8778 |  |  |  | 544993.1009 | 2224606.92 | 68.9865
RC | 37 | Robert B. Goergen Athletic Center | 244043.8 | Yes | 5629548.0771 | 2340492.1975 | 2397381.5252 |  |  | 688935.4006 | 2022407.6596 | 16838841.4393 | 68.9993 | 10722011.5718 | 2465526.3603 | 2032902.3242 |  |  | 348646.6845 | 906716.9184 | 20472447.3467 | 83.8884
RC | 38 | Fauver Stadium | 63096.9 | Yes | 1727318.5843 | 223430.4869 | 413019.0238 |  |  |  | 567041.0069 | 3359969.9805 | 53.251 | 1664703.5592 | 242643.1485 | 347936.6826 |  |  |  | 457131.5189 | 3094506.6689 | 49.0437
RC | 39 | University Health Service Building | 27790 | Yes | 2178602.5557 | 1000334.5459 | 277824.2447 |  |  |  | 149003.4555 | 4126873.4244 | 148.5021 | 3089726.8897 | 2061819.9137 | 306098.2626 |  |  |  | 110102.9443 | 6195954.0752 | 222.9562
RC | 40 | Danforth Dining Hall | 35128 | Yes | 5361906.4529 | 2904325.4504 | 867673.8973 |  | 86601.9243 |  | 1377159.6603 | 11313337.1652 | 322.0604 | 3988798.0357 | 1419662.4388 | 889594.9528 |  | 92652.309 |  | 409137.9198 | 8536410.7624 | 243.0087
RC | 41 | Spurrier Hall | 56011.9 | Yes | 2796416.2598 |  | 150157.8383 |  |  |  | 70574.6304 | 3308754.8039 | 59.0724 | 3549263.5713 |  | 167378.1232 |  |  |  | 230001.2833 | 4120357.7276 | 73.5622
RC | 42 | Susan B. Anthony Hall | 179431.8 | Yes | 7190748.664 | 1538452.96 | 1225820.0025 |  |  |  | 5017637.8495 | 12911699.4725 | 71.9588 | 7610322.668 | 1423710.7083 | 1114579.1751 |  |  |  | 4052498.308 | 12836977.5217 | 71.5424
RC | 43 | Wilder Tower | 78821.9 | Yes | 4444874.3311 |  | 318729.1529 |  |  |  | 1525824.6658 | 5532378.2009 | 70.1883 | 3389045.9473 |  | 304627.3162 |  |  |  | 1479677.7417 | 4428434.3501 | 56.1828
RC | 44 | Sage Art Center | 29821 | Yes | 2535632.9034 |  | 266823.7428 |  |  |  | 261706.7627 | 3446035.514 | 115.5573 | 2634111.3234 |  | 289156.5875 |  |  |  | 151413.0477 | 3620713.6 | 121.4149
RC | 45 | Anderson Tower | 74852.9 | Yes | 3934947.0635 |  | 338753.6036 |  |  |  | 2074728.0545 | 5090774.3588 | 68.0104 | 3487554.6746 |  | 324906.2688 |  |  |  | 1647918.7794 | 4596134.8639 | 61.4022
RC | 46 | O_Brien Hall | 54380.9 | Yes | 1732362.6822 | 809580.2634 | 296634.157 |  |  |  | 714303.2544 | 3554058.6893 | 65.3549 | 1913472.5857 | 938414.2188 | 293916.2416 |  |  |  | 605009.6899 | 3854729.0207 | 70.8839
RC | 47 | Genesee Hall | 71402.9 | Yes | 4972000 | 1918104.6097 | 484319.8007 |  |  |  | 2049508.5714 | 8542603.7696 | 119.6395 | 4453319.3317 | 2082625.1578 | 492477.2503 |  |  |  | 2313631.5951 | 8216276.8673 | 115.0692
RC | 48 | 612 Wilson Boulevard | 28572 | No | 1242422.1423 |  | 419631 | 419631 |  |  | 146482.5955 | 2674203.1143 | 93.5952 | 1252468.0199 |  | 357917 | 357917 |  |  | 117820.4844 | 2473680.8239 | 86.5771
RC | 91 | Drama House | 10221 | Yes | 431796.6363 |  | 31027.6615 |  |  |  | 126007.9909 | 537663.0172 | 52.6038 | 438906.4252 |  | 32078.0089 |  |  |  | 110657.9784 | 548356.5915 | 53.65
RC | 92 | Delta Kappa Epsilon Fraternity | 9066 | Yes | 379988.2897 |  | 31900.3585 |  |  |  | 361962.3639 | 488832.3129 | 53.9193 | 374408.2852 |  | 31296.9916 |  |  |  | 391469.5924 | 481193.6206 | 53.0767
RC | 93 | Alpha Delta Phi Fraternity | 10546 | Yes | 442929.2354 |  | 59021.7766 |  |  |  | 156312.6418 | 644311.5372 | 61.0953 | 511580.4001 |  | 52434.7973 |  |  |  | 98172.1387 | 690487.9286 | 65.4739
RC | 94 | Douglass Leadership House -Medieval House | 8389 | Yes | 420330.488 |  | 33228.898 |  |  |  | 143649.4868 | 533707.488 | 63.6199 | 357672.7984 |  | 33909.7086 |  |  |  | 114620.6847 | 473372.7241 | 56.4278
RC | 95 | Sigma Chi Fraternity | 8909 | Yes | 554000 |  | 54349.3873 |  |  |  | 193650 | 739440.1095 | 82.9992 | 474550.2007 |  | 39783.4047 |  |  |  | 186278.7667 | 610291.1777 | 68.5028
RC | 96 | Theta Chi Fraternity | 7611 | Yes | 410629.7683 |  | 50182.6924 |  |  |  | 167247.6809 | 581853.1146 | 76.449 | 475682.4986 |  | 31104.2461 |  |  |  | 115784.931 | 581810.1863 | 76.4433
RC | 97 | Psi Upsilon Fraternity | 13670 | Yes | 551443.5071 |  | 48269.1921 |  |  |  | 441541.6224 | 716137.9906 | 52.3876 | 568108.1963 |  | 50801.7171 |  |  |  | 228610.6977 | 741443.6549 | 54.2387
RC | 98 | Sigma Alpha Mu Fraternity | 11532 | Yes | 402928.4412 |  | 36821.4304 |  |  |  | 250125.6143 | 528563.1616 | 45.8345 | 322979.2184 |  | 28794.4364 |  |  |  | 95891.1388 | 421225.8353 | 36.5267
RC | 99 | Sigma Phi Epsilon Fraternity | 12650 | Yes | 574691.6397 |  | 46677.1964 |  |  |  | 211498.8562 | 733954.2339 | 58.0201 | 462367.0046 |  | 48640.3042 |  |  |  | 173208.9438 | 628327.7226 | 49.6702
RC | 125 | Goler House | 359143.7 | No | 14361000 |  | 1382718 | 1382718 |  |  | 11085000 | 19078833.816 | 53.1231 | 13964664.4039 |  | 1476683 | 1476683 |  |  | 5104000 | 19003106.7999 | 52.9123
RC | 51-56 | Hill Court | 151493.9 | Yes | 9589509.3481 |  | 616587.0196 |  |  |  |  | 11693304.2592 | 77.1866 | 9395666.9005 |  | 631774.3119 |  |  |  |  | 11551280.8526 | 76.2491
SC | 300 | University Facilities Center | 41046 | Yes |  |  | 305410 |  | 1332190.781 |  | 442000 | 2374249.701 | 57.8436 |  |  | 300789.8667 |  | 1381741.3098 |  | 439000 | 2408036.3349 | 58.6668
SC | 333 | Center For Optoelectronics | 98090.9 | Yes |  |  | 3244130.886 |  |  |  |  | 11068974.5831 | 112.8441 |  |  | 3828121.1933 |  |  |  |  | 13061549.5117 | 133.1576
SC | 334 | Lab For Laser Energetics | 199479.8 | Yes |  |  | 17343802.4918 |  | 34996691.9429 |  | 9744000 | 94173746.0451 | 472.0967 |  |  | 16916622.84 |  | 37334532.3185 |  | 11242000 | 95054049.4486 | 476.5096
SC | 340 | East River Road Medical Building | 92077.9 | Yes |  |  | 2115468.5 |  | 1109053.303 |  | 3388573.6077 | 8327031.825 | 90.4346 |  |  | 2295156.5667 |  | 1313739.4129 |  | 3111911.0285 | 9144813.6184 | 99.3161
SC | 301-332 | Whipple Park | 338597.7 | No |  |  | 349875 | 349875 | 19055190.1646 |  | 11145000 | 20248963.6646 | 59.8024 |  |  | 347873 | 347873 | 16377350.3106 |  | 10424000 | 17564292.9866 | 51.8736
SC | 335-336 | Bloch Alumni and Advancement Center | 133190.9 | No |  |  | 902277 | 902277 | 5403058.8988 |  | 594000 | 8481628.0228 | 63.6802 |  |  | 615601 | 615601 | 4958825.2004 |  | 293000 | 7059255.8124 | 53.001
[5 empty] | 486610351.863 | 568415216.5527 |  | 30071842.7594 | 147119515.0753 | 600360256.891 |  | 1802505340.3819 |  | 502370147.5306 | 602508075.022 |  | 29963200.4428 | 150549397.9833 | 530677529.3036 |  | 1786105149.8395
Data obtained from eSight EUI rollup reports 7/22/2021 | [15 empty] | Total in MMBTU: |  | 150549.398
[6 empty] | 2020-06-30 | 2021-07-01 | [10 empty] | 2304265.73
[15 empty] | Total MMBTU: | 1786105.1498 |  | 2454815.128
1802505.3404
2509156.6331
Note on K13: ====== ID#AAAASdC3AN0 Author (2021-12-06 04:15:24) used FY21 because FY20 was not available
Note on T20: ====== ID#AAAASdC3AN4 Author (2021-12-06 04:15:24) Using FY20 value because steam meter is offline in FY21
Note on H31: ====== ID#AAAASdC3AN8 Author (2021-12-06 04:15:24) Electricity is included in Valentine and DeKewiet
Note on G58: ====== ID#AAAASdC3AOA Author (2021-12-06 04:15:24) This reading is low because the CHW meter was not working correctly the first half of FY20
Note on S109: ====== ID#AAAAUVaOL7k Zein Tynon (2022-01-20 23:41:27) This is what I used specifically.

## Campus
Campus Site Energy Use (Excluding Central Utility Plant)
(Includes only energy used at the building, does not include energy used on behalf of the building by the central plant)
|  |  | FY20 |  | FY21
|  | SqFt | kBTU | kBTU/SqFt/y | kBTU | kBTU/SqFt/y
Campus | Abbreviation | Area | Energy | EUI | Energy | EUI
Eastman | ESM | 585275.9 | 29515867.9201 | 50.4307 | 28063415.6554 | 47.949
Memorial Art Gallary | MAG | 134047 | 15230704.4565 | 113.6221 | 14513734.1485 | 108.2735
Medical Center | MC | 5963058.2 | 1529610671.2246 | 256.5145 | 1477809224.3697 | 247.8274
Mid Campus | Mid | 808074.2 | 64240455.6228 | 79.4982 | 65980358.7686 | 81.6514
Off Campus | Off | 267355.9 | 90465891.1712 | 338.3725 | 98945318.1736 | 370.0884
River Campus | RC | 4208743.3 | 586154031.6275 | 139.2706 | 612913065.7142 | 145.6285
South Campus | SC | 902483.2 | 144674593.8416 | 160.3072 | 144291997.7125 | 159.8833
Total |  | 12869037.7 | 2459892215.8643 | 191.1481 | 2442517114.5424 | 189.798
This information is a summary of the consumption by individual buildings on the previous tab.
No consideration was given to asdjusting this information due to energy losses in the central plant.

## Summary
| FY20 | FY21
Imported Electric (Buildings) | 30071842.7594 | 29963200.4428 | kWh | Buildings Tab
Imported Gas (Buildings) | 147119.5151 | 150549.398 | mmBTU | Buildings Tab
Imported Electric (CUP) | 161646558 | 167844490 | kWh | H:\CU_Admin\Energy Management\Data\Energy Data from Paul\STATION 710 (AND MCCP)_ FY14_FY21 Electric Cost Actual.xlsx, STATION 710 WITH STANDBY RATE TARIFF_EFFECTIVE APRIL 19_2021 - June 2021.xlsx, CUP FY14_FY21 Electric Cost Actual.xlsx
Imported Gas (CUP) | 2312890.87 | 2304265.73 | mmBTU | H:\CU_Admin\Energy Management\Data\Energy Data from Paul\Natural Gas - Plant Historical Data - December 2021.xls
Imported Electric and Gas for all buildings on Building Tab
Imported Electric (Total) | 191718400.7594 | 197807690.4428 | kWh
Imported Gas (Total) | 2460010.3851 | 2454815.128 | mmBTU
Imported Fuel Oil (Generators) | 13674 | 15378 | Gal | H:\CU_Admin\EARTH\NOX Cap Rolling Avg Spreadheet\NOX SO2 CAP Track.xls
Imported Propane (Generators) | 3909.42 | 5947.8 | Gal | H:\CU_Admin\EARTH\NOX Cap Rolling Avg Spreadheet\NOX SO2 CAP Track.xls
Note: I don't know if Fuel Oil and Propane were used in the baseline year, so they are included seperatly. But the amount of Fuel Oil use is so low it makes little actual difference.
Note on C4: University of Rochester: CUP Substation + 710 Substation
Note on D4: University of Rochester: Includes CUP electric up to mid april 2021 + 710 electric up to mid april 2021 + 710 electric after mid april