## FCA Summary
BldgCode | BuildingName | Address | GSF | CostGSF | ReplacementValueExclContents | DMCostEST | FCI | CostGSFEsc | AssignableSqFt | Functionality | DateBuilt | AgeOfBldg | DateRemodel | Renovation year (age) | DMBBldgType | MUSICCode | AlarmDevices | Standpipes | SpecialExtinguishSystems | NoOfStories
AN | Anspach Hall | 1429 S. Washington St. | 122537 | 247.6512 | 30346431.1688 | 643643.0091 | 0.02121 | 0 | 63698 | Academic/Administration | 1966 | 50 | 2013 | 2013 | C | FR |  |  |  | 5
PM | Bohannon School House-Poor Museum | 401 W. Preston St. | 1166 | 193.0434 | 225088.5893 | 31004.9129 | 0.13775 | 0 | 898 | Miscellaneous | 1972 | 44 | 2005 | 1972 | C | F |  |  |  | 1
CM | Botanical Gardens Pavilion | Near Library Pond | 616 | 166.8217 | 102762.1428 |  |  | 0 | 616 | Academic/Administration | 2012 | 4 |  | 2012 | [5 empty] | 1
UC | Bovee University Center | 103 E Preston St. | 151317 | 319.3474 | 48322688.3176 | 7898735.6782 | 0.16346 | 0 | 85927 | Academic/Administration | 1960 | 56 | 1970, 2009 | 1960 | C/E | FR |  |  |  | 3
BR | Brooks Science Hall | 200 E. Library Dr. | 128461.0094 | 289.1468 | 37144092.3569 | 2408950.4623 | 0.064854 | 0 | 68211 | Academic/Administration | 1964 | 52 | 1993 | 1964 | C | FR |  |  |  | 4
BH | Carlin Alumni House | 524 E. Bellows St. | 11573.5353 | 310.7462 | 3596432.4628 | 967424.7083 | 0.269 | 0 | 8864 | Academic/Administration | 1941 | 75 | 1971, 1990 | 1941 | C | F |  |  |  | 3
EA | CART (Center For Applied Research Technology) | 2625 S. Denison Dr | 31312.5 | 304.7404 | 9542184.8955 | 131612.6915 | 0.013793 | 0 | 20616 | Academic/Administration | 2006 | 10 | 2006 renovation | 2006 |  | M |  |  | Yes - FM200 | 1
PH | Central Energy Facility | 1730 East Campus Dr. | 65058.2867 | 897.2764 | 58375264.4878 | 1320237.2802 | 0.022616 | 0 | 6721 | Miscellaneous/PowerHouse | 1961 | 55 | 1983, 1992 | 1961 | P | FR |  |  |  | 2
CS | Combined Services Building | 1720 East Campus Dr. | 70906 | 189.3541 | 13426342.7696 | 736173.0604 | 0.05483 | 0 | 61716 | Academic/Administration | 1990 | 26 |  | 1990 | C | NC |  |  |  | 2
DC | Data Center | 1710 S. East Campus Dr. | 5016 | 998.2917 | 5007431.1794 |  |  | 0 | 4500 | Academic/Administration | 2013 | 3 |  | 2013
SC | Dow Science Complex ** | 201 E. Ottawa Ct. | 170675.7765 | 241.2184 | 41170144.0068 | 9506389.7664 | 0.2309 | 0 | 105772 | Academic/Administration | 1992 | 24 |  | 1992 | C | M |  |  |  | 3
EV | Events Center | See Rose/SAC |  | 392.3941 | 17404602 | 0 | 0 | 0 |  | Academic/Administration | 2010 | 6 |  | 2010 | [5 empty] | 2
FI | Finch Field House | 1275 East Campus Dr. | 142963.9 | 274.1216 | 39189494.392 | 8434019.3569 | 0.21521 | 0 | 70390 | Academic/Administration | 1951 | 65 |  | 1951 | C | FR |  |  |  | 1
FS | Flammable Storage Bldg. | On Campus- Brooks | 630.0434 | 335.1984 | 211189.5348 | 0 | 0 | 0 | 518 | Miscellaneous | 1979 | 37 |  | 1979 | F | M |  |  |  | 1
FO | Foust Hall | 600 E. Preston St. | 53880.2484 | 244.4037 | 13168529.5166 | 1753571.3805 | 0.13316 | 0 | 30390 | Academic/Administration | 1973 | 43 | 1980, 1991 | 1973 | A/C | M |  |  |  | 3
GR | Grawn Hall | 150 E. Bellows St. | 102493.2726 | 249.5193 | 25574049.8843 | 3335811.8806 | 0.13044 | 0 | 48362 | Academic/Administration | 1915 | 101 | 1966, 1989 | 1915 | C | M |  |  |  | 4
GH | Greenhouse | On Campus- Brooks | 5675.6733 | 317.181 | 1800215.7876 | 0 | 0 | 0 | 4408 | Academic/Administration | 1992 | 24 |  | 1992 | C | M |  |  |  | 1
GE | Grounds East |  |  | 0 | 0 | 0 |  | 0 | 407.9 | Miscellaneous | 1965 | 51 |  | 1965 | H | F |  |  |  | 1
GN | Grounds North - Pole Bldg | On Campus- Lot 14 | 672 | 45.3223 | 30456.5839 | 0 | 0 | 0 | 672 | Miscellaneous | 1986 | 30 |  | 1986 | H | F |  |  |  | 1
GS | Grounds South - CHIP | 2375 West Campus Dr. | 33217 | 51.997 | 1727184.3388 | 0 | 0 | 0 | 27695 | Academic/Administration | 1987 | 29 | 1988 | 1987 | F | NC |  |  |  | 1
HP | Health Professions Building | 1280 East Campus Dr. | 234373 | 324.7349 | 76109097.4052 | 1518.608 | 1.9953e-05 | 0 | 131851 | Academic/Administration | 2003 | 13 | 2011 CMED | 2003 | C | M | Yes | Yes | Yes | 3
HP3 | Health Professions Gazebo | 1280 East Campus Dr. | 300 | 182.3295 | 54698.8437 | 0 | 0 | 0 |  | Academic/Administration | 2008 | 8 |  | 2008 | C | M | No | No | No | 1
IT | Industrial Education Technology Bldg. | 1700 East Campus Dr. | 118206.9792 | 243.8567 | 28825563.4418 | 160823.7487 | 0.0055792 | 0 | 73772 | Academic/Administration | 1989 | 27 |  | 1989 | C | NC |  |  |  | 2
AC | Indoor Athletic Complex | 360 E. Broomfield St. | 237908 | 70.3536 | 12628968.03 | 270051.5258 | 0.021383 | 0 | 151139 | Academic/Administration | 1998 | 18 |  | 1998 | E | FR |  |  |  | 2
IF | Intramural Sports Complex | 2201 S. Crawford St. | 2118.875 | 151.7857 | 321614.9789 | 0 | 0 | 0 | 1275 | Athletic Fields/Stadiums | 1999 | 17 |  | 1999 | E | FR |  |  |  | 1
ST | Kelly/Shorts Stadium | 2300 East Campus Dr. | 177093.0237 | 448.5578 | 79436449.8745 | 3548189.5764 | 0.044667 | 0 | 24292 | Athletic Fields/Stadiums | 1973 | 43 | 1985,1998 | 1973 | K | M |  |  |  | 2
L1 | Lot 1 Storage Building | On Campus- Douglas | 11087.8828 | 88.8965 | 985673.7488 | 61883.2751 | 0.062783 | 0 |  | Miscellaneous | 1984 | 32 |  | 1984 | H | F |  |  |  | 1
MO | Moore Hall & Bush Theatre | 401 E. Ottawa Ct. | 197566.5764 | 319.1972 | 63062706.0118 | 1874354.5524 | 0.029722 | 0 | 87915 | Academic/Administration | 1971 | 45 |  | 1971 | C | FR |  |  |  | 4
MP | Motor Pool-University Attorney's Offices | 1303 West Campus Dr. | 4421.4652 | 225.2173 | 995790.3878 | 158701.5048 | 0.15937 | 0 | 3480 | Academic/Administration | 1987 | 29 | 1988 | 1987 | C | M |  | No |  | 1
MS | Multi-Purpose Stadium | 2239 W. Campus Drive | 13579 | [7 empty] | 2015 | 1
MU | Music Building | 1400 East Campus Dr. | 109032.5182 | 217.4634 | 23710579.453 | 37256.5157 | 0.0015713 | 0 | 53260 | Academic/Administration | 1997 | 19 |  | 1997 | C | M |  |  |  | 2
BT | Bennett Track Grandstand,Pressbox, Field, Field Hockey Bleachers and Field | 200 E. Broomfield St. | 6117 | 1001.3589 | 6125312.681 | 1845960.3798 | 0.30137 | 0 |  | Athletic Fields/Stadiums | 1999 | 17 |  | 1999 | J | NC |  |  |  | TBD
ED | Education Building | 195 E. Ojibway Ct. | 146630 | 347.4781 | 50950713.3277 | 0 | 0 | 0 | 84147 | Academic/Administration | 2009 | 7 |  | 2009 | M | M | Yes |  |  | 4
NA | North Art Studio | 250 W. Preston St. | 18089.412 | 239.9637 | 4340801.4164 | 841137.9767 | 0.19377 | 0 | 10195 | Academic/Administration | 1976 | 40 |  | 1976 | C | NC |  |  |  | 2
PA | Park Library | 250 E. Preston St. | 282297.9294 | 302.5633 | 85413003.0852 | 1470379.0911 | 0.017215 | 0 | 208166 | Academic/Administration | 1969 | 47 | 2002 | 2002 | C | FR |  |  |  | 4
PE | Pearce Hall | 1501 S. Washington St. | 131122 | 251.1173 | 32926999.0314 | 7699062.3372 | 0.23382 | 0 | 63562 | Academic/Administration | 1967 | 49 |  | 1967 | C | FR | Yes | Yes |  | 5
PO | Powers Hall | 1101 S. Washington St. | 49565.4693 | 258.0561 | 12790672.1982 | 3377983.1148 | 0.2641 | 0 | 25035 | Academic/Administration | 1939 | 77 | 1960 | 1939 | C | M | Yes | Yes |  | 2
PB | Public Broadcasting | 1999 East Campus Dr. | 11331.5242 | 188.2173 | 2132788.9171 | 869677.6182 | 0.40777 | 0 | 6506 | Academic/Administration | 1981 | 35 | 1981 | 1981 | C | M | Yes | Yes |  | 1
RL | Research Laboratory Facility | 2630 Denison Drive | 14168 | 446.6166 | 6327663.9982 |  |  | 0 | 9160 | Academic/Administration | 2013 | 3 |  | 2013
S4 | Rinsing Station | On Campus- Lot 63 | 389.35 | 36.8498 | 14347.4843 | 0 | 0 | 0 | 377.69 | Miscellaneous | 1994 | 22 |  | 1994 | H | F | No | No |  | 1
RN | Ronan Hall | 1101 S. Washington St. | 66184.1215 | 256.9086 | 17003268.2969 | 2128225.6963 | 0.12517 | 0 | 41431 | Academic/Administration | 1954 | 62 | 2009 | 1954 | C | M | Yes | Yes |  | 4
RO | Rose-Ryan/Student Act. Cntr. | 300 E. Broomfield St. | 441051 | 292.6859 | 129089430.3703 | 3636677.5835 | 0.028172 | 0 | 260417 | Academic/Administration | 1973 | 43 | 1990, 2010 | 1973 | E | NC70% FR30% | Yes | Yes |  | 3
RW | Rowe Hall | 600 E. Bellows St. | 47427 | 264.5231 | 12545535.3314 | 3802007.2526 | 0.30306 | 0 | 23515 | Academic/Administration | 1958 | 58 | 1993 | 1958 | C | M | Yes | Yes |  | 3
S1 | Salt Storage Facility | On Campus- Lot 1 | 1625.3993 | 81.786 | 132934.9857 | 0 | 0 | 0 | 1549.9826 | Miscellaneous | 1986 | 30 |  | 1986 |  | F |  |  |  | 1
SF | Satellite Energy Facility | 350 W. Preston St. | 16800 | 1498.8103 | 25180013.1512 | 12655.0665 | 0.00050258 | 0 | 1346 | PowerPlant | 2006 | 10 |  | 2006 |  | M |  |  |  | 2
SL | Sloan Hall | 1101 S. Franklin St. | 48133.7803 | 281.6825 | 13558442.3977 | 1685710.0665 | 0.12433 | 0 | 26157 | Academic/Administration | 1941 | 75 | 1960, 1969 | 1941 | C | M |  | Yes |  | 4
SM | Smith Hall | 1100 S. Franklin St. | 20477.9316 | 259.89 | 5322010.0978 | 1676508.3531 | 0.31501 | 0 | 8858 | Academic/Administration | 1934 | 82 | 1980 | 1934 | C | M | Yes | Yes |  | 3
SO | Special Olympics Center | 1120 S. Mission St. | 14424 | 239.9637 | 3461235.7566 | 121615.1889 | 0.035136 | 0 | 8065 | Academic/Administration | 1939 | 77 | 1989 | 1939 | C | M | Yes | Yes |  | 1
TS | Theunissen Stadium | 2320 West Campus Dr. | 25627 | 49.9017 | 1278831.2647 | 314197.4597 | 0.24569 | 0 | 13145 | Athletic Fields/Stadiums | 2002 | 14 |  | 2002 | J | M | Yes | Yes |  | 2
UA | University Art Gallery | 251 E. Preston St. | 5264 | 233.3037 | 1228110.4553 | 393811.1157 | 0.32066 | 0 | 3194 | Academic/Administration | 1960 | 56 | 1989 | 1960 | C | M | Yes | Yes |  | 1
VS | Margo Jonker Varsity Softball Stadium | 100 E. Broomfield St. | 6397.8834 | 162.3817 | 1038898.9426 | 52834.9026 | 0.050857 | 0 | 2338 | Athletic Fields/Stadiums | 1997 | 19 | 1997 | 1997 | E | F |  | No |  | 2
VS2,3 | VS - Field Dugouts |  | 804.2089 | 0 | 0 | 0 |  | 0 | 671.1689 | Athletic Fields/Stadiums | 2006 | 10 |  | 2006 |  | F |  |  |  | 1
WA | Warriner Hall | 1200 S. Franklin | 101749.8121 | 362.3853 | 36872639.8554 | 5256898.7998 | 0.14257 | 0 | 67163 | Academic/Administration | 1928 | 88 | 1956 | 1928 | C | M | Yes | Yes |  | 4
WE | West Hall | 305 W. Hopkins Ct. | 9168 | 248.8115 | 2281103.6183 | 909046.3075 | 0.39851 | 0 | 5610 | Academic/Administration | 1942 | 74 | 1948, 1957, 1962, 1985 | 1942 | C | M | Yes | No |  | 2
WI | Wightman Hall | 1150 S. Washington St. | 73324.9232 | 244.5216 | 17929529.2745 | 3494114.8634 | 0.19488 | 0 | 43632 | Academic/Administration | 1948 | 68 | 1955, 1990 | 1948 | C | M | Yes | Yes |  | 3
|  |  | 3742028.3113 |  | 1100440012.5286 | 82868856.668 | 0.075305
SELF LIQUIDATING FACILITY
BldgCode | BuildingName | Address | GSF | CostGSFEsc | ReplacementValueExclContents | DMCostEST | FCI | CostGSFEsc | AssignableSqFt | Functionality | DateBuilt | AgeOfBldg | DateRemodel | Renovation year (age) | DMBBldgType | MUSICCode | AlarmDevices | Standpipes | SpecialExtinguishSystems | NoOfStories
BN | Barnes Hall | 1301 S. Washington St. | 52464 | 258.0561 | 13538655.7554 | 2876132.0822 | 0.21244 | 0 | 35747 | Residence Halls/Apartment Complexes | 1951 | 65 | 1956 | 1951 | E | M |  |  |  | 4
BF | Barnes Kitchen | 1301 S. Washington St. | 10294.2833 | 305.5662 | 3145585.3642 | 1230757.7237 | 0.39127 | 0 | 7073 | Dining Commons | 1939 | 77 | 1960 | 1939 | E | M |  |  |  | 2
BE | Beddow Hall | 100 W. Broomfield St. | 65688.3482 | 261.0709 | 17149314.8703 | 2216549.9097 | 0.12925 | 0 | 41486 | Residence Halls/Apartment Complexes | 1962 | 54 |  | 1962 | E | M |  |  |  | 3
CL | Calkins Hall | 300 W. Hopkins Ct. | 68217.7924 | 256.9086 | 17525735.7885 | 5501759.8045 | 0.31392 | 0 | 43805 | Residence Halls/Apartment Complexes | 1958 | 58 |  | 1958 | E | M | Yes | Yes |  | 4
CP | Campbell Hall | 212 W. Broomfield St. | 87468 | 154.2953 | 11919264 | 1269362.1541 | 0.1065 | 0 | 52391 | Residence Halls/Apartment Complexes | 2003 | 13 |  | 2003 | C/E | M |  |  |  | 5
CF | Carey Dining Commons | 1901 West Campus Dr. | 72807 | 434.5943 | 31641506.2899 | 2846061.1776 | 0.089947 | 0 | 51650 | Dining Commons | 1969 | 47 |  | 1969 | E | M |  |  |  | 2
CA | Carey Hall | 202 W. Broomfield St. | 66474.1351 | 264.3407 | 17571822.3769 | 4878190.0903 | 0.27761 | 0 | 43921 | Residence Halls/Apartment Complexes | 1969 | 47 |  | 1969 | [5 empty] | 9
CE | Celani Hall *** | 303 E. Broomfield St. | 79899.4722 | 154.2953 | 12328112.1897 | 195900.4292 | 0.015891 | 0 | 50438 | Residence Halls/Apartment Complexes | 2006 | 10 |  | 2006 | E | M |  |  |  | 5
CO | Cobb Hall | 204 W. Broomfield St. | 71117 | 264.3407 | 18799120.7422 | 2607605.0844 | 0.13871 | 0 | 45285 | Residence Halls/Apartment Complexes | 1970 | 46 |  | 1970 | E | M |  |  |  | 9
EM | Emmons Hall | 500 E. Ojibway Ct. | 65028 | 256.9086 | 16706250.7706 | 3830656.9879 | 0.22929 | 0 | 44794 | Residence Halls/Apartment Complexes | 1964 | 52 |  | 1964 | [5 empty] | 4
FB | Fabiano Hall *** | 300 E. Ojibway Ct. | 79899.4722 | 154.2953 | 12328112.1897 | 197165.9359 | 0.015993 | 0 | 47582 | Residence Halls/Apartment Complexes | 2006 | 10 |  | 2006 | E | M |  |  |  | 5
GA | Graduate Housing East | 510 E. Bellows | 51675 | 238.6767 | 12333618.4141 |  |  | 0 | 36173 | Residence Halls/Apartment Complexes | 2013 | 3 |  | 2013
GA | Graduate Housing West | 410 E. Bellows | 58520 | 238.237 | 13941628.5923 |  |  | 0 | 40966 | Residence Halls/Apartment Complexes | 2013 | 3 |  | 2013
HE | Herrig Hall | 403 E. Broomfield St. | 65085 | 256.9086 | 16720894.5594 | 5749016.3703 | 0.34382 | 0 | 44742 | Residence Halls/Apartment Complexes | 1966 | 50 |  | 1966 | E | M | Yes | Yes |  | 4
KS | Kesseler Hall | 208 W. Broomfield St. | 80089 | 154.2953 | 10913728 | 1180776.6887 | 0.10819 | 0 | 48388 | Residence Halls/Apartment Complexes | 2003 | 13 |  | 2003 | E | F | No | No |  | 5
| Kewadin Village Apt. Pole Barn | 301 W. Broomfield | 2500 | 91.6313 | 229078.1527 |  |  | 0 | 2206 | Miscellaneous | 2013 | 3 |  | 2013
KE | Kewadin Village Apts. Total |  | 73988 | 189.0967 | 12997411 | 1786399.6954 | 0.13744 | 0 | 61716 | Residence Halls/Apartment Complexes | 1972 | 44 |  | 1972 | E | F | No | No |  | 2
| KE - Building 1 | 301 W. Broomfield | 7306.4243 | 0 |  |  |  | 0
| KE - Building 2 | 301 W. Broomfield | 7344.619 | 0 |  |  |  | 0
| KE - Building 3 | 301 W. Broomfield | 7165.8892 | 0 |  |  |  | 0
| KE - Building 4 | 301 W. Broomfield | 7285.4093 | 0 |  |  |  | 0 |  |  |  |  | 2014
| KE - Building 5 | 301 W. Broomfield | 8872.8436 | 0 |  |  |  | 0 |  |  |  |  | 2014
| KE - Building 6 | 301 W. Broomfield | 7181.1069 | 0 |  |  |  | 0
| KE - Building 7 | 301 W. Broomfield | 7141.4867 | 0 |  |  |  | 0
| KE - Building 8 | 301 W. Broomfield | 7167.4807 | 0 |  |  |  | 0
| KE - Building 9 | 301 W. Broomfield | 7348.9448 | 0 |  |  |  | 0
| KE - Building 10 | 301 W. Broomfield | 7174.6964 | 0 |  |  |  | 0
KU | Kulhavi Hall | 210 W. Broomfield St. | 82904 | 154.2953 | 11297328 | 240446.2633 | 0.021283 | 0 | 50973 | Residence Halls/Apartment Complexes | 2003 | 13 |  | 2003 | E | M | Yes | Yes |  | 5
LA | Larzelere Hall | 203 W. Bellows St. | 80068 | 256.9086 | 20570155.7284 | 6014222.7838 | 0.29238 | 0 | 50939 | Residence Halls/Apartment Complexes | 1957 | 59 | 1972 | 1957 | E | M |  |  |  | 4
MF | Merrill Dining Commons | 150 W. Ojibway Ct. | 61009 | 438.7504 | 26767723.1536 | 1952679.4401 | 0.072949 | 0 | 41891 | Dining Commons | 1960 | 56 | 2001 | 1960 | C/E | M |  |  |  | 2
ME | Merrill Hall | 101 W. Ojibway Ct. | 69755.7398 | 261.0709 | 18211192.3746 | 1655654.3259 | 0.090914 | 0 | 44274 | Residence Halls/Apartment Complexes | 1960 | 56 |  | 1960 | E | M |  |  |  | 4
NW | Northwest Apartments |  | 142511 | 184.7318 | 24547593 | 3214258.1921 | 0.13094 | 0 | 122213 | Residence Halls/Apartment Complexes | 1967 | 49 | 1968 | 1967 | E | M | No | Yes |  | 2
| NW - Building 100 | 300 W. Bellows | 5961.3925 | 0 |  |  |  | 0
| NW - Building 200 | 300 W. Bellows | 11885.9852 | 0 |  |  |  | 0
| NW - Building 300 | 300 W. Bellows | 14443.6466 | 0 |  |  |  | 0
| NW - Building 400 | 300 W. Bellows | 12011.5286 | 0 |  |  |  | 0
| NW - Building 500 | 300 W. Bellows | 14336.5738 | 0 |  |  |  | 0
| NW - Building 600 | 300 W. Bellows | 6043.4403 | 0 |  |  |  | 0
| NW - Building 700 | 300 W. Bellows | 11921.2527 | 0 |  |  |  | 0
| NW - Building 800 | 300 W. Bellows | 8928.3094 | 0 |  |  |  | 0
| NW - Building 900 | 300 W. Bellows | 11984.8769 | 0 |  |  |  | 0
| NW - Building 1000 | 300 W. Bellows | 5982.4221 | 0 |  |  |  | 0
| NW - Building 1100 | 300 W. Bellows | 9037.7874 | 0 |  |  |  | 0
| NW - Building 1200 | 300 W. Bellows | 5995.2691 | 0 |  |  |  | 0
| NW - Building 1300 | 300 W. Bellows | 12027.6865 | 0 |  |  |  | 0
| NW - Building 1400 | 300 W. Bellows | 8928.9158 | 0 |  |  |  | 0
| NW - Building 1500 | 300 W. Bellows | 1481.0239 | 0 |  |  |  | 0
| NW - Building 1600 | 300 W. Bellows | 1541.3202 | 0 |  |  |  | 0
RF | Robinson Dining Commons | 251 W. Bellows St. | 67791 | 434.5943 | 29461581.3438 | 2974765.2629 | 0.10097 | 0 | 50362 | Dining Commons | 1954 | 62 |  | 1954 | E | M | Yes | Yes |  | 4
RB | Robinson Hall | 1200 S. Washington St. | 68351.399 | 256.9086 | 17560060.4696 | 4608061.8415 | 0.26242 | 0 | 41985 | Residence Halls/Apartment Complexes | 1954 | 62 |  | 1954 | E | M | Yes | Yes |  | 4
SA | Saxe Hall | 401 E. Broomfield St. | 65883.7778 | 256.9086 | 16926107.4149 | 5288485.0736 | 0.31245 | 0 | 46655 | Residence Halls/Apartment Complexes | 1966 | 50 |  | 1966 | C/E | M | Yes | No |  | 1
| South Quad Success Center Addition |  | 2271.9105 | 141.0825 | 320526.9087 | 0 |  | 0 |  | Residence Halls/Apartment Complexes | 2004 | 12 |  | 2004 | E | M | Yes | Yes |  | 5
SW | Sweeney Hall | 100 E. Ojibway Ct | 74557.0317 | 261.0709 | 19464669.8761 | 2124110.0542 | 0.10913 | 0 | 44793 | Residence Halls/Apartment Complexes | 1960 | 56 |  | 1960 | E | M | Yes | Yes |  | 5
TH | Thorpe Hall | 101 E Broomfield St. | 74842.2667 | 261.0709 | 19539136.4286 | 2703979.5716 | 0.13839 | 0 | 44488 | Residence Halls/Apartment Complexes | 1962 | 54 |  | 1962 | E | M | Yes | Yes |  | 4
TR | Trout Hall | 301 W. Bellows St. | 65861 | 256.9086 | 16920255.613 | 3968455.004 | 0.23454 | 0 | 41580 | Residence Halls/Apartment Complexes | 1959 | 57 |  | 1959 | E | M | Yes | Yes |  | 9
TM | Troutman Hall | 206 W. Broomfield St. | 104192 | 264.3407 | 27542190.8738 | 4826005.5723 | 0.17522 | 0 | 40824 | Residence Halls/Apartment Complexes | 1969 | 47 | 1962, 1966 | 1969 | E | M |  | No |  | 2
WC | Washington Court Apts. |  | 0 |  |  | 0 | - | 0 |  | Residence Halls/Apartment Complexes | 1957 |  |  | 1957 | [5 empty] | 2
WH | Wheeler Hall | 200 W. Broomfield St. | 71117 | 264.3407 | 18799120.7422 | 1177677.2699 | 0.062645 | 0 | 46617 | Residence Halls/Apartment Complexes | 1970 | 46 |  | 1970 | E | M | Yes | Yes |  | 9
WF | Woldt Dining Commons | 1900 East Campus Dr. | 105256.6386 | 427.6769 | 45015832.8441 | 22779.1197 | 0.00050602 | 0 | 65524 | Dining Commons | 1964 | 52 | 1968, 2006 | 2006 | C/E | M | Yes | Yes | Halon/FM200/ETC | 2
WO | Woldt Hall | 400 E. Ojibway Ct. | 65222 | 256.9086 | 16756091.0341 | 1701442.3303 | 0.10154 | 0 | 43882 | Residence Halls/Apartment Complexes | 1964 | 52 |  | 1964 | E | M | Yes | Yes |  | 4
|  |  |  | subtotal | 569489404.8613 | 78839356.2388 | 0.13844
|  |  | 2252808.2675 | Total | 1669929417.3899 | 161708212.9067 | 0.096835
Note: Bold font indicates a 2013 update.
GENERAL INSTITUTION FACILITY - OFF CAMPUS
BP | Barstow Property | 3321 W. Chippewa River | 2733.05 | 64.48 | 176227.064 |  |  |  | 2688.05 | Miscellaneous | 1982 | 34 |  |  | Off Campus | F |  |  |  | 2
| Art Studio |  | 1150 | 217.39 | 250000
BI | Beaver Island Boathouse/Mesocosm | 37707 Michigan Ave. | 5255.95 | 248 | 1303475.6 |  |  |  | 5139.7 | Biological Research Station(Beaver Island) | 1938 | 78 | 2012 | [6 empty] | 1.5
BI | Beaver Island Campground Fac |  | 4530 | 52.27 | 236783.1 |  |  |  |  | Biological Research Station(Beaver Island) | 1972 | 44 | 1990 |  | Off Campus | F |  |  |  | 1
BI | Beaver Island Director's House |  | 2520 | 80.59 | 203086.8 |  |  |  |  | Biological Research Station(Beaver Island) | 1990 | 26 |  |  | Off Campus | F
BI | Beaver Island Duplex (Apts) |  | 6768 | 50.35 | 340768.8 |  |  |  |  | Biological Research Station(Beaver Island) | 1979 | 37 | 1990 |  | Off Campus | F
BI | Beaver Island Main Bldg. | 33850 E. Side Dr. | 8051 | 122.57 | 986811.07 |  |  |  |  | Biological Research Station(Beaver Island) | 1959 | 57 | 1979, 1995 |  | Off Campus | M |  | No
BI | Old Research Building |  | 2133 | 149.97 | 319886.01 |  |  |  |  | Biological Research Station(Beaver Island) |  |  |  |  | Off Campus
BI | New Research Building |  | 2793 | 149.97 | 418866.21 |  |  |  |  | Biological Research Station(Beaver Island) | 2003 | 13 |  |  | Off Campus
BI | Beaver Island Pole Barn |  | 1975 | 41.95 | 82851.25 |  |  |  |  | Biological Research Station(Beaver Island) | 1984 | 32 |  |  | Off Campus | F |  | No |  | 1
BI | Beaver Island Garage |  | 2276 | 41.95 | 95478.2 |  |  |  |  | Biological Research Station(Beaver Island) |  |  |  |  | Off Campus
BI | Beaver Island Academic Center * |  | 13429.6818 | 205.03 | 2753487.6595 |  |  |  | 10154.4 | Biological Research Station(Beaver Island) | 2006 | 10 |  |  | Off Campus
BI | BI - CMUBS Guest House (formerly Hindes House) |  | 2592 | 80.59 | 208889.28 |  |  |  |  | Biological Research Station(Beaver Island) |  |  |  |  | Off Campus
FH | Forest Lane House (President's Residence) | 1214 Forest Lane | 6208 | 135.37 | 840376.96 |  |  |  |  | Miscellaneous | 1980 | 36 |  |  | E | F |  |  |  | 2
NL | McNeel Nature Ctr. Lodge(Neithercut)-Clare County | 4105 West Cadillac | 2114.36 | 52.27 | 110517.5972 |  |  |  |  | Miscellaneous | 1973 | 43 |  |  | Off Campus | F |  |  |  | 1
NL | McNeel Nature Ctr.(Neithercut) Sheds (Two) | 4105 West Cadillac | 398.125 | 41.95 | 16701.3438 |  |  |  |  | Miscellaneous |  |  |  |  | Off Campus |  |  |  |  | 1
| East Campus - Saginaw Site | Covenant Education Building - 1632 Stone Street | 51971 | 330.95 | 17199802.45 |  |  |  | 1 | Academic/Administration | 2015 | 1 |  |  | Off Campus
|  | Total Off-Campus GSF | 116898.1668
S2 | PBS Bldgs/Towers Owned by CMU
| Atlanta, MI #1 - WPHN-FM |  | 1487 | [6 empty] | Public Broadcasting | 1975
| Atlanta, MI #2 - WCML TV & FM | [8 empty] | Public Broadcasting | 2003
| Barryton, MI - WCMU-TV |  | 800 | [6 empty] | Public Broadcasting | 2002
| Cadillac, TV 27 |  | 600 | [7 empty] | 2001
| Goodrich, MI - WCMZ-TV |  | 1531 | [6 empty] | Public Broadcasting | 1979
| Lewiston, MI - Elk Hill | [8 empty] | Public Broadcasting | 1975
| Lincoln, MI - WCMB-FM | [8 empty] | Public Broadcasting | 1997
| Mt. Pleasant, MI #1 - South Campus | [8 empty] | Public Broadcasting
| Mt. Pleasant, MI #2 - South Campus | [8 empty] | Public Broadcasting | 1996
| Mt. Pleasant, MI #3 - PBC Monopole |  | 84 | 123.23 | [5 empty] | Public Broadcasting | 2008
| Mt. Pleasant, MI #4 - Chippewa River |  | 64 | [6 empty] | Public Broadcasting | 1980
| Saint Helen, MI - Indian Springs | 6137 N. Quarterline Rd. | 384 | 21.57 | 8282.88 |  |  |  |  | Public Broadcasting | 1975 | 41 |  |  | Off Campus | F
| Sault Saint Marie, MI - WCMZ-FM Sugar Island |  | 384 | 99.72 | 38292.48 |  |  |  | 529 | Public Broadcasting | 1966 | 50 | 1972, 1979 |  | F | F
| Freesoil, MI - WCMW-TV/Manistee | [8 empty] | Public Broadcasting
| Sterling, MI - WWCM-FM |  | 288 | [6 empty] | Public Broadcasting | 1989
| Manistee,TV 21 Building 1 (PBS) |  | 384 | 21.57 | 8282.88
| Manistee,TV 21 Building 2 (PBS) |  | 288 | 21.57 | 6212.16 | [5 empty] | 2009
| Manistee,TV 21 Building 3 (PBS) | 600 N. Hubbard Lake |  |  | 0 |  |  |  |  | Public Broadcasting Sites(off-campus) | 1998 | 18 |  |  | Off Campus
| Oscoda WCMB 95.7 (PBS) |  | 576 | 46.58 | 26830.08 |  |  |  | 462.6667 | Miscellaneous | 1987 | 29 |  |  | H | F |  | No |  | 1
| PBS Generator Building |  | 524
| Bay City, WUCX 90.1-FM (PBS) |  | 288 | [16 empty] | 1
| T.V. Antenna & Equip. Bldg. (PBS) | 8513 E. Traverse Hwy. | 576 | 190.92 | 109969.92 |  |  |  |  | Public Broadcasting Sites(off-campus) | 1981 | 35 | 1981 |  | Off Campus | F |  |  |  | 1
| Traverse City, Ch 46 (PBS) |  | 96 | 16.53 | 1586.88 |  |  |  | 2272.08 | Miscellaneous | 1994 | 22 |  |  | H | F
|  | Total CMU/PBS GSF | 8354
PBS Bldgs/Towers Leased by CMU
| Baldwin, MI | 7584 US23 North | 180 | Leased | [5 empty] | Public Broadcasting Sites(off-campus)
| Cheboygan, MI |  |  | Leased | [5 empty] | Public Broadcasting Sites(off-campus)
| University Center, MI | Traynor Rd. |  | Leased | [5 empty] | Public Broadcasting Sites(off-campus)
| Goetzville, MI | 3399 Wressell Rd. |  | Leased | [5 empty] | Public Broadcasting Sites(off-campus)
| Harbor Springs, MI FM 103.9 |  |  | Leased | [5 empty] | Public Broadcasting Sites(off-campus)
| Harrison, MI |  | 80 | Leased | [5 empty] | Public Broadcasting Sites(off-campus)
| Kalkaska, MI |  | 800 | Leased | [5 empty] | Public Broadcasting Sites(off-campus)
| Guilford Twp., MI |  |  | Leased | [5 empty] | Public Broadcasting Sites(off-campus)
BUILDINGS UNDER CONSTRUCTION
| Biosciences Bldg. | 1455 Calumet Ct. | 168970
| Grawn Renovation |  | 6360 | New GSF
LAND DATA
Main Campus
| Improved (Landscaped and maintained by CMU) | 564 acres
| Total Main Campus | 871 acres (more or less)
Beaver Island
| Biological Station | 130 acres (more or less)
| Egbert Property (adjacent to Biological Station) | 80 acres (more or less)
| Miller's Marsh | 230 acres (more or less)
| New Property (next to Miller's Marsh) | 40 acres (more or less)
| Hindes House | 4.01 acres
| Boathouse | 0.2 acres (more or less)
| Viets Woods | 45.79 acres
| Barstow Property | 3.9 acres (more or less)
| President's Residence -1214 Forest Lane | 0.47 acres
| Neithercut | 252 acres (more or less)
| Sterling | 5 acres (improved)
| Barryton | 40 acres (unimproved)
| Barryton | 2 acres (improved)
| SW corner Broomfield & Crawford (McGuirk Donation) | 54.36 acres (unimproved)
Note on D2: haas1d: CAD file ~ 119178.5713 2013 Added Student Lounge
Note on J2: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D3: Restroom Addition Summer of 2005 - 174 Additional Sq. Ft (Peter Gorton)
Note on J3: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on B4: Construction Summer of 2012
Note on D5: haas1d: CAD file ~ 142374.7637 SF
Note on J5: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J6: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J7: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on Q7: F=Frame
Note on B8: Wet Lab Addition 2006
Note on J8: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D9: haas1d: Measured from CAD file
Note on J9: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on P9: P=Energy Conversion Plants-200 Million BTU/Hour and Under Oil and Gas Plants-Heating and Cooling
Note on J10: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J11: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J12: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J14: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on Q14: FR=Fire Resistive
Note on J15: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J16: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D17: haas1d: CAD file ~ 102493.2726 using first floor measured footprint
Note on J17: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on P17: C=Office/Administration, laboratories, chapels, museums, auditoriums, food service , laundries, and all university and college facilites (except those described by Types E,F,G,H and I below)
Note on Q17: M=Masonry
Note on J18: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on C19: Methner, Daniel Joseph: Demo Aug. 2014 as part of Olympic Drive Connector project
Note on D19: Methner, Daniel Joseph: Building Demo as part of Olympic Drive Connector Street.
Note on P19: H=Unheated warehouses, sheds, garages, barns
Note on J20: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D21: Methner, Daniel Joseph: Added 1256 GSF - Pole Barn Addition PBS/Biology Storage Bldg.
Note on J21: Strandskov, Matthew Jon: Per 2013 Master Plan Add 1223 SF for 2014 pole barn addition
Note on D22: methn1dj: Added 60,500 GSF for the HP Addition 11.16.11
Note on E22: methn1dj: corrected 2-4-14. original did not include soft cost.
Note on J22: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R22: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on J24: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D25: haas1d: Tunnel to ST GSF~2276.667 measured from scans pending verification
Note on J25: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D27: haas1d: Bleachers = 101508.3 SF
Note on J27: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on P27: K=Outdoor Stadiums-Seating Capacity 20,000 or more
Note on D29: haas1d: Measured from CAD file
Note on J29: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J30: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D33: haas1d: Bennet track Grandstand; includes uncovererd bleachers and pressbox and consessions building on north side of track. Consessions ~ 131.267 Field Hockey bleachers and dugout/shelters767.5
Note on E34: Cost per Sq. Ft. data received from Chad Stirrett, EHS Project Manager
Note on J34: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on L34: substatinal completion Feb. 2009
Note on O34: substatinal completion Feb. 2009
Note on R34: Alarms are central station and monitored
Note on J35: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on Q35: NC=Noncombustible
Note on D36: haas1d: penthouse ~ 15810.6294 SF
Note on J36: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J37: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R37: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on J38: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R38: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on J39: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R39: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on B40: Facilities Management: Substantial Completion May 1, 2013
Note on J40: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J42: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R42: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on D43: haas1d: Measured from CAD file 11.17.11 added Event Center GSF to Total (47,569 GSF).
Note on J43: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R43: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on J44: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R44: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on C46: north end of PL 1 6 - south of West Hall
Note on J46: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J47: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R47: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on J48: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R48: Water Flow/Fire Pump/Smoke Detection/Pull Station
Note on J49: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R49: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on D50: haas1d: Includes Bleachers~ 2593.74 SF; gross sq footage taken from BD
Note on J50: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R50: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on J51: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R51: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on D52: haas1d: bleachers added; bleacher sf = 1621.5 overhang on east side = 1228.5561
Note on J52: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J54: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R54: Water Flow/Fire Pump/Smoke Detection/Pull Station
Note on J55: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R55: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on J56: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R56: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on J62: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J63: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on E64: Methner, Daniel Joseph: 12-10-14 add $4.05 (to $249.91) for 2013 South Quad Improvements for Fire Protection
Note on J64: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D65: haas1d: Measured from CAD file
Note on J65: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R65: water Flow/Fire Pump/Smoke Detection/Pull Stations.
Note on D66: haas1d: Measured from CAD file
Note on J66: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J67: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D68: haas1d: Measured from CAD file
Note on J68: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J69: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D70: haas1d: Measured from CAD file
Note on J70: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D71: Field Verified June 2007 Original sf was 64,810
Note on J71: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J72: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J73: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J74: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D75: Field Verified June 2007 Original sf was 64,864
Note on J75: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R75: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on D76: haas1d: Measured From CAD file
Note on J76: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J78: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D82: Methner, Daniel Joseph: 10-31-14 Added 137 GSF for ADA upgrade to Room 408
Note on D83: Methner, Daniel Joseph: 10-31-14 Added 137 GSF for ADA upgrade to Room 508
Note on D89: haas1d: Measured from CAD file
Note on J89: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R89: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on D90: haas1d: Measured from CAD file
Note on J90: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D91: haas1d: Measured from CAD file
Note on E91: Methner, Daniel Joseph: 12-10-14 add $4.05 (to $422.75) for 2013 SouthQuadImprovements Fire Protection
Note on J91: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on D92: haas1d: Measured From CAD file
Note on E92: Methner, Daniel Joseph: 12-10-14 add $4.05 (to $249.91) for 2013SouthQuadImprovement Fire Protection
Note on J92: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J93: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on J110: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R110: Water Flow/Fire Pump/Smoke Detection/Pull Station
Note on D111: haas1d: Measured From CAD file
Note on J111: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R111: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on J112: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on B113: Addition to Merrill Hall-2004
Note on R113: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on E114: Methner, Daniel Joseph: 12-10-14 add $4.05 (to $249.91) for 2013SouthQuadImprovement Fire Protection
Note on J114: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R114: Water Flow/Fire Pump/Smoke Detection/Pull Station
Note on E115: Methner, Daniel Joseph: 12-10-14 add $4.05 (to $249.91) for 2013SouthQuadImprovement Fire Protection
Note on J115: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R115: Water Flow/Fire Pump/Smoke Detection/Pull Station
Note on D116: haas1d: Measured from CAD file
Note on J116: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R116: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on D117: haas1d: Measured from CAD file
Note on J117: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on B118: Remaining Apts. Scheduled for demolition as part of Bioscience Project
Note on C118: Methner, Daniel Joseph: Building Demo June 2014
Note on D119: haas1d: Measured from CAD file
Note on J119: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R119: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on J120: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R120: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on D121: Field Verified June 2007 - Original sf was 65,189
Note on J121: Strandskov, Matthew Jon: Per 2013 Master Plan
Note on R121: Water Flow/Fire Pump/Smoke Detection/Pull Stations
Note on B132: Boathouse acquired Summer 2006 Mesocosm Built 2013
Note on C132: Charlevoix County
Note on L132: Purchased in 2005
Note on B134: methn1dj: Includes particle walk-out basement
Note on B135: methn1dj: Includes the 3 staff houses (Staff 1&2, Staff 3&4, and Staff 4&5) and the Cooks Cabin
Note on B136: methn1dj: Dining and Dormitory includes lean-to
Note on B139: methn1dj: Includes walk-in freezer
Note on B141: Construction to start Summer 2006
Note on D141: haas1d: East Boardwalk area is 1250.2818; Gross doesn’t include west sidewalk under roof overhang
Note on E141: Based on Use & Finance Statement Cost per sq. ft.
Note on B142: methn1dj: 34013 East Side Drie Beaver Island, MI 49782
Note on D143: haas1d: basement is included 2806SF; porch and decks not included; Main level is 3402SF
Note on B145: trevi1cm: 2 Sheds 12' 3"x 16
Note on D153: methn1dj: PBS reporting
Note on D155: methn1dj: PBS purchased May 18, 2010. Added 11.20.12.
Note on D162: methn1dj: 16x24
Note on P163: F=Heated quonsets, warehouses, sheds, garages, barns
Note on D165: methn1dj: PBS reporting
Note on D166: methn1dj: 12x24
Note on D167: methn1dj: 1x2
Note on D172: methn1dj: 8x12

## Escalation Factor
Escalation Factor
Record Escalation Factor for prior year(s):
2013 | 1.0238
2014 | 1.019
2015 | 1.028
2016 | tbd
2017 | tbd
2018 | tbd
2019 | tbd
2020 | tbd
2021 | tbd
2022 | tbd
2023 | tbd

## FCA Bldg Detail
BLDG NAME | BLDG CODE | CATEGORY | ID No. | System 1 |  | Description/ Location | Condition Rating | Quantity | Units | Construction Cost (18% GC/CA) | Project Cost (33% Owner soft costs) | Construction Cost Esc (2.80%) | Project Cost Escalation (2.80%) | Estimated Install Date | Est Useful Life | Est Replace Date | A/E Comments | Estimator Comments/Qualifications | GF or SF | ION | Date Complete | Actual Cost | Notes
INDOOR ATHLETIC COMPLEX | AC | ARCH | 1001 | Envelope | Exterior Doors |  | 3 | 6 | ea | 38868.7712 | 51695.4657 | 0 | 0 | 1998 | 30 | 2028 | Doors in west side of track facility are difficult to close and should be replaced, 3 pair of double doors | Price is for removing old doors and replacing them with new aluminum framed entry doors | GF
INDOOR ATHLETIC COMPLEX | AC | ARCH | 1002 | Interior Structure | Floor Finishes | Weight room | 3 | 1760 | sf | 40091.2506 | 53321.3633 | 0 | 0 | 1998 | 15 | 2013 | Weight room floor and turf surfaces should be replaced in 3 to 5 years. | Price is for removing existing rubber flooring and replacing with new. | GF
INDOOR ATHLETIC COMPLEX | AC | ARCH | 1003 | Interior Structure | Casework | Training room | 4 | 32 | lf | 20248.1064 | 26929.9815 | 0 | 0 | 1998 | 20 | 2018 | Casework is damaged and wood surfaces exposed & in need of replacement, Approx 32 linear ft of upper and lower cabinets | Price is for removing old cabinets and replacing with plastic laminate upper and lower cabinets | GF
INDOOR ATHLETIC COMPLEX | AC | ARCH | 1004 | Interior Structure | Curtains Netting | Field turf area | 1 | 1 | lot | 0 | 0 | 0 | 0 | 1998 | 20 | 2018 | Curtains, netting and cables are showing signs of wear and need to be replaced | price is for replacing netting and wiring at batting cages, area divider curtains and window curtain. Price assumes reconnecting to existing support structures and reusing existing motor winches | GF | 684275 | 2014-08-01 | 38882.78
INDOOR ATHLETIC COMPLEX | AC | ARCH | 1005 | Interior Structure | Locker rooms |  | 3 | 1800 | sf | 170843.3976 | 227221.7188 | 0 | 0 | 1998 | 30 | 2028 | Some locker rooms need to be upgraded to match the balance of the facility, Approx 1,800 SF | A budget of $75/sf was used for removing old finishes and replacing with updated finishes | GF
ANSPACH HALL | AN | ARCH | 1006 | Envelope | Windows | Single Pane Alum | 4 | 3611 | sf | 251335.948 | 334276.8108 | 0 | 0 | 1964 | 30 | 1994 | Windows not renovated in 2012 and need to be replaced. |  | GF
ANSPACH HALL | AN | EH&S | 1007 | Environmental Health and Safety | Asbestos abatement | Allowance | 4 | 50000 | sf | 189825.9973 | 252468.5764 | 0 | 0 | 1966 |  | 1966 | flooring |  | GF
ANSPACH HALL | AN | MECH | 1008 | Ventilation/Terminal Units | AHU/CHW Cool/Steam Heat | AHU-5/W. Basement Mech. Rm. | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 30 | 1995 | Scheduled for replacement 2013 |  | GF
ANSPACH HALL | AN | MECH | 1009 | Ventilation/Terminal Units | AHU/CHW Cool/Steam Heat | AHU-6/W. Basement Mech. Rm. | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 30 | 1995 | Scheduled for replacement 2013 |  | GF
ANSPACH HALL | AN | MECH | 1010 | Ventilation/Terminal Units | AHU/CHW Cool/Steam Heat | AHU-7/W. Basement Mech. Rm. | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 30 | 1995 | Scheduled for replacement 2013 |  | GF
ANSPACH HALL | AN | MECH | 1011 | Ventilation/Terminal Units | Terminal Unit | HW Convector/Various | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 25 | 1990 | Scheduled for replacement 2013 |  | GF
ANSPACH HALL | AN | MECH | 1012 | Ventilation/Terminal Units | Terminal Unit | HW Fin Tube/Various | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 25 | 1990 | Scheduled for replacement 2013 |  | GF
ANSPACH HALL | AN | MECH | 1013 | Heating Water System | Pumps | System/W. Mech. Rm. | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 20 | 1985 | Scheduled for replacement 2013 |  | GF
ANSPACH HALL | AN | MECH | 1014 | Heating Water System | Piping | Entire system/W. Wing | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 40 | 2005 | Scheduled for replacement 2013 |  | GF
ANSPACH HALL | AN | MECH | 1015 | Heating Water System | Insulation | Entire system/W. Wing | 3 |  |  | 0 | 0 | 0 | 0 | 1965 |  | 1965 | Scheduled for replacement 2013 |  | GF
ANSPACH HALL | AN | MECH | 1016 | Steam System | PRV Station | System/W. Mech. Rm. | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 50 | 2015 | Scheduled for replacement 2013 |  | GF
ANSPACH HALL | AN | MECH | 1017 | Steam System | Piping | Entire system/W. Wing | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 50 | 2015 | Scheduled for replacement 2013 |  | GF
ANSPACH HALL | AN | MECH | 1018 | Building Management | HVAC Control | Pneumatic | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 25 | 1990 | Scheduled for replacement 2013 |  | GF
ANSPACH HALL | AN | MECH | 1019 | Storm/Sanitary sewer system | Piping | Entire building | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 40 | 2005 | Good condition, no reported problems |  | GF
ANSPACH HALL | AN | MECH | 1020 | Storm/Sanitary sewer system | Sump pumps | W. Mech. Rm. | 3 |  |  | 0 | 0 | 0 | 0 | Unknown | 10 | 10 | Replace as a precautionary measure |  | GF
ANSPACH HALL | AN | MECH | 1021 | Fire protection system | Piping | Basement/W. Mech. Rm. | 3 |  |  | 0 | 0 | 0 | 0 | 1965 | 40 | 2005 | Good condition, no reported problems |  | GF
ANSPACH HALL | AN | EH&S | 1022 | Environmental Health and Safety | Asbestos abatement | allowance for mech items | 3 | 40000 | sf | 202481.0638 | 269299.8148 | 0 | 0 | 1965 |  | 1965 | allowance for partial bldg |  | GF
ANSPACH HALL | AN | ELEC | 1023 | Distribution | Panel BA | Room 181 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 1966 | 40 | 2006 | Needs upgrade | Scheduled for replacement 2013 | GF
ANSPACH HALL | AN | ELEC | 1024 | Lighting | 4 foot wraparounds | Ground floor corridor | 3 |  |  | 0 | 0 | 0 | 0 | unknown | 20 | 20 | Needs upgrade |  | GF
ANSPACH HALL | AN | ELEC | 1025 | Lighting | Day-Brites | Ground floor corridor | 3 |  |  | 0 | 0 | 0 | 0 | unknown | 20 | 20 | Needs upgrade |  | GF
ANSPACH HALL | AN | ELEC | 1026 | Lighting | 2x4 troffers | 1st floor classrooms | 3 |  |  | 0 | 0 | 0 | 0 | unknown | 20 | 20 | Needs upgrade |  | GF
ANSPACH HALL | AN | ELEC | 1027 | Lighting | 2x4 troffers | 2nd floor classrooms | 3 |  |  | 0 | 0 | 0 | 0 | unknown | 20 | 20 | Needs upgrade |  | GF
ANSPACH HALL | AN | ELEC | 1028 | Lighting | 4 foot wraparounds | 2nd floor corridor | 3 |  |  | 0 | 0 | 0 | 0 | unknown | 20 | 20 | Needs upgrade |  | GF
ANSPACH HALL | AN | ELEC | 1029 | Lighting controls | occupancy sensors | 1st floor corridors | 4 |  |  | 0 | 0 | 0 | 0 | unknown | 10 | 10 | None |  | GF
ANSPACH HALL | AN | ELEC | 1030 | Lighting controls | occupancy sensors | 2nd floor corridor | 4 |  |  | 0 | 0 | 0 | 0 | unknown | 10 | 10 | None |  | GF
ANSPACH HALL | AN | LSAF | 1031 | Life Safety | Security | Some Areas | 3 |  |  | 0 | 0 | 0 | 0 | unknown | 10 | 10 | Good Condition |  | GF
CARLIN ALUMNI HOUSE | BH | ARCH | 1032 | Envelope | Foundation/Slab | Concrete residential | 3 | 380 | sf | 31258.0142 | 41573.1589 | 0 | 0 | 1941 | 100 | 2041 | Water leaks at bottom of foundation wall. | Waterproof repair of 25% of perimeter. Quantity is based off of 94 lnft feet of foundation and 4' wide area. Price includes excavating, backfilling area and appling waterproofing to the foundation wall. | GF
CARLIN ALUMNI HOUSE | BH | ARCH | 1033 | Interior Structure | Interior Doors | Wood Door Hardware | 3 | 26 | ea | 13942.0224 | 18542.8898 | 0 | 0 | 1990 | 40 | 2030 | Doors do not have accessible hardware. |  | GF
CARLIN ALUMNI HOUSE | BH | ARCH | 1034 | Interior Structure | Stairs | Carpeted wood | 3 | 80 | lf | 12869.5591 | 17116.5137 | 0 | 0 | 1990 | 15 | 2005 | Staits do not have proper handrails |  | GF
CARLIN ALUMNI HOUSE | BH | MECH | 1035 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | AC-4/W. Exterior | 3 | 5 | Tons | 164515.8643 | 218806.0996 | 0 | 0 | 1990 | 15 | 2005 | Replace nearing end of useful life |  | GF
CARLIN ALUMNI HOUSE | BH | MECH | 1036 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | AC-5/W. Exterior | 3 | 5 | Tons | 164515.8643 | 218806.0996 | 0 | 0 | 1990 | 15 | 2005 | Replace nearing end of useful life |  | GF
CARLIN ALUMNI HOUSE | BH | MECH | 1037 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | AC-6/S. Exterior | 3 | 5 | Tons | 164515.8643 | 218806.0996 | 0 | 0 | 1990 | 15 | 2005 | Replace nearing end of useful life |  | GF
CARLIN ALUMNI HOUSE | BH | MECH | 1038 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | AC-7/S. Exterior | 3 | 5 | Tons | 164515.8643 | 218806.0996 | 0 | 0 | 1990 | 15 | 2005 | Replace nearing end of useful life |  | GF
CARLIN ALUMNI HOUSE | BH | MECH | 1039 | Ventilation/Terminal Units | AHU/DX Cool | American Standard split/W.Exterior | 3 | 1.5 | Tons | 49354.7593 | 65641.8299 | 0 | 0 | 1989 | 15 | 2004 | Replace nearing end of useful life |  | GF
CARLIN ALUMNI HOUSE | BH | MECH | 1040 | Ventilation/Terminal Units | AHU/DX Cool | Coleman split/W. Exterior | 3 | 3 | Tons | 98709.5186 | 131283.6597 | 0 | 0 | 1990 | 15 | 2005 | Replace nearing end of useful life |  | GF
CARLIN ALUMNI HOUSE | BH | MECH | 1041 | Ventilation/Terminal Units | Terminal units/Window AC | West offices | 3 | 3 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 2002 | 10 | 2012 | Replace nearing end of useful life |  | GF
CARLIN ALUMNI HOUSE | BH | MECH | 1042 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 8220 |  | 36408.6263 | 48423.473 | 0 | 0 | 1941 | 40 | 1981 | Replace all drainage piping |  | GF
CARLIN ALUMNI HOUSE | BH | MECH | 1043 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rms. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | 1971 | 10 | 1981 | Replace nearing end of useful life |  | GF
CARLIN ALUMNI HOUSE | BH | ELEC | 1044 | Branch Circuits | Panel LPA | Office | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | OK |  | GF
CARLIN ALUMNI HOUSE | BH | ELEC | 1045 | Lighting | 4 foot troffers with silver parabolic diffusers | Basement | 3 | 28 | ea | 12401.9652 | 16494.6137 | 0 | 0 | Unknown | 20 | 20 | needs upgrade |  | GF
CARLIN ALUMNI HOUSE | BH | LSAF | 1046 | Life Safety | Emergency Lighting | Bld | 3 | 20 | ea | 12655.0665 | 16831.2384 | 0 | 0 | Unknown | 20 | 20 | Wall mounted battery packs | Price is for 20 battery pack wall mounted units | GF
BROOKS HALL | BR | ARCH | 1047 | Envelope | Windows | Building Exterior | 3 | 7050 | sf | 490700.203 | 652631.27 | 0 | 0 | 1964 | 30 | 1994 |  | Price is for removing existing windows and replacing them with new alum framed windows, new caulk and minor finish repair around new windows. | GF
BROOKS HALL | BR | ARCH | 1048 | Envelope | Exterior Doors | Building Exterior | 3 | 20 | ea | 126550.6649 | 168312.3843 | 0 | 0 | 1964 | 30 | 1994 |  | Price is for removing existing exterior entry doors and replacing them with new alum entry doors | GF
BROOKS HALL | BR | ARCH | 1049 | Envelope | Exterior Wall System | Building Exterior | 3 | 1000 | sf | 31637.6662 | 42078.0961 | 0 | 0 | 1964 | 100 | 2064 |  | Brick tuck pointing and repair, 1000 s.f. | GF
BROOKS HALL | BR | ARCH | 1050 | Envelope | Roof/Penetrations | Roof Leak | 5 | 5000 | sf | 171729.2522 | 228399.9055 | 0 | 0 | 2010 | 30 | 2040 | Leak in one area. Refer to roof report for recent installation. |  | GF |  |  |  | Roof Section 3
BROOKS HALL | BR | ARCH | 1051 | Interior Structure | Partitions | gyp bd/cmu | 3 | 300 | sf | 3037.216 | 4039.4972 | 0 | 0 | 1964 | 40 | 2004 |  | Price is for repainting and minor wall repair to about 300 sf of walls | GF
BROOKS HALL | BR | ARCH | 1052 | Floor Finishes | Resilient Flooring | Corridor | 3 | 21050 | sf | 133194.5748 | 177148.7844 | 0 | 0 | 1989 | 20 | 2009 | Corridor tile in good condition | Price is for removing existing floor and replacing it with new VCT flooring | GF
BROOKS HALL | BR | ARCH | 1053 | Floor Finishes | Resilient Flooring | Classrooms | 3 | 500 | sf | 3163.7666 | 4207.8096 | 0 | 0 | 1989 | 20 | 2009 | Replace classroom tile as necessary where worn. | Price is for removing existing floor and replacing it with new VCT flooring | GF
BROOKS HALL | BR | ARCH | 1054 | Ceiling Finishes | Corridors |  | 3 | 21050 | sf | 119875.1173 | 159433.906 | 0 | 0 | 1964 | 20 | 1984 | 2 x 4 ceiling tile with ceiling mounted 1 x 4 lights. | Price is for removing existing ceiling and replacing it with 2x4 ACT ceiling system | GF
BROOKS HALL | BR | ARCH | 1055 | Fixed Equipment/Furnishings | Lab casework | Labs (2-3 rooms) | 4 | allowance |  | 536231.6308 | 713188.069 | 0 | 0 | unknown | 40 | 40 |  |  | GF
BROOKS HALL | BR | ARCH | 1056 | Conveying Systems | Elevators | Cylinder Replacement | 1 | 1 | qty | 0 | 0 | 0 | 0 | unknown | 30 | 30 | Otis Elevator recommendation for 2013. | Refer to May 1, 2013 letter from Otis | GF | 684251 | 2013-08-15 | 34500
BROOKS HALL | BR | ARCH | 1057 | Conveying Systems | Elevators | Modernization | 3 | 1 | qty | 64347.7957 | 85582.5683 | 0 | 0 | unknown |  | 0 | Otis Elevator recommendation for 2022. | Refer to May 1, 2013 letter from Otis | GF
BROOKS HALL | BR | ADAC | 1058 | BF/ADA Compliance | Interior Door Hardware | Interior classroom | 3 | 110 | ea | 69602.8657 | 92571.8114 | 0 | 0 | 1964 | 30 | 1994 | Replace with ADA-accessible door hardware | Price is for replacing existing hardware with new ADA compliant hardware | GF
BROOKS HALL | BR | ADAC | 1059 | BF/ADA Compliance | Toilet Rooms |  | 3 | 1025 | sf | 129714.4315 | 172520.1939 | 0 | 0 | 1964 | 30 | 1994 | Renovate 2nd and 3rd floor toilet rooms for ADA-accessibility. |  | GF
BROOKS HALL | BR | ADAC | 1060 | BF/ADA Compliance | Exterior doors | Power Assist Hardware | 3 | 7 | ea | 53151.2792 | 70691.2014 | 0 | 0 | 1989 | 20 | 2009 | Replace replace power openers. | Price is for replacing 1 automatic opener at each entry (7 total) | GF
BROOKS HALL | BR | EH&S | 1061 | Environmental Health & Safety | asbestos abatement | allowance | 3 | 42600 | sf | 348204.1544 | 463111.5253 | 0 | 0 | 1964 |  | 1964 |  |  | GF
BROOKS HALL | BR | MECH | 1062 | Ventilation/Terminal Units | RTU/DX Cool/No Heat | RTU-2/S. Roof | 3 | 7.5 | Tons | 29100.3254 | 38703.4328 | 0 | 0 | 1993 | 15 | 2008 | Remove no longer used | price is for disconnect and removal of old unit only. | GF
BROOKS HALL | BR | MECH | 1063 | Storm/Sanitary sewer system | Sump pumps | Rm. 008 | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | 2002 | 10 | 2012 | Replace as a precautionary measure | Price is for replacing existing sump pump with a new one. | GF
BROOKS HALL | BR | ELEC | 1064 | Distribution | Panel DLP-B | Tunnel | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1964 | 40 | 2004 | Needs upgrade | Price is for removing old panel and replacing it with a new one and reconnect to the existing feeds | GF
BROOKS HALL | BR | ELEC | 1065 | Distribution | Panel DLP-D | Tunnel | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1964 | 40 | 2004 | Needs upgrade | Price is for removing old panel and replacing it with a new one and reconnect to the existing feeds | GF
BROOKS HALL | BR | ELEC | 1066 | Branch Circuit | Panel LPBC | Tunnel | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1964 | 40 | 2004 | Needs upgrade | Price is for removing old panel and replacing it with a new one and reconnect to the existing feeds | GF
BROOKS HALL | BR | ELEC | 1067 | Branch Circuit | Panel PP-A | Tunnel | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1964 | 40 | 2004 | Needs upgrade | Price is for removing old panel and replacing it with a new one and reconnect to the existing feeds | GF
BROOKS HALL | BR | ELEC | 1068 | Branch Circuit | Unmarked QO | room 327 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1980 | 40 | 2020 | Full needs upgrade | Price is for removing old panel and replacing it with a new one and reconnect to the existing feeds | GF
BROOKS HALL | BR | ELEC | 1069 | Distribution | Panel DLP-C | Tunnel | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1964 | 40 | 2004 | Needs upgrade | Price is for removing old panel and replacing it with a new one and reconnect to the existing feeds | GF
BROOKS HALL | BR | ELEC | 1070 | Branch Circuit | Panel LPBA | !st Fl. Corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1964 | 40 | 2004 | Needs upgrade | Price is for removing old panel and replacing it with a new one and reconnect to the existing feeds | GF
BROOKS HALL | BR | ELEC | 1071 | Branch Circuit | Panel LP-2D | N.mech. Room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1964 | 40 | 2004 | Needs upgrade | Price is for removing old panel and replacing it with a new one and reconnect to the existing feeds | GF
BENNETT TRACK | BT | ARCH | 1072 | Track surface |  |  | 4 | 58550 | sf | 696496.8942 | 926340.8693 | 0 | 0 | unknown |  | 0 | Deteriorating and in need of surface replacement; substrate in good condition. | Price is to furnish and install a 1/2" thick ISS-1000® system. Budget was given by Dynamic Sports | GF
BENNETT TRACK | BT | ARCH | 1073 | Envelope | Field Hockey Surface | Playing surface | 3 | 82573 | sf | 1149463.4855 | 1528786.4357 | 0 | 0 | unknown |  | 0 | Showing signs or wear in several key areas- replace. Is there undreground piping to be repaired? | Includes removal of existing turf, new turf surface and standard markings. Does not include any drainage or base work. Need clarification | GF
COMBINED SERVICES BUILDING | CS | ARCH | 1074 | Envelope | Windows | Insul. Alum. | 3 | 2720 | lf | 10326.5343 | 13734.2906 | 0 | 0 | 1990 | 30 | 2020 | Caulk around office windows, air infiltration around windows. | Price is for removing and replacing caulk around existing windows | GF
COMBINED SERVICES BUILDING | CS | ARCH | 1075 | Envelope | Exterior Doors | Overhead | 3 | 2 | ea | 3796.5199 | 5049.3715 | 0 | 0 | 1990 | 30 | 2020 | Add weatherstripping at bottom of door. | Price is for adding weatherstripping to the bottom of the 2 overhead doors | GF
COMBINED SERVICES BUILDING | CS | ARCH | 1076 | Floor Finishes | Carpet | offices | 1 | 14700 | sf | 3242.2298 | 4312.1619 | 0 | 0 | 1990 | 15 | 2005 | Office area worn and should be replaced 1-3 years. | Area includes print shop area and 2nd floor offices and corridors. Nothing for the Police Department was included. | GF | 684611 | 2015-05-01 | 42136.97 | The project list was to recarpet south end of the building. This also included reskinning office panels. There are three rooms left to be re-carpeted 212, 213, & 217. The rest of the building has been completed over the past 10 years.
COMBINED SERVICES BUILDING | CS | ARCH | 1077 | Conveying Systems | Elevators | 2000 lb. capacity | 3 | 1 | ea | 56947.7992 | 75740.5729 | 0 | 0 | 1990 | 40 | 2030 | Finishes should be updated. | price is for updating finishes only | GF
COMBINED SERVICES BUILDING | CS | ADAC | 1078 | BF/ADA Compliance | Interior Door Hardware |  | 3 | 76 | ea | 48089.2527 | 63958.706 | 0 | 0 | 1990 |  | 1990 | Upgrade door handles to ADA-accessible lever handles. | double check quantity. 30 was on the spreadsheet when it was sent to me I just want to make sure that is the number of hardware sets that need to be changed out. _ Looking at plan I count 76 hardware sets.we can keep the 76 to be safe. | GF
COMBINED SERVICES BUILDING | CS | MECH | 1079 | Domestic cold water system | Piping | Entire building | 3 | 70000 | sf | 287902.7626 | 382910.6742 | 0 | 0 | 1990 | 40 | 2030 | Good condition, no reported problems. Galvanized/copper mix | Should be 2? Rated at 3 based on the reported galvanized piping and related service issues. Price is for reaplcing existing piping and includes some architectural demo and patching/replacing of finishes | GF
COMBINED SERVICES BUILDING | CS | MECH | 1080 | Domestic hot water system | Piping | Entire building | 3 | 70000 | sf | 287902.7626 | 382910.6742 | 0 | 0 | 1990 | 40 | 2030 | Good condition, no reported problems. Galvanized/copper mix | Should be 2? Rated at 3 based on the reported galvanized piping and related service issues. Price is for reaplcing existing piping and includes some architectural demo and patching/replacing of finishes | GF
COMBINED SERVICES BUILDING | CS | LSAF | 1081 | Life Safety | Egress Lighting | Building remainder | 3 | 60 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 2009 | 20 | 2029 | Wallmounted battery units | Price is for 60 new Wall mounted battery units. | GF
CART | EA | ARCH | 1082 | Envelope | Exterior Doors | Front entrance | 3 | 2 | ea | 15186.0798 | 20197.4861 | 0 | 0 | 2001 | 30 | 2031 | Add power assist opener at front building entrance. |  | GF
CART | EA | MECH | 1083 | Ventilation/Terminal Units | AHU/DX Cool/Nat. Gas Heat | /East exterior on grade | 4 | 50 | Tons | 98709.5186 | 131283.6597 | 0 | 0 | 2001 | 15 | 2016 | Replace condenser coils |  | GF
CART | EA | SUST | 1084 | Energy/Lighting | 2x4 3 lamp parabolic flourescent troffers | Computer Room | 3 | 16 | ea | 7086.8372 | 9425.4935 | 0 | 0 | 2001 | 20 | 2021 | Could be upgraded for energy savings |  | GF
CART | EA | SUST | 1085 | Energy/Lighting | 4 foot 4 lamp surface wraparound flourescent fixtures | Corridor by Room B | 3 | 16 | ea | 7086.8372 | 9425.4935 | 0 | 0 | 2001 | 20 | 2021 | Could be upgraded for energy savings |  | GF
CART | EA | SUST | 1086 | Energy/Lighting | 2x4 3 lamp flourescent troffers with acrylic lenses | Corridors | 3 | 8 | ea | 3543.4186 | 4712.7468 | 0 | 0 | 2001 | 20 | 2021 | Could be upgraded for energy savings |  | GF
EDUCATION AND HUMAN SERVICES | ED | SUST | 1087 | Energy/Lighting | 150 Watt MH fixtures on pendants | Corridors | 3 |  |  | 0 | 0 | 0 | 0 | 2009 | 20 | 2029 | Could be upgraded for energy savings |  | GF
FINCH HALL | FI | ARCH | 1088 | Envelope | Windows | Single Pane Alum. | 4 | 1600 | sf | 111364.5851 | 148114.8982 | 0 | 0 | 1951 | 30 | 1981 | Original to building. | Includes removing of old window, new aluminum framed window, caulk and minor finish patch around. | GF
FINCH HALL | FI | ARCH | 1089 | Envelope | Glass Block | Fieldhouse | 3 | 1200 | sf | 53151.2792 | 70691.2014 | 0 | 0 | 1951 | 40 | 1991 | Repairs have been made to glass block - paint lintels to remove rust. | Price is for cleaning and painting lintels only. | GF
FINCH HALL | FI | ARCH | 1090 | Envelope | Exterior Doors | Alum. entry doors | 4 | 26 | ea | 164515.8643 | 218806.0996 | 0 | 0 | 1951 | 30 | 1981 | Original to building. | Includes removal and replacement of new Aluminum Entry Doors. | GF
FINCH HALL | FI | ARCH | 1091 | Envelope | Exterior Wall System | Brick / Conc. Block | 1 | 1000 | sf | 0 | 0 | 0 | 0 | 1951 | 30 | 1981 | Brick requires tuck pointing and replacing broken bricks | Brick pointing and replace damage. | GF | 684236 | 2013-10-18 | 116197 | Limestone was also completed but not glass block.
FINCH HALL | FI | ARCH | 1092 | Envelope |  | Limestone/Gl. Block | 3 | 100 | lf | 12655.0665 | 16831.2384 | 0 | 0 | 1951 | 40 | 1991 | Broken Limestone. | Price is to remove and replace damaged limestone areas. | GF
FINCH HALL | FI | ARCH | 1093 | Envelope | Roof/Penetrations | Fieldhouse | 3 | 33000 | sf | 960519.5464 | 1277490.9967 | 0 | 0 | 1993 | 20 | 2013 | Entire roof in fair condition. Cracking and weathering. | Asphalt roof with Aggregate | GF
FINCH HALL | FI | ARCH | 1094 | Envelope |  | Roofs 2-10 | 3 | 52700 | sf | 1533920.6089 | 2040114.4098 | 0 | 0 | 1996 | 20 | 2016 | Entire roof in fair condition. Cracking and weathering. | Asphalt roof with Aggregate | GF
FINCH HALL | FI | ARCH | 1095 | Interior Structure | Partitions | Conc. Walls Ptd. | 3 | 85700 | sf | 135567.3997 | 180304.6417 | 0 | 0 | 1951 | 30 | 1981 | Paint | Price is for repainting of existing partitions | GF
FINCH HALL | FI | ARCH | 1096 | Interior Structure | Stairs | Terrazzo | 3 | 1200 | sf | 68337.359 | 90888.6875 | 0 | 0 | 1951 | 30 | 1981 |  | Price is for removing and replacing existing terrazzo on stairs | GF
FINCH HALL | FI | ARCH | 1097 | Interior Structure | Toilet Rooms | Fieldhouse | 4 | 585 | sf | 55524.1042 | 73847.0586 | 0 | 0 | 1951 | 30 | 1981 | Room 121 and Room 118 | Price is for renovation of existing bathroom finishes only | GF
FINCH HALL | FI | ARCH | 1098 | Interior Structure | Toilet Rooms | Finch Hall | 3 | 480 | sf | 60744.3191 | 80789.9445 | 0 | 0 | 1951 | 30 | 1981 |  | Price is for updating finishes and making bathrooms ADA compliant | GF
FINCH HALL | FI | ARCH | 1099 | Floor Finishes | Fieldhouse | Gym Floor | 4 | 31700 | sf | 601748.4115 | 800325.3872 | 0 | 0 | 1983 | 20 | 2003 |  | Floor is concrete apron and rubber flooring in center. | GF
FINCH HALL | FI | ARCH | 1100 | Floor Finishes | ROTC | Wood Gym Floor | 3 | 10600 | sf | 28283.364 | 28283.364 | 0 | 0 | 1983 | 10 | 1993 | Floor shows excessive wear. CMU comment need to plan $6000 every other year for screen and recoat. | $27,000 is cost for screen and recoat everyother year for the next 10 years | GF | 684227 | 2013-07-02 | 17125.9 | Need to plan the same work every 10yrs. Every other year screen and recoat
FINCH HALL | FI | ARCH | 1101 | Wall Finishes | Glazed Block | Locker Rooms | 3 | 100 | sf | 6327.5332 | 8415.6192 | 0 | 0 | 1951 | 30 | 1981 | Repair glazed block @ Women locker rm shower + vertical crack @ corridor | Price is for repairing existing glazed block in women's locker room and in hallway | GF
FINCH HALL | FI | ARCH | 1102 | Ceiling Finishes | Corridors | 12" x 12" spine | 3 | 3815 | sf | 31381.4011 | 41737.2635 | 0 | 0 | 1951 | 30 | 1981 | Original to building. | Price is for removing old ceiling system and replacing it with a new ACT ceiling. Additional money has been added to the typical ceiling price for the added work to demo of the existing splined ceiling | GF
FINCH HALL | FI | ARCH | 1103 | Ceiling Finishes | Offices | 2' x 2' / 2' x 4' | 3 | 4550 | sf | 25911.2486 | 34461.9607 | 0 | 0 | 1983 | 20 | 2003 | Has been renovated - not original ceiling. | Price is for removing old ceiling system and replacing it with a new ACT ceiling. | GF
FINCH HALL | FI | ARCH | 1104 | Ceiling Finishes | Entry lobbies | plaster | 3 |  |  | 0 | 0 | 0 | 0 | Unknown | 40 | 40 | repairs needed - O&M? |  | GF
FINCH HALL | FI | ADAC | 1105 | BF/ADA Compliance | Accessible Entrances | Front entry | 3 | 1 | ea | 7593.0399 | 10098.7431 | 0 | 0 | 1983 | 20 | 2003 | Replace door and opener. | Price is for adding automatic opener only. Door replacement cost is included above | GF
FINCH HALL | FI | ADAC | 1106 | BF/ADA Compliance |  | Side entry | 4 | 1 | ea | 7593.0399 | 10098.7431 | 0 | 0 | 1983 | 20 | 2003 | Replace door and opener. | Price is for adding automatic opener only. Door replacement cost is included above | GF
FINCH HALL | FI | MECH | 1107 | Ventilation/Terminal Units | AHU | AHU-1 R.A. Fan/Rm. 211 | 3 |  |  | 0 | 0 | 0 | 0 | 1951 | 40 | 1991 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1108 | Ventilation/Terminal Units | AHU/Steam Heat | AHU/S.W. Fieldhouse | 3 | 10000 | cfm | 126550.6649 | 168312.3843 | 0 | 0 | 1951 | 40 | 1991 | Replace nearing end of useful life | Price includes removing and replacing existing unit and reconnecting to existing mains. Mech information came from sheet M-1 dated 10-1-49 | GF
FINCH HALL | FI | MECH | 1109 | Ventilation/Terminal Units | AHU/Steam Heat | AHU/N.W. Fieldhouse | 3 | 10000 | cfm | 126550.6649 | 168312.3843 | 0 | 0 | 1951 | 40 | 1991 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1110 | Ventilation/Terminal Units | AHU/Exhaust | AHU/S.E. Fieldhouse | 3 | 10140 | cfm | 128322.3742 | 170668.7577 | 0 | 0 | 1951 | 40 | 1991 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1111 | Ventilation/Terminal Units | AHU/Exhaust | AHU/N.E. Fieldhouse | 3 | 10140 | cfm | 128322.3742 | 170668.7577 | 0 | 0 | 1951 | 40 | 1991 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1112 | Ventilation/Terminal Units | AHU/Steam Heat | AHU/W. Gymnasium | 3 | 6270 | cfm | 79347.2669 | 105531.8649 | 0 | 0 | 1951 | 40 | 1991 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1113 | Ventilation/Terminal Units | AHU/Steam Heat | AHU/W. Gymnasium | 3 | 6270 | cfm | 79347.2669 | 105531.8649 | 0 | 0 | 1951 | 40 | 1991 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1114 | Ventilation/Terminal Units | AHU/Steam Heat | AHU/E. Gymnasium | 3 | 6270 | cfm | 79347.2669 | 105531.8649 | 0 | 0 | 1951 | 40 | 1991 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1115 | Ventilation/Terminal Units | AHU/Steam Heat | AHU/E. Gymnasium | 3 | 6270 | cfm | 79347.2669 | 105531.8649 | 0 | 0 | 1951 | 40 | 1991 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1116 | Ventilation/Terminal Units | Terminal units/Unit Heater | Steam/Various locations | 3 | 27 | ea | 119590.3783 | 159055.2031 | 0 | 0 | 1951 | 20 | 1971 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1117 | Ventilation/Terminal Units | Terminal units/Unit Ventilators | Steam/Various locations | 3 | 4 | ea | 78461.4122 | 104353.6783 | 0 | 0 | 1951 | 20 | 1971 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1118 | Ventilation/Terminal Units | Terminal units/Cabinet Heaters | Steam/Various locations | 3 | 10 | ea | 56947.7992 | 75740.5729 | 0 | 0 | 1951 | 20 | 1971 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1119 | Ventilation/Terminal Units | Terminal units/Fin Tube | Steam/Various locations | 3 |  |  | 0 | 0 | 0 | 0 | 1951 | 25 | 1976 | Replace nearing end of useful life | With UH? Unable to answer. | GF
FINCH HALL | FI | MECH | 1120 | Steam System | PRV Station | Entire building | 3 | 1 | ea | 132878.1981 | 176728.0035 | 0 | 0 | 1951 | 50 | 2001 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1121 | Steam System | Piping | Entire building | 4 | 85700 | sf | 298248.2794 | 396670.2116 | 0 | 0 | 1951 | 50 | 2001 | Replace condensate piping as it is reaching end of useful life with reported failures. | PRV Price include steam piping to heat exchanger. Should address entire building, repair clamps were visible on condensate lines at various locations throughout building. Price is for replacing the steam pipe in the building. Some architectural demo and patching/replacement of finishes is included | GF
FINCH HALL | FI | MECH | 1122 | Building Management | HVAC Control | Pneumatic/DDC | 3 | 85700 | sf | 433815.6792 | 576974.8533 | 0 | 0 | 1951 | 25 | 1976 | Upgrade to new DDC system | price is for replacing existing controls with new DDC controls | GF
FINCH HALL | FI | MECH | 1123 | Storm/Sanitary sewer system | Piping | Entire building | 4 | 85700 | sf | 298248.2794 | 396670.2116 | 0 | 0 | 1951 | 40 | 1991 | Replace all drainage piping, failures reported | Price is for replacing strom/sanitary piping only. No other piping has been included | GF
FINCH HALL | FI | MECH | 1124 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rms. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | 2000 | 10 | 2010 | Replace nearing end of useful life | Verify Quantity One duplex unit. | GF
FINCH HALL | FI | MECH | 1125 | Domestic cold water system | Piping | Entire building | 3 | 85700 | sf | 298248.2794 | 396670.2116 | 0 | 0 | 1951 | 40 | 1991 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | MECH | 1126 | Domestic hot water system | Piping | Entire building | 3 | 85700 | sf | 298248.2794 | 396670.2116 | 0 | 0 | 1951 | 40 | 1991 | Replace nearing end of useful life |  | GF
FINCH HALL | FI | EH&S | 1127 | Environmental Health & Safety | asbestos abatement | allowance for mech | 3 | 85700 | sf | 433815.6792 | 576974.8533 | 0 | 0 | 1951 |  | 1951 |  |  | GF
FINCH HALL | FI | ELEC | 1128 | Distribution | Westinghouse 480v. Distribution Panel | Room 211 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 | Needs Upgrade | is this the main distribution panel? Yes | GF
FINCH HALL | FI | ELEC | 1129 | Distribution | Westinghouse Lighting Distribution | Room 211 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 | Needs Upgrade |  | GF
FINCH HALL | FI | ELEC | 1130 | Panel Boards | Panel LPZ | Gym | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 | Needs Upgrade |  | GF
FINCH HALL | FI | ELEC | 1131 | Panel Boards | Panel A | Room 004 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | Full-needs upgrade |  | GF
FINCH HALL | FI | ELEC | 1132 | Panel Boards | Fire Alarm Panel | Room 004 | 4 | 1 | 1 | 6327.5332 | 8415.6192 | 0 | 0 | 1970 | 40 | 2010 | Full-needs upgrade |  | GF
FINCH HALL | FI | ELEC | 1133 | Panel Boards | Lighting Panel | Room 211 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 | Needs Upgrade |  | GF
FINCH HALL | FI | ELEC | 1134 | Panel Boards | Lighting Panel | Gym | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 | Needs Upgrade |  | GF
FINCH HALL | FI | ELEC | 1135 | Panel Boards | LP109 | Room 109 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 | Needs Upgrade |  | GF
FINCH HALL | FI | ELEC | 1136 | Panel Boards | Lighting Panel | Room 125 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 | Needs Upgrade |  | GF
FINCH HALL | FI | ELEC | 1137 | Panel Boards | Lighting Panel | Room 125 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | Needs Upgrade |  | GF
FINCH HALL | FI | ELEC | 1138 | Panel Boards | Two circuit Fuse Panel | Room 125 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | Needs Upgrade |  | GF
FINCH HALL | FI | ELEC | 1139 | Panel Boards | Lighting Panel | Corridor outside of Gym | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 | Needs Upgrade |  | GF
FINCH HALL | FI | ELEC | 1140 | Panel Boards | Lighting Panel | Gym | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 | Needs Upgrade |  | GF
FINCH HALL | FI | ELEC | 1141 | Panel Boards | Lighting Panel | Corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 | Needs Upgrade |  | GF
FINCH HALL | FI | ELEC | 1142 | Lighting | 4 foot wraparound fixtures | corridors and some rooms | 3 | 100 | 1 | 44292.7327 | 58909.3345 | 0 | 0 | Unknown | 20 | 20 | Has T-8's | Plans show 2' fixtures in corridor. Quantity is for replacing 4' fixtures in the first floor offices. | GF
FINCH HALL | FI | ELEC | 1143 | Lighting | 2x2 surface | W. Entrance | 3 | 10 | ea | 6327.5332 | 8415.6192 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade | Exterior and Interior or Exterior? Price include removal and replacement of exterior fixtures at the west entrance. | GF
FINCH HALL | FI | ELEC | 1144 | Lighting | Controls |  | 3 | 85700 | sf | 108453.9198 | 144243.7133 | 0 | 0 | Unknown |  | 0 | None |  | GF
FINCH HALL | FI | ELEC | 1145 | Lighting | 12x12 recessed fixtures | Exterior Canopies | 4 | 4 | ea | 2531.0133 | 3366.2477 | 0 | 0 | Unknown | 20 | 20 | Needs Upgrade | price is for replacing 1' x 1' recessed lights in entry overhangs | GF
FINCH HALL | FI | LSAF | 1146 | Life Safety | Egress lighting | Bld. | 3 | 50 | ea | 31637.6662 | 42078.0961 | 0 | 0 | Unknown | 20 | 20 | Battery Wallpacks | price is for adding 100 battery wall packs for emergency egress lighting | GF
FINCH HALL | FI | LSAF | 1147 | Life Safety | Fire Alarm Simplex 4002 | Bld. | 3 | 142963.9 | sf | 904608.8299 | 1203129.7437 | 0 | 0 | Unknown | 40 | 40 | Needs Upgrade if renovated | Upgrade entire system or just main panel? | GF
| FI | LSAF | 1148 | Life Safety | Area of Refuge | Allowance | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | GF
FOUST HALL | FO | ARCH | 1149 | Envelope | Exterior Doors | Orig. Aluminum | 3 | 14 | ea | 88585.4654 | 117818.669 | 0 | 0 | 1973 | 30 | 2003 | Exterior doors original to building. | Price is for removing existing doors and replacing them with new aluminum framed doors | GF
FOUST HALL | FO | ARCH | 1150 | Envelope | Roof/Penetrations |  | 1 | 470 | sf | 0 | 0 | 0 | 0 | 1989 | 30 | 2019 | Repaired roof in good condition, leaks to be repaired. | Price is for removal and replacement of 470 sf of roofing | GF | 654046 | 2013-11-15 | 465621.92 | the entire roof was replaced along with fixing the access hatch and guard rails.
FOUST HALL | FO | ARCH | 1151 | Interior Structure | Interior Doors | Corridor / Office | 3 | 205 | ea | 129714.4315 | 172520.1939 | 0 | 0 | 1989 | 40 | 2029 | Door Hardware does not meet current barrier free codes. | Price is for replacing existing hardware with ADA compliant hardware | GF
FOUST HALL | FO | ARCH | 1152 | Interior Structure | Stairs | Quarry tile | 3 | 50 | sf | 3163.7666 | 4207.8096 | 0 | 0 | 1973 | 40 | 2013 | Repair leak in corner of stair structure. | Area shown in picture only? | GF
FOUST HALL | FO | ARCH | 1153 | Conveying Systems | Elevators | Cab finishes | 3 | 1 | ea | 56947.7992 | 75740.5729 | 0 | 0 | 1973 | 40 | 2013 | Recommend cab finish upgrade. | Price is for replacing elevator finishes only | GF
FOUST HALL | FO | ARCH | 1154 | Conveying Systems | Elevators | cylinder replacement | 1 | 1 | ea | 0 | 0 | 0 | 0 | 1973 | 40 | 2013 | Otis Elevator recommends this work for 2014 per May 1, 2013 letter. |  | GF | 654346 | 2015-08-01 | 35500
FOUST HALL | FO | ARCH | 1155 | Conveying Systems | Elevators | modernization | 3 | 1 | ea | 64347.7957 | 85582.5683 | 0 | 0 | 1973 | 40 | 2013 | Otis Elevator recommends this work for 2022 per May 1, 2013 letter. |  | GF
FOUST HALL | FO | ADAC | 1156 | BF/ADA Compliance | Toilet Rooms |  | 3 | 570 | sf | 72133.879 | 95938.059 | 0 | 0 | 1997 | 40 | 2037 | Some first floor toilets are ADA=accessible. | Price is for toilet rooms 111, 109, and second floor mens and women's | GF
FOUST HALL | FO | MECH | 1157 | Ventilation/Terminal Units | AHU/CHW Cool/Steam Heat | SA-3/033 | 4 | 6000 | cfm | 75930.3989 | 100987.4306 | 0 | 0 | 1973 | 40 | 2013 | Replace nearing end of useful life |  | GF
FOUST HALL | FO | MECH | 1158 | Ventilation/Terminal Units | Terminal units/VAV | Carrier/Various locations | 4 | 22 | ea | 208808.597 | 277715.4341 | 0 | 0 | 1973 | 20 | 1993 | Replace nearing end of useful life. Failures reported. Consider replacement with VAV box with terminal reheat. | Price is replacing units with new and connect to existing ductwork | GF
FOUST HALL | FO | MECH | 1159 | Chilled Water System | Pumps | Entire building/Rm. 034 | 3 | 2 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1973 | 20 | 1993 | Replace nearing end of useful life | chilled water pumps only | GF
FOUST HALL | FO | MECH | 1160 | Chilled Water System | Piping | Entire building | 4 | 52000 | sf | 325741.4114 | 433236.0771 | 0 | 0 | 1973 | 40 | 2013 | Replace nearing end of useful life. Evidence of extensive external rust | Price is for replacing existing chilled water pipes. Some architectural demo and patch/replacement of finishes is included | GF
FOUST HALL | FO | MECH | 1161 | Chilled Water System | Insulation | Entire building | 3 | 52000 | sf | 78967.6149 | 105026.9278 | 0 | 0 | 1973 |  | 1973 | Replace with piping system | price is for insulation on new chilled water pipes | GF
FOUST HALL | FO | MECH | 1162 | Heating Water System | Pumps | Entire building/Rm. 034 | 3 | 3 | ea | 17084.3398 | 22722.1719 | 0 | 0 | 1973 | 20 | 1993 | Replace nearing end of useful life | Price is for replacing inline heating water pumps | GF
FOUST HALL | FO | MECH | 1163 | Building Management | HVAC Control | Pneumatic/DDC | 3 | 52000 | sf | 263225.3829 | 350089.7593 | 0 | 0 | 1973 | 25 | 1998 | Upgrade to new DDC system | Price is for replacing existing controls to new DDC controls | GF
FOUST HALL | FO | MECH | 1164 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rms. | 3 | 2 | ea | 45558.2394 | 60592.4583 | 0 | 0 | Unknown | 10 | 10 | Replace as precautionary measure | price is for replacing existing sump pumps with new ones. | GF
FOUST HALL | FO | EH&S | 1165 | Environmental Health & Safety | Asbestos abatement | Allowance for mech items | 3 | 53880 | sf | 272741.9929 | 362746.8506 | 0 | 0 | 1973 |  | 1973 |  |  | GF
GRAWN HALL | GR | ARCH | 1166 | Envelope | Entrance Soffit | Entrance | 3 | 4 | ea | 5062.0266 | 6732.4954 | 0 | 0 | 1915 |  | 1915 | Add vents in soffit to improve airflow above soffit. | Four. How big? Budget is currently $1,000/ea | GF
GRAWN HALL | GR | ARCH | 1167 | Envelope | Alum. Trim | Top of building | 3 | 145 |  | 2752.477 | 3660.7944 | 0 | 0 | 1915 |  | 1915 | Add new finish, replace rusted alum. fascia. | only on 88 Addition? | GF
GRAWN HALL | GR | ARCH | 1168 | Interior Structure | Toilet Rooms | All | 1 | 1560 | sf | 0 | 0 | 0 | 0 | 1966 | 40 | 2006 | Finishes are original. | Price is for updating Finishes | GF | 654089 | 2013-08-26 | 65415.25 | This work was completed as part of the 2012DomesticWaterReplacement
GRAWN HALL | GR | ARCH | 1169 | Floor Finish | Carpet | Corridors | 3 | 320 | sf | 3239.697 | 4308.797 | 0 | 0 | 1998 |  | 1998 | Carpeted floors in corridors and public areas have to be replaced. | quantity from auditorium. Unit price increased because of the small area | GF
GRAWN HALL | GR | ARCH | 1170 | Floor Finish | Composite Tile | Corridors | 3 | 11780 | sf | 74538.3416 | 99135.9943 | 0 | 0 | 1960 |  | 1960 | Corridor tile in need of replacement. | 1966 addition sf only | GF
GRAWN HALL | GR | ARCH | 1171 | Floor Finish | Carpet | Offices / Classrooms | 3 | 390 | sf | 2714.5118 | 3610.3006 | 0 | 0 | 1988 | 20 | 2008 | replace carpet in auditorium in 1966 bldg |  | GF
GRAWN HALL | GR | ARCH | 1172 | Conveying Systems | Elevators | modernization | 5 |  |  | 46652.1519 | 62047.362 | 0 | 0 | 1988 | 30 | 2018 | Otis recommends this work in 2014. |  | GF
GRAWN HALL | GR | ARCH | 1173 | Conveying Systems | Elevators | cylinder replacement | 5 |  |  | 38072.4458 | 50636.3529 | 0 | 0 | 1988 | 30 | 2018 | Otis recommends this work in 2014. |  | GF
GRAWN HALL | GR | ADAC | 1174 | BF/ADA Compliance | Interior Doors | Offices / Classrooms | 3 | 205 | ea | 129714.4315 | 172520.1939 | 0 | 0 | 1915 | 40 | 1955 | Classroom hardware does not meet ADA requirements. | Includes removal of old hardware and replacing with new ADA compliant hardware | GF
GRAWN HALL | GR | EH&S | 1175 | Environmental Health and Safety | asbestos abatement | allowance for flooring | 3 | 11780 | sf | 44723.005 | 59481.5966 | 0 | 0 | 1960 |  | 1960 |  |  | GF
GRAWN HALL | GR | MECH | 1176 | Ventilation/Terminal Units | AHU/Chilled Cool/Hot Water Heat | AHU-2, Rm. 004 | 3 | 3000 | cfm | 37965.1995 | 50493.7153 | 0 | 0 | 1989 | 30 | 2019 | Fair condition, replace with future renovations | Mech Information was taken from sheet M-5 dated 4-9-65. Price includes removing old unit and replacing with same size unit and reconnect to existing mains. | GF
GRAWN HALL | GR | MECH | 1177 | Ventilation/Terminal Units | AHU/Chilled Cool/Hot Water Heat | AHU-3, Rm. 013 | 3 | 18000 | cfm | 227791.1968 | 302962.2917 | 0 | 0 | 1966 | 30 | 1996 | Replace nearing end of useful life, evaluate space requirements | Mech Information was taken from sheet M-5 dated 4-9-65. Price includes removing old unit and replacing with same size unit and reconnect to existing mains. | GF
GRAWN HALL | GR | MECH | 1178 | Ventilation/Terminal Units | Unit Vent/Chilled Cool/Hot Water Heat | All Classrooms | 3 | 32 | ea | 1093397.7445 | 1454219.0001 | 0 | 0 | 1966 | 20 | 1986 | Replace nearing end of useful life, evaluate space requirements | More Detail on Units, What about Fin Tube? Quantity was taken from mech drawings dated 4-9-65. There was no visible fin tube, U.V. quantity sounds about right, no additional information to add on U.V.s. Price is for replacing units with new and reconnecting to existing pipes | GF
GRAWN HALL | GR | MECH | 1179 | Chilled Water System | Pumps | Entire building, Rm. 001 | 4 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1966 | 20 | 1986 | Replace nearing end of useful life | Pumps for AHU #1? Building pumps | GF
GRAWN HALL | GR | MECH | 1180 | Chilled Water System | Insulation | Entire system | 4 | 84465 | sf | 128269.2229 | 170598.0665 | 0 | 0 | 1966/1989 |  | 0 | Replace with insulation rated for operating conditions |  | GF
GRAWN HALL | GR | MECH | 1181 | Heating Water System | Pumps | Entire building, Rm. 001 | 3 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1966 | 20 | 1986 | Replace nearing end of useful life | Mechanical information was taken from mech drawings dated 4-9-65 | GF
GRAWN HALL | GR | MECH | 1182 | Heating Water System | Heat exchanger | Entire building, Rm. 001 | 3 | 2 | ea | 75930.3989 | 100987.4306 | 0 | 0 | 1966 | 24 | 1990 | Replace nearing end of useful life | price is for replacing 2 heat exchangers | GF
GRAWN HALL | GR | MECH | 1183 | Heating Water System | Insulation | Entire system | 3 | 84465 | sf | 128269.2229 | 170598.0665 | 0 | 0 | 1966/1989 |  | 0 | Good condition | should be 2? Rating of 2 will work as 3 was arrived at because of ACM content and CMU is OK with retained encapsulated ACM components. Price is for replacing all of the heating water pipe insulation | GF
GRAWN HALL | GR | MECH | 1184 | Steam System | Insulation | Entire system | 3 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1966 |  | 1966 | Good condition | should be 2? Rating of 2 will work as 3 was arrived at because of ACM content and CMU is OK with retained encapsulated ACM components. Price is for replacing steam piping insulation for the PRV station | GF
GRAWN HALL | GR | MECH | 1185 | Building Management | HVAC Control | Hybrid and straight pneumatic | 4 | 84465 | sf | 427564.0763 | 568660.2215 | 0 | 0 | 1966/1989 | 20 | 20 | Replace with DDC system. Oil contamination related component failures reported | price is for replacing pneumatic controls with new DDC controls | GF
GRAWN HALL | GR | EH&S | 1186 | Environmental Health & Safety | Asbestos abatement | allowance for mech items | 3 | 84465 | sf | 427564.0763 | 568660.2215 | 0 | 0 | 1966 |  | 1966 |  |  | GF
GRAWN HALL | GR | MECH | 1187 | Heating | Ice melt equipment | Room A - 2nd Floor | 3 | 1 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 2000 | 40 | 2040 | 1 of 3 not working |  | GF
GRAWN HALL | GR | LSAF | 1188 | Life Safety | Fire Alarm | Room 243 | 5 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 1960 | 40 | 2000 | Does not meet code, replace | Price is for replacing fire alarm panel only | GF
GRAWN HALL | GR | LSAF | 1189 | Life Safety | Area of Refuge | Allowance | 5 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | 1960 |  | 1960 | per S. Esch |  | GF
GRAWN HALL | GR | ELEC | 1190 | Distribution | Panel LP2C | Room 237 | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Obsolete, full, replace | price includes replacing panel only, reusing existing feeders | GF
GRAWN HALL | GR | ELEC | 1191 | Distribution | Panel LP1C |  | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Electrical | price includes replacing panel only, reusing existing feeders | GF
GRAWN HALL | GR | ELEC | 1192 | Distribution | PanelLP1G/Lp1D |  | 5 | 2 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 1967 | 40 | 2007 | Obsolete, full, replace | price includes replacing panel only, reusing existing feeders | GF
GRAWN HALL | GR | LSAF | 1193 | Life Safety | Emergency Lighting | Corridors | 5 | 30 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 1967 | 15 | 1982 | Does not meet code, replace | Price is for adding 100 emergency lights in the buildings corridors | GF
GRAWN HALL | GR | ELEC | 1194 | Lighting | Lighting | 90% of facility | 3 | 76018.5 | sf | 240504.7929 | 319871.3746 | 0 | 0 | Unknown | 20 | 20 | Replace/energy savings | price is for replacing about 650 lights | GF
HEALTH PROFESSIONS BUILDING | HP | MECH | 1195 | Heating Water System | HWPumps | Entire building, Basement Mech. Rm. | 3 | 1 | ea | 759.304 | 1009.8743 | 0 | 0 | 2003 | 20 | 2023 | Good condition, repair shaft seals | Price is for 1 person for 8 hours of work to replace seals | GF
HEALTH PROFESSIONS BUILDING | HP | MECH | 1196 | Heating Water System | HWPumps | New wing, Basement Mech. Rm. | 3 | 1 | ea | 759.304 | 1009.8743 | 0 | 0 | 2012 | 10 | 2022 | Good condition, repair shaft seals | Price is for 1 person for 8 hours of work to replace seals | GF
INDUSTRIAL EDUCATION TECHNOLOGY | IT | ARCH | 1197 | Floor Finishes |  | Carpet tile | 3 | 10015 | sf | 69707.27 | 92710.6691 | 0 | 0 | 1989 | 15 | 2004 | Repair tile floor, tiles coming off floor. Replace classroom carpet tile. |  | GF
INDUSTRIAL EDUCATION TECHNOLOGY | IT | ARCH | 1198 | Floor Finishes |  | Ceramic Tile | 3 | 1000 | sf | 10124.0532 | 13464.9907 | 0 | 0 | 1989 | 15 | 2004 |  | price is based off a 1000 sf area | GF
INDUSTRIAL EDUCATION TECHNOLOGY | IT | ARCH | 1199 | Wall Finishes |  | Tile | 3 | 500 | sf | 7593.0399 | 10098.7431 | 0 | 0 | 1989 | 10 | 1999 | Repair wall tile coming off. | price is for repairing 500 sf of ceramic wall tile | GF
INDUSTRIAL EDUCATION TECHNOLOGY | IT | ADAC | 1200 | BF/ADA Compliance | Interior Door Hardware | Hardware | 3 | 116 | ea | 73399.3856 | 97621.1829 | 0 | 0 | 1989 | 40 | 2029 | Replace non-accessible door hardware with accessible hardware. | Same as above? | GF
BUSH THEATRE | MO | ARCH | 1201 | Envelope | Exterior Doors | Exterior walls | 3 | 14 | ea | 88585.4654 | 117818.669 | 0 | 0 | 1971 | 30 | 2001 | Doors original to building. |  | GF
BUSH THEATRE | MO | ARCH | 1202 | Envelope | Exterior Wall System |  | 3 | 500 | sf | 15818.8331 | 21039.048 | 0 | 0 | 1971 | 40 | 2011 | Tuck point and repair brick. |  | GF
BUSH THEATRE | MO | ARCH | 1203 | Envelope | Roof/Penetrations |  | 3 | 500 | sf | 14553.3265 | 19355.9242 | 0 | 0 | 1993/1999 | 30 | 30 | Identified roof leaks to be repaired. |  | GF
BUSH THEATRE | MO | ARCH | 1204 | Interior Structure | Interior Doors | Wood / Glass | 3 | 50 | ea | 31637.6662 | 42078.0961 | 0 | 0 | Unknown | 40 | 40 | Remove lites in interior wood doors, replace with metal panels. |  | GF
BUSH THEATRE | MO | ARCH | 1205 | Interior Structure | Stairs | Quarry / Terrazzo | 3 | 100 | sf | 10756.8065 | 14306.5527 | 0 | 0 | 1971 | 40 | 2011 | Repair cracks in terrazzo stair. |  | GF
BUSH THEATRE | MO | ARCH | 1206 | Interior Structure | Toilet Rooms | Bush Theater | 3 | 430 | sf | 54416.7859 | 72374.3252 | 0 | 0 | 1971 | 40 | 2011 | Renovate toilet rooms at Bush Theater to be accessible. |  | GF
BUSH THEATRE | MO | ARCH | 1207 | Ceiling Finishes | Moore / Bush connector | 12" x 12" spline | 3 | 3265 | sf | 24791.2752 | 32972.3961 | 0 | 0 | 1971 | 30 | 2001 | 12" x 12" spline ceiling in fair condition, replace and update |  | GF
BUSH THEATRE | MO | ARCH | 1208 | Ceiling Finishes | Bush corridor | 12" x 12" spline | 3 | 5755 | sf | 43697.9446 | 58118.2663 | 0 | 0 | 1971 | 30 | 2001 | 12" x 12" spline ceiling in fair condition, replace and update |  | GF
BUSH THEATRE | MO | ARCH | 1209 | Conveying Systems | Elevators | cylinder replacement | 1 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | Otis recommends this work to be scheduled for 2016. |  | GF | 654191 | 2015-08-21 | 134430
BUSH THEATRE | MO | MECH | 1210 | Ventilation/Terminal Units | AHU/CHW Cool/Steam Heat | AHU-1/Rm. 117 | 3 | 6000 | cfm | 75930.3989 | 100987.4306 | 0 | 0 | 1971 | 30 | 2001 | Good condition no reported problems. |  | GF
BUSH THEATRE | MO | MECH | 1211 | Ventilation/Terminal Units | AHU/CHW Cool/Steam Heat | AHU-2/Rm. 213 | 3 | 7500 | cfm | 94912.9987 | 126234.2882 | 0 | 0 | 1971 | 30 | 2001 | Good condition no reported problems. |  | GF
BUSH THEATRE | MO | MECH | 1212 | Ventilation/Terminal Units | AHU/CHW Cool/Steam Heat | AHU-3/Rm. 346 | 3 | 6280 | cfm | 79473.8175 | 105700.1773 | 0 | 0 | 1971 | 30 | 2001 | Good condition no reported problems. |  | GF
BUSH THEATRE | MO | MECH | 1213 | Ventilation/Terminal Units | AHU/CHW Cool/Steam Heat | AHU-4/Rm. 443 | 3 | 7615 | cfm | 96368.3313 | 128169.8806 | 0 | 0 | 1971 | 30 | 2001 | Good condition no reported problems. |  | GF
BUSH THEATRE | MO | MECH | 1214 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-5/Rm. 103 | 3 | 7000 | cfm | 88585.4654 | 117818.669 | 0 | 0 | 1971 | 30 | 2001 | Good condition no reported problems. |  | GF
BUSH THEATRE | MO | MECH | 1215 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-6/Rm. 103 | 3 | 7000 | cfm | 88585.4654 | 117818.669 | 0 | 0 | 1971 | 30 | 2001 | Good condition no reported problems. |  | GF
BUSH THEATRE | MO | MECH | 1216 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-7/Rm. 104 | 3 | 10000 | cfm | 126550.6649 | 168312.3843 | 0 | 0 | 1971 | 30 | 2001 | Good condition no reported problems. |  | GF
BUSH THEATRE | MO | MECH | 1217 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-8/Rm. 104 | 3 | 17230 | cfm | 218046.7956 | 290002.2381 | 0 | 0 | 1971 | 30 | 2001 | Good condition no reported problems. |  | GF
BUSH THEATRE | MO | MECH | 1218 | Chilled Water System | Insulation | Entire system(s) | 3 | 78350 | sf | 118982.9351 | 158247.3037 | 0 | 0 | 1971 |  | 1971 | Good condition, reported to be some ACM |  | GF
BUSH THEATRE | MO | MECH | 1219 | Heating Water System | Insulation | Entire system | 3 | 78350 | sf | 118982.9351 | 158247.3037 | 0 | 0 | 1971 |  | 1971 | Good condition, reported to be some ACM |  | GF
BUSH THEATRE | MO | MECH | 1220 | Building Management | HVAC Control | Pneumatic | 3 | 78350 | sf | 396609.7837 | 527491.0123 | 0 | 0 | 1971 | 25 | 1996 | Replace with new DDC, reaching end of useful life |  | GF
BUSH THEATRE | MO | ELEC | 1221 | Branch Circuits | Westinghouse motor control panelboard | room 010 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1971 | 40 | 2011 | needs upgrade |  | GF
BUSH THEATRE | MO | ELEC | 1222 | Branch Circuits | unmarked Westinghouse | ciene shop | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1971 | 40 | 2011 | needs upgrade |  | GF
BUSH THEATRE | MO | ELEC | 1223 | Branch Circuits | unmarked Westinghouse | ciene shop | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1971 | 40 | 2011 | needs upgrade |  | GF
BUSH THEATRE | MO | ELEC | 1224 | Branch Circuits | Panel LP1d | by room 170 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1971 | 40 | 2011 | needs upgrade |  | GF
BUSH THEATRE | MO | ELEC | 1225 | Branch Circuits | unmarked Westinghouse | Radio Station | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1971 | 40 | 2011 | needs upgrade |  | GF
BUSH THEATRE | MO | ELEC | 1226 | Branch Circuits | unmarked Westinghouse | Radio Station | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1971 | 40 | 2011 | needs upgrade |  | GF
BUSH THEATRE | MO | ELEC | 1227 | Branch Circuits | unmarked Westinghouse | Radio Station | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1971 | 40 | 2011 | needs upgrade |  | GF
BUSH THEATRE | MO | ELEC | 1228 | Branch Circuits | Panel LP1H | TV Station | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1971 | 40 | 2011 | needs upgrade |  | GF
BUSH THEATRE | MO | ELEC | 1229 | Lighting | 250 Watt incandescent | Sciene shop | 4 | 8 | ea | 3543.4186 | 4712.7468 | 0 | 0 | Unknown | 20 | 20 | needs upgrade |  | GF
BUSH THEATRE | MO | LSAF | 1230 | Life Safety | wall mounted egress lighting | building | 3 | 12 | ea | 7593.0399 | 10098.7431 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ARCH | 1231 | Envelope | Exterior Doors | Alum. insulated | 3 | 2 | ea | 12655.0665 | 16831.2384 | 0 | 0 | 1987 | 30 | 2017 | Replace doors to match new campus standard. Add power assist operator. See below. |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ARCH | 1232 | Envelope | Exterior Wall System | Brick / CMU wall | 3 | 200 | sf | 6327.5332 | 8415.6192 | 0 | 0 | 1987 | 100 | 2087 | Tuck point brick - allow 200 sf |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ARCH | 1233 | Floor Finishes | Painted Concrete | Storage Room | 3 | 1455 | sf | 3901.0851 | 5188.4432 | 0 | 0 | 1987 | 30 | 2017 | Concrete floor to be repainted. |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ADAC | 1234 | BF/ADA Compliance | Power Assist Hardware | Front Entrance | 3 | 1 | ea | 6434.7796 | 8558.2568 | 0 | 0 | 1987 | 40 | 2027 | Provide power assist operator if entry door is replaced. |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | MECH | 1235 |  | Heater/Nat. Gas | Entire building/Room 101C | 3 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 1994 | 15 | 2009 | Good condition, no reported problems. Replace weeping dielectric unions. |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | MECH | 1236 | Natural gas piping system | Piping | Entire system | 3 | 3260 | sf | 10488.6907 | 13949.9586 | 0 | 0 | Unknown | 40 | 40 | Good condition, no reported problems. Paint exposed piping. |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ELEC | 1237 | Distribution | Panel LPA Square D NQOD 200 Amp main breaker | Room 101C | 4 | 1 | ea | 10124.0532 | 13464.9907 | 0 | 0 | 1987 | 40 | 2027 | Panel is full - tandem breakers |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ELEC | 1238 | Branch Circuit Condition | QO load center 125 amp main lug | Room 101C | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1987 | 40 | 2027 | nedds upgrade for addition of circuits |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ELEC | 1239 | Branch Circuit Condition | Circuits | Work Area | 3 | 3260 | sf | 22690.5342 | 30178.4105 | 0 | 0 | 1987 | 40 | 2027 | Needs additional circuits |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ELEC | 1240 | Branch Circuit Condition | Circuits | West Exterior | 3 | 1 | allw | 6327.5332 | 8415.6192 | 0 | 0 | 1987 | 40 | 2027 | Needs additional circuits |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ELEC | 1241 | Lighting | High Pressure Sodium Wallpacks | Exterior | 3 | 4 | 1 | 2531.0133 | 2531.0133 | 0 | 0 | 1987 | 20 | 2007 | Yellowed |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ELEC | 1242 | Lighting | 2 lamp 2x4 flourescent troffers | University Events side | 3 | 50 | 1 | 22146.3664 | 29454.6672 | 0 | 0 | 1987 | 20 | 2007 | Should be upgraded for energy savings |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ELEC | 1243 | Lighting | 4 lamp 2x4 flourescent troffers | General Counsel side | 3 | 50 | 1 | 22146.3664 | 0 | 0 | 0 | 1987 | 20 | 2007 | Should be upgraded for energy savings |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ELEC | 1244 | Lighting | 8 foot flourescent slimline shop lights | work area | 3 | 20 | 1 | 8858.5465 | 0 | 0 | 0 | 1987 | 20 | 2007 | Should be upgraded for energy savings |  | GF
MOTOR POOL UNIV ATTY EVENTS | MP | ELEC | 1245 | Lighting/Controls | Occupancy sensors | Building | 4 | 3260 | sf | 8251.1033 | 10973.9675 | 0 | 0 | Unknown |  | 0 | No automatic lighting controls in building | Unit price increased because of small SF area | GF
MUSIC BUILDING | MU | ARCH | 1246 | Envelope | Roof/Penetrations |  | 3 | 580 | sf | 16881.8587 | 22452.8721 | 0 | 0 | 1995 | 30 | 2025 | Roof repair needed above Mechanical Room and window bump-outs. | Area: Bumpouts are (2) @ 140 sf. Mech Room area is about 300 SF. Price is for removal and replacement of damaged area | GF
MUSIC BUILDING | MU | ARCH | 1247 | Floor Finishes | Carpet | Classrooms | 3 | 2000 | sf | 13920.5731 | 18514.3623 | 0 | 0 | 1995 | 15 | 2010 | select rooms may need carpet replaced |  | GF
MUSIC BUILDING | MU | ARCH | 1248 | Ceiling Finishes | Painted gyp bd. | Below Roof | 3 | 600 | sf | 6454.0839 | 8583.9316 | 0 | 0 | 1995 | 20 | 2015 | Repair areas due to roof leaks in Music Rooms. |  | GF
NORTH ART STUDIO | NA | ARCH | 1249 | Envelope | Windows | South Wall | 4 | 450 | sf | 31321.2896 | 41657.3151 | 0 | 0 | 1976 | 30 | 2006 | Windows are leaking and not weather tight. | Price is for replacing existing windows with new windows, new caulk and minor finish patch | GF
NORTH ART STUDIO | NA | ARCH | 1250 | Envelope | Exterior Doors |  | 3 | 5 |  | 31637.6662 | 42078.0961 | 0 | 0 | 1976 | 30 | 2006 | Doors to be replaced to match campus standard. | Price is for removing old entry doors and replacing with new aluminum doors | GF
NORTH ART STUDIO | NA | ARCH | 1251 | Envelope | Exterior Wall System | Ptd. Block | 3 | 1750 | sf | 4429.2733 | 5890.9334 | 0 | 0 | 1976 | 40 | 2016 |  | Price is for repainting exist exterior block wall. Includes some minor repairs. | GF
NORTH ART STUDIO | NA | ARCH | 1252 | Envelope | Skylights | At Roof Peak | 4 | 700 | sf | 53151.2792 | 70691.2014 | 0 | 0 | 1976 | 30 | 2006 | Leaking and do not open. | Price is for replacement of skylights. Includes removal of existing and replacing with new aluminum framed skylights the same size. | GF
NORTH ART STUDIO | NA | ARCH | 1253 | Interior Structure | Interior Doors | Hollow Metal | 3 | 21 | ea | 1993.173 | 2650.9201 | 0 | 0 | 1976 | 40 | 2016 | No issues, may need painting | Price is for repaint of existing metal doors | GF
NORTH ART STUDIO | NA | ARCH | 1254 | Interior Structure | Toilet Rooms | Lower Level | 3 | 9 | lf | 1708.434 | 2272.2172 | 0 | 0 | 1976 | 30 | 2006 | Replace countertops | Price is for removal of old countertops and replacing with new plastic laminate countertops in bathrooms only. | GF
NORTH ART STUDIO | NA | ARCH | 1255 | Wall Finishes |  | Painted CMU | 3 | 14600 | sf | 16628.7574 | 22116.2473 | 0 | 0 | 1976 | 40 | 2016 | No issues, may need painting | Price is for repainting existing interior partitions | GF
NORTH ART STUDIO | NA | ARCH | 1256 | Ceiling Finishes | Wood Plank Ceiling |  | 4 | 4550 | sf | 86370.8288 | 114873.2023 | 0 | 0 | 1976 | 30 | 2006 | Repair finish on wood ceiling, repair stains from skylight leaks. | Refinish south side of wood ceiling. Price is for sanding and refinishing existing wood ceiling | GF
NORTH ART STUDIO | NA | ARCH | 1257 | Conveying Systems | Elevators |  | 4 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1976 | 30 | 2006 | Elevator requires maintenance. | Repairs on lift, not replacement. What types of repairs. Carrying 20,000 for budget | GF
NORTH ART STUDIO | NA | ADAC | 1258 | BF/ADA Compliance | Interior Door Hardware |  | 3 | 21 | ea | 13287.8198 | 17672.8003 | 0 | 0 | 1976 | 30 | 2006 | Interior hardware not ADA compliant |  | GF
NORTH ART STUDIO | NA | ADAC | 1259 | BF/ADA Compliance | Toilet Rooms |  | 4 | 300 | sf | 37965.1995 | 50493.7153 | 0 | 0 | 1976 | 30 | 2006 | Toilet Rooms large enough to comply with ADA | Price is for renovation of bathroom to meet ADA code | GF
NORTH ART STUDIO | NA | MECH | 1260 | Ventilation/Terminal Units | AHU/Steam Heat | AHU-1, Room 201 | 3 | 8520 | cfm | 107821.1665 | 143402.1514 | 0 | 0 | 1976 | 30 | 2006 | Replace nearing end of useful life. Evaluate space usage, zoning and adequate return air ducting. Evaluate mechanical and passive cooling options. | Price is for removing old unit and replacing with a new one the same size. Mech information came from Mechanical sheets dated 6-9-98 | GF
NORTH ART STUDIO | NA | MECH | 1261 | Ventilation/Terminal Units | AHU/Steam Heat | MUA-1, Room 105 | 4 | 7785 | cfm | 98519.6926 | 131031.1912 | 0 | 0 | 1976 | 30 | 2006 | Replace nearing end of useful life. Evaluate space ventilation requirements. | Price is for removing old unit and replacing with a new one the same size. Mech information came from Mechanical sheets dated 6-9-99 | GF
NORTH ART STUDIO | NA | MECH | 1262 | Ventilation/Terminal Units | AHU | MUA-2, Room 105 | 4 | 8520 | cfm | 107821.1665 | 143402.1514 | 0 | 0 | 1976 | 30 | 2006 | Replace nearing end of useful life. Evaluate space ventilation requirements. | Need information on Unit. Couldn't find it on old Mech Drawings. Some of the mechanical equipment appeared as if it was installed later possible from salvage. Any information of what size to replace it with? No suggestion on capacity, heat gain from kilns would have to be determined. The addition of a passive system to supplement the existing ventilation would be another option. Price is a budget place holder based on the CFM from AHU-1. Further direction is needed to revise budget | GF
NORTH ART STUDIO | NA | MECH | 1263 | Ventilation/Terminal Units | Terminal units | Steam radiation, First Floor | 4 | 1 | ea | 3796.5199 | 5049.3715 | 0 | 0 | 1976 | 25 | 2001 | Replace nearing end of useful life | Price is for replacing old units with new ones with the same capacity | GF
NORTH ART STUDIO | NA | MECH | 1264 | Ventilation/Terminal Units | Terminal units | Steam cabinet heater, E. First Floor | 4 | 1 | ea | 5694.7799 | 7574.0573 | 0 | 0 | 1976 | 20 | 1996 | Replace nearing end of useful life | Price is for replacing old units with new ones with the same capacity | GF
NORTH ART STUDIO | NA | MECH | 1265 | Ventilation/Terminal Units | Terminal units | Steam reheat, AHU-1 | 3 | 1 | ea | 5315.1279 | 7069.1201 | 0 | 0 | 1976 | 25 | 2001 | Replace nearing end of useful life | Price is for replacing old units with new ones with the same capacity | GF
NORTH ART STUDIO | NA | MECH | 1266 | Steam System | Insulation | Entire system | 3 | 1 | ea | 12655.0665 | 16831.2384 | 0 | 0 | Unknown |  | 0 | Replace with known material with greater R value | price is to replace insulation for PRV station only | GF
NORTH ART STUDIO | NA | MECH | 1267 | Steam System | Piping | Entire building | 3 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1976 | 50 | 2026 | Replace piping associated with finned tube radiation | Price is for steam piping from PRV station to heat exchanger | GF
NORTH ART STUDIO | NA | MECH | 1268 | Building Management | HVAC Control | Hybrid and straight pneumatic | 3 | 12700 | sf | 72323.705 | 96190.5276 | 0 | 0 | 1976 | 20 | 1996 | Replace with DDC system | price is for replacing existing pneumatic controls with new DDC controls. Nit price was increased because of small SF area | GF
NORTH ART STUDIO | NA | ELEC | 1269 | Branch Panel | 120/208 ITE |  | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade | Price includes taking out old panel and replacing it with a new panel and reuse existing feeds | GF
NORTH ART STUDIO | NA | ELEC | 1270 | Branch Panel | 120/208 ITE |  | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade | Price includes taking out old panel and replacing it with a new panel and reuse existing feeds | GF
NORTH ART STUDIO | NA | ELEC | 1271 | Branch Panel | 120/208 ITE |  | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade | Price includes taking out old panel and replacing it with a new panel and reuse existing feeds | GF
NORTH ART STUDIO | NA | ELEC | 1272 | Branch Panel | 120/208 ITE |  | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade | Price includes taking out old panel and replacing it with a new panel and reuse existing feeds | GF
NORTH ART STUDIO | NA | ELEC | 1273 | Branch Panel | 120/208 ITE |  | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade | Price includes taking out old panel and replacing it with a new panel and reuse existing feeds | GF
NORTH ART STUDIO | NA | ELEC | 1274 | Branch Panel | 120/208 ITE |  | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade | Price includes taking out old panel and replacing it with a new panel and reuse existing feeds | GF
NORTH ART STUDIO | NA | ELEC | 1275 | Branch Panel | 120/208 ITE |  | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade | Price includes taking out old panel and replacing it with a new panel and reuse existing feeds | GF
NORTH ART STUDIO | NA | ELEC | 1276 | Branch Panel | 120/208 ITE |  | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade | Price includes taking out old panel and replacing it with a new panel and reuse existing feeds | GF
NORTH ART STUDIO | NA | ELEC | 1277 | Branch Panel | 120/208 ITE |  | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade | Price includes taking out old panel and replacing it with a new panel and reuse existing feeds | GF
PARK LIBRARY | PA | ARCH | 1278 | Envelope | Roof/Penetrations | Atrium metal roof | 4 | 700 | lf | 7086.8372 | 9425.4935 | 0 | 0 | 2003 | 30 | 2033 | Metal roof at atrium leaks, seal windows, weather strip glass / roof. | Price is for adding weather seal/caulk to atrium roof | GF
PARK LIBRARY | PA | ARCH | 1279 | Envelope | Roof/Penetrations | Flat membrane roof | 3 | 870 | sf | 25322.788 | 33679.3081 | 0 | 0 | 2003 | 30 | 2033 | Repair leaks at curved ext. stair and atrium roof glass. | price is for replacing damaged roof at curved area | GF
PARK LIBRARY | PA | ARCH | 1280 | Conveying Systems | Elevators | Cylinder Replacement | 5 |  |  | 39144.909 | 52062.729 | 0 | 0 | 1969 | 30 | 1999 | Otis recommendation for cylinder replacement in 2015 | Refer to Otis letter dated May 1, 2013. | GF
PARK LIBRARY | PA | ARCH | 1281 | Conveying Systems | Elevators | Modernization | 3 |  |  | 64347.7957 | 85582.5683 | 0 | 0 | 1969 | 30 | 1999 | Otis recommendation for modernization in 2021. | Refer to Otis letter dated May 1, 2013. | GF
PARK LIBRARY | PA | MECH | 1282 | Chilled Water System | Chiller/Steam | Rm. 001C | 3 | 2 @ 465 | Tons | 1235767.2424 | 1643570.4325 | 0 | 0 | 1987 | 30 | 2017 | Good condition, no reported problems | Need Pricing? Price is for 2 new chillers | GF
PARK LIBRARY | PA | MECH | 1283 | Chilled Water System | Cooling Tower | Steam Absorbers/Roof | 3 | 1 | ea | 91116.4787 | 121184.9167 | 0 | 0 | 1987 | 20 | 2007 | Replace, rust perforation | what capacity? Price is based on a 10-25 ton capacity cooling tower | GF |  |  |  | In 2015 CMU implemented a short term repair by removing rust and coating-painted cooling tower see ION 654193
PARK LIBRARY | PA | SUST | 1284 | Energy/Lighting | 30" fluorescent fixtures and 50 watt halogen | study carolls | 3 | 30 | ea | 7593.0399 | 10098.3141 | 0 | 0 | Unknown | 20 | 20 | should have an automatic control installed |  | GF
PUBLIC BROADCASTING | PB | ARCH | 1285 | Envelope | Exterior Wall System | Brick / EIFS | 3 | 500 | sf | 22146.3664 | 29454.6672 | 0 | 0 | 1981 | 100 | 2081 | EIFS needs repair as noted in report. Metal roof fascia needs repair. | Budget is based on 500 sf | GF
PUBLIC BROADCASTING | PB | ARCH | 1286 | Envelope | Roof/Penetrations | PVC Roof | 3 | 10000 | sf | 291066.5292 | 387118.4838 | 0 | 0 | 1981 | 30 | 2011 | Metal fascia needs repair. Membrane roof replacement within 5 years |  | GF
PUBLIC BROADCASTING | PB | ADAC | 1287 | BF/ADA Compliance | Interior Door Hardware | knob-type | 3 | 25 | ea | 13405.7908 | 17829.7017 | 0 | 0 | 1981 | 30 | 2011 | Interior door hardware is not ADA-accessible. | price is for replacing hardware on 25 doors to comply with ADA codes | GF
PUBLIC BROADCASTING | PB | ADAC | 1288 | BF/ADA Compliance | Toilet Rooms | Need ADA access | 3 | 300 | sf | 32173.8978 | 42791.2841 | 0 | 0 | 1981 | 30 | 2011 | Lobby toilet room is not ADA-accessible. | budget is based on 300 sf | GF
PUBLIC BROADCASTING | PB | MECH | 1289 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-1/Above room 121 | 3 | 8500 | cfm | 107568.0651 | 143065.5266 | 0 | 0 | 1981 | 30 | 2011 | Upgrade humidifier to self contained electrically generated steam injection type. |  | GF
PUBLIC BROADCASTING | PB | MECH | 1290 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-2/Above room 121 | 3 | 7700 | cfm | 97444.0119 | 129600.5359 | 0 | 0 | 1981 | 30 | 2011 | Upgrade humidifier to self contained electrically generated steam injection type. Add hot water reheat coils to VAV boxes. |  | GF
PUBLIC BROADCASTING | PB | MECH | 1291 | Ventilation/Terminal Units |  | VAV Office area | 3 | 9 | ea | 28473.8996 | 37870.2865 | 0 | 0 | unknown | 20 | 20 | Good condition, add hot water reheat coils. |  | GF
PUBLIC BROADCASTING | PB | MECH | 1292 | Chilled Water System | Chiller | Entire system | 4 | 60 | Tons | 107568.0651 | 143065.5266 | 0 | 0 | 1981 | 20 | 2001 | Replace chiller system reported in poor condition. |  | GF
PUBLIC BROADCASTING | PB | MECH | 1293 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 11500 | sf | 116426.6117 | 154847.3935 | 0 | 0 | 1981 | 40 | 2021 | Good condition, investigate restroom drainage for size, slope and condition. | should be 2? | GF
PUBLIC BROADCASTING | PB | SUST | 1294 | Lighting | 2x4 3 lamp parabolic troffers | offices | 3 | 42 | ea | 18602.9477 | 24741.9205 | 0 | 0 | 1981 | 20 | 2001 | Needs upgrade for energy savings |  | GF
PUBLIC BROADCASTING | PB | SUST | 1295 | Lighting | Two lamp surface wraparound fixtures | Room 112 | 3 | 6 | ea | 2657.564 | 3534.5601 | 0 | 0 | 1981 | 20 | 2001 | Needs upgrade for energy savings |  | GF
PUBLIC BROADCASTING | PB | SUST | 1296 | Lighting | 2x2 parabolic troffers with T-8 U-Tube lamps | Corridor | 3 | 16 | ea | 7086.8372 | 9425.4935 | 0 | 0 | 1981 | 20 | 2001 | Needs upgrade for energy savings |  | GF
PUBLIC BROADCASTING | PB | SUST | 1297 | Lighting | Two lamp surface wraparound fixtures | Outside Portable | 3 | 3 | ea | 1898.26 | 2524.6858 | 0 | 0 | 1981 | 20 | 2001 | Needs upgrade for energy savings |  | GF
PUBLIC BROADCASTING | PB | SUST | 1298 | Lighting | 2 lamp wraparound fixtures without lenses with T-12 Lamps | Mechanical room | 3 | 3 | ea | 1328.782 | 1767.28 | 0 | 0 | 1981 | 20 | 2001 | Needs upgrade for energy savings |  | GF
PUBLIC BROADCASTING | PB | SUST | 1299 | Lighting/Controls | No automatic lighting controls | Building | 3 | 11500 | sf | 21829.9897 | 29033.8863 | 0 | 0 | Unknown |  | 0 | Upgrade for energy savings |  | GF
PEARCE HALL | PE | ARCH | 1300 | Envelope | Windows | Ext. single pane | 4 | 9420 | sf | 655658.9947 | 872026.4629 | 0 | 0 | 1967 | 30 | 1997 | Exterior windows original to windows and need replacement. | 9,417 SF | GF
PEARCE HALL | PE | ARCH | 1301 | Envelope | Exterior Doors | Alum. doors | 3 | 8 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1967 | 30 | 1997 | Exterior alum. doors to be replaced. | some are double doors, 666 SF | GF
PEARCE HALL | PE | ARCH | 1302 | Envelope | Exterior Wall System |  | 3 | 500 | sf | 15818.8331 | 21039.048 | 0 | 0 | 1967 | 30 | 1997 |  | price is for re-tuckpointing 500 sf of exterior wall surface | GF
PEARCE HALL | PE | ARCH | 1303 | Envelope | Roof/Penetrations |  | 3 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 |  |  | GF
PEARCE HALL | PE | ARCH | 1304 | Interior Structure | Partitions | CMU / Brick / Gyp. | 3 | 2500 | sf | 37965.1995 | 50493.7153 | 0 | 0 | 1967 | 40 | 2007 | Corridor walls painted / Exposed Brick / Gypsum painted | price is based off an area of 2500 sf. Price is for removing drywall and replacing it with new, finishing drywall and repainting area | GF
PEARCE HALL | PE | ARCH | 1305 | Interior Structure | Interior Doors | Wood Doors | 3 | 205 | ea | 129714.4315 | 172520.1939 | 0 | 0 | 1967 | 40 | 2007 | Mixture of accessible / not accessible door hardware. Replace 205. |  | GF
PEARCE HALL | PE | ARCH | 1306 | Interior Structure | Stairs | Quarry Tile | 3 | 6000 | sf | 121488.6383 | 161579.8889 | 0 | 0 | 1967 | 40 | 2007 |  | price is for removing existing tile in stairways and replacing it with new quarry tile. | GF
PEARCE HALL | PE | ARCH | 1307 | Interior Structure | Toilet Rooms | Building Lobby | 3 | 820 | sf | 103771.5452 | 138016.1551 | 0 | 0 | 1967 | 40 | 2007 | Toilet rooms near elevators are accessible. | price is for renovating bathrooms on 1st floor only | GF
PEARCE HALL | PE | ARCH | 1308 | Floor Finishes | resilient tile | Corridors | 3 | 18949 | sf | 119900.4274 | 159467.5685 | 0 | 0 | Unknown | 15 | 15 |  |  | GF
PEARCE HALL | PE | ARCH | 1309 | Wall Finishes | Wall panels | Computer Room 205 | 4 | 1338 | sf | 22858.8466 | 30402.266 | 0 | 0 | Unknown | 10 | 10 | Remove asbestos panels from walls. Renovate walls. |  | GF
PEARCE HALL | PE | ARCH | 1310 | Conveying Systems | Elevator - Cab Finishes | passenger/2500lb | 3 | 2 |  | 88585.4654 | 117818.669 | 0 | 0 | 1967 | 30 | 1997 | Passenger elevators 2500 lb. Finishes worn. | Price is for updating finishes only | GF
PEARCE HALL | PE | ARCH | 1311 | Conveying Systems | duplex modernization | passenger/2500lb | 1 | 2 | total | 0 | 0 | 0 | 0 | 1967 | 30 | 1997 | Otis recommendation for 2013 |  | GF | 654192 | 2015-08-21 | 182770 | cylinder replacement and modification combined in one project.
PEARCE HALL | PE | ARCH | 1312 | Conveying Systems | duplex cylinder replacement | passenger/2500lb | 1 | 2 | total | 0 | 0 | 0 | 0 | 1967 | 30 | 1997 | Otis recommendation for 2013 |  | GF | 654192 | 2015-08-21 | 182770 | cylinder replacement and modification combined in one project.
PEARCE HALL | PE | EH&S | 1313 | Evironmental Health & Safety | Asbestos abatement | allowance for arch items | 4 | 1338 | SF | 88872.7354 | 118200.7381 | 0 | 0 | 1967 |  | 1967 | wall finish panels and flooring, work related to elevator |  | GF
PEARCE HALL | PE | MECH | 1314 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-1/Basement Mech. Rm. | 3 | 3600 | cfm | 45558.2394 | 60592.4583 | 0 | 0 | 1967 | 30 | 1997 | Replace reaching end of useful life |  | GF
PEARCE HALL | PE | MECH | 1315 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-2/Basement Mech. Rm. | 3 | 3600 | cfm | 45558.2394 | 60592.4583 | 0 | 0 | 1967 | 30 | 1997 | Replace reaching end of useful life |  | GF
PEARCE HALL | PE | MECH | 1316 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-3/Basement Mech. Rm. | 3 | 3600 | cfm | 45558.2394 | 60592.4583 | 0 | 0 | 1967 | 30 | 1997 | Replace reaching end of useful life |  | GF
PEARCE HALL | PE | MECH | 1317 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-5/Rm. 008 | 3 | 8000 | cfm | 101240.5319 | 134649.9074 | 0 | 0 | 1967 | 30 | 1997 | Replace reaching end of useful life |  | GF
PEARCE HALL | PE | MECH | 1318 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-6/Rm. 008 | 3 | 8000 | cfm | 101240.5319 | 134649.9074 | 0 | 0 | 1967 | 30 | 1997 | Replace reaching end of useful life |  | GF
PEARCE HALL | PE | MECH | 1319 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-7/Mech. Rm. Under Restrooms | 3 | 8000 | cfm | 101240.5319 | 134649.9074 | 0 | 0 | 1967 | 30 | 1997 | Replace reaching end of useful life |  | GF
PEARCE HALL | PE | MECH | 1320 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-8/Mech. Rm. Under Restrooms | 3 | 8000 | cfm | 101240.5319 | 134649.9074 | 0 | 0 | 1967 | 30 | 1997 | Replace reaching end of useful life |  | GF
PEARCE HALL | PE | MECH | 1321 | Chilled Water System | Pumps | System/Rm. 008 | 3 | 4 | ea | 101240.5319 | 134649.9074 | 0 | 0 | 1967 | 20 | 1987 | Replace reaching end of useful life | price is for replacing 4 pumps with new base mounted VFD pumps | GF
PEARCE HALL | PE | MECH | 1322 | Chilled Water System | Piping | Entire system | 3 | 114849 | sf | 719443.7568 | 956860.1966 | 0 | 0 | 1967 | 40 | 2007 | Replace reaching end of useful life, failures reported |  | GF
PEARCE HALL | PE | MECH | 1323 | Chilled Water System | Insulation | Entire system | 3 | 114849 | sf | 174410.6077 | 231966.1083 | 0 | 0 | 1967 |  | 1967 | Replace with system |  | GF
PEARCE HALL | PE | MECH | 1324 | Heating Water System | Pumps | System/Rm. 008 | 3 | 5 | ea | 126550.6649 | 168312.3843 | 0 | 0 | 1967 | 20 | 1987 | Good condition, no reported problems | price is to replace 5 existing pumps with base mounted VFD pumps and connect to existing piping | GF
PEARCE HALL | PE | MECH | 1325 | Heating Water System | Piping | Entire system | 3 | 114849 | sf | 1206340.0367 | 1604432.2488 | 0 | 0 | 1967 | 40 | 2007 | Replace reaching end of useful life, failures reported | Price is for replacing existing heating water pipes | GF
PEARCE HALL | PE | MECH | 1326 | Heating Water System | Insulation | Entire system | 3 | 114849 | sf | 174410.6077 | 231966.1083 | 0 | 0 | 1967 |  | 1967 | Replace with system | Price is for replacing insulation for hot water piping | GF
PEARCE HALL | PE | MECH | 1327 | Building Management | HVAC Control | Pneumatic | 3 | 114849 | sf | 581368.6924 | 773220.3609 | 0 | 0 | 1967 | 25 | 1992 | Replace reaching end of useful life | price is for replacing existing controls with new DDC controls | GF
PEARCE HALL | PE | MECH | 1328 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 114849 | sf | 363355.4327 | 483262.7255 | 0 | 0 | 1967 | 40 | 2007 | Continue replacement of cast iron pipe, quantity unknown | Price is for replacing drainage pipe for the building with new | GF
PEARCE HALL | PE | MECH | 1329 | Storm/Sanitary sewer system | Sump pumps | Mech. Rm. Under Restrooms | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown | 10 | 10 | Replace as Precautionary measure | price is for replacing 1 sump pump with a new unit. | GF
PEARCE HALL | PE | MECH | 1330 | Fire protection system | Piping | Rm. 008 | 4 | 114849 | sf | 726710.8655 | 966525.4511 | 0 | 0 | 1967 | 40 | 2007 | Replace reaching end of useful life, failures reported | Prive is for replace the fire protection piping in the building | GF
PEARCE HALL | PE | MECH | 1331 | Natural gas piping system | Piping | N. Exterior | 3 | 1 | ea | 63275.3324 | 84156.1921 | 0 | 0 | 1972 | 40 | 2012 | Remove no longer used | $50000 is a rough budget. Further clarification is needed to updated pricing | GF
PEARCE HALL | PE | EH&S | 1332 | Environmental Health & Safety | Asbestos abatement | Allowance for mech items | 3 | 114849 | sf | 581368.6924 | 773220.3609 | 0 | 0 | 1967 |  | 1967 |  |  | GF
PEARCE HALL | PE | ELEC | 1333 | Branch Circuit | Unmarked Square D Panel | Room 012 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Bad retrofit job |  | GF
PEARCE HALL | PE | ELEC | 1334 | Branch Circuit | Unmarked GE Panel | Room 008 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1335 | Branch Circuit | Panel DLPE | Room 008 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1336 | Branch Circuit | Panel BB | Room 008 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1337 | Branch Circuit | Panel DLPD | Room 008 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1338 | Branch Circuit | Panel 1D | 1st floor corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1339 | Branch Circuit | Unmarked GE Panel | Room 128 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1340 | Branch Circuit | Unmarked GE Panel | Room 129 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1341 | Branch Circuit | Unmarked GE Panel | 1st floor corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1342 | Distribution | Lighting Distribution panel B | Central mech.Room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1343 | Branch Circuit | Power Panel B | Central mech.Room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1344 | Branch Circuit | Unmarked GE Panel | 1st floor corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1345 | Branch Circuit | Unmarked GE Panel | S.Central corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1346 | Branch Circuit | Unmarked GE Panel | 2nd floor corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1347 | Branch Circuit | Unmarked GE Panel | 2nd floor corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1348 | Branch Circuit | Unmarked GE Panel | 2nd floor corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1349 | Branch Circuit | Panel LP13D | By room 324A | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1350 | Branch Circuit | Unmarked GE Panel | By room 328 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1351 | Branch Circuit | Unmarked GE Panel | By room 304 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1352 | Branch Circuit | Unmarked GE Panel | By Room 403 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1353 | Branch Circuit | Unmarked GE Panel | By room 419 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Needs Upgrade |  | GF
PEARCE HALL | PE | ELEC | 1354 | Lighting | 2x4 troffer | 1st floor corridor | 3 | 44 | ea | 19488.8024 | 25920.1072 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
PEARCE HALL | PE | ELEC | 1355 | Lighting | 2x4 troffer | 1st floor classrooms | 3 | 171 | ea | 75740.5729 | 100734.962 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
PEARCE HALL | PE | ELEC | 1356 | Lighting | 2x4 troffer | 2nd floor corridor | 3 | 44 | ea | 19488.8024 | 25920.1072 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
PEARCE HALL | PE | ELEC | 1357 | Lighting | 2x4 troffer | 2nd floor classrooms | 3 | 221 | ea | 97886.9393 | 130189.6292 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
PEARCE HALL | PE | ELEC | 1358 | Lighting | 2x4 troffer | 3rd floor corridor | 3 | 44 | ea | 19488.8024 | 25920.1072 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
PEARCE HALL | PE | ELEC | 1359 | Lighting | 2x4 troffer | 3rd floor classrooms | 3 | 204 | ea | 90357.1747 | 120175.0424 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
PEARCE HALL | PE | ELEC | 1360 | Lighting | 2x4 troffer | 4th floor corridors | 3 | 44 | ea | 19488.8024 | 25920.1072 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
PEARCE HALL | PE | ELEC | 1361 | Lighting | 2x4 troffer | 4th floor classrooms | 3 | 219 | ea | 97001.0846 | 129011.4425 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
PEARCE HALL | PE |  | 1362 | Lighting | Occupancy sensors | corridors and classrooms | 3 | 114849 | sf | 145342.1731 | 193305.0902 | 0 | 0 | Unknown |  | 0 | Good Condition |  | GF
PEARCE HALL | PE | ELEC | 1363 | Lighting | 12x12 recessed | Exterior | 3 | 16 | ea | 10124.0532 | 13464.9907 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
PEARCE HALL | PE | LSAF | 1364 | Life Safety | Egress Lighting | BLd. | 4 | 60 | ea | 37965.1995 | 50493.7153 | 0 | 0 | Unknown | 20 | 20 | No visible egress lighting |  | GF
PEARCE HALL | PE | LSAF | 1365 | Life Safety | Simplex Fire Alarm | Panel | 3 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | Unknown |  | 0 | Needs upgrade with renovation | Price is for new main panel | GF
PEARCE HALL | PE | LSAF | 1366 | Life Safety | Area of Refuge | Allowance | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 |  |  | GF
CENTRAL ENERGY FACILITY | PH | ARCH | 1367 | Envelope | Windows | Exterior Office | 3 | 275 | ea | 1044.043 | 1388.5772 | 0 | 0 | 1985 | 30 | 2015 | All exterior windows need to be caulked in office area |  | GF
CENTRAL ENERGY FACILITY | PH | ARCH | 1368 | Envelope | Exterior Doors | Entry Doors | 3 | 2 | ea | 27841.1463 | 37028.7245 | 0 | 0 | 1985 | 30 | 2015 | Replace exterior alum. doors, add accessible opener. | Price is for replacing 2 entry doors and adding automatic openers to each door | GF
CENTRAL ENERGY FACILITY | PH | ARCH | 1369 | Interior Structure | Partitions | CMU / Drywall | 3 |  |  | 0 | 0 | 0 | 0 | 1961 | 40 | 2001 | Repair drywall cracks at windows in office area. Seal windows. |  | GF
CENTRAL ENERGY FACILITY | PH | ARCH | 1370 | Floor Finishes | Tile |  | 3 | 4663 | sf | 88515.8625 | 117726.0972 | 0 | 0 | 1961 | 40 | 2001 | In 1961 building, tile is old and worn. |  | GF
CENTRAL ENERGY FACILITY | PH | EH&S | 1371 | Environmental Health & Safety | asbestos abatement |  | 3 | 4663 | sf | 60716.478 | 80752.9157 | 0 | 0 | 1961 |  | 1961 |  |  | GF
CENTRAL ENERGY FACILITY | PH | MECH | 1372 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-1/N. Mezzanine | 3 | 2700 | cfm | 34168.6795 | 45444.3438 | 0 | 0 | 1984 | 30 | 2014 | Good condition, no reported problems |  | GF
CENTRAL ENERGY FACILITY | PH | MECH | 1373 | Ventilation/Terminal Units | Terminal units | Steam Unit Heaters/Various | 3 | 4 | ea | 15186.0798 | 20197.4861 | 0 | 0 | 1961 | 25 | 1986 | Good condition, no reported problems |  | GF
CENTRAL ENERGY FACILITY | PH | MECH | 1374 | Heating Water System | Pumps | Entire system/Basement | 3 | 1 | ea | 5694.7799 | 6719.8403 | 0 | 0 | 1961 | 20 | 1981 | Good condition, no reported problems | Price is for 1 in line circulating pump | GF
CENTRAL ENERGY FACILITY | PH | MECH | 1375 | Heating Water System | Insulation | Entire system | 3 | 65000 | sf | 98709.5186 | 131283.6597 | 0 | 0 | 1961 |  | 1961 | Good condition, no reported problems |  | GF
CENTRAL ENERGY FACILITY | PH | MECH | 1376 | Building Management | HVAC Control | Pneumatic & DDC | 3 | 65000 | sf | 329031.7287 | 437612.1991 | 0 | 0 | 1984 | 25 | 2009 | Good condition, no reported problems | This number may need to be adjusted if controls only need to serve the office area. Price is based on total building SF. | GF
CENTRAL ENERGY FACILITY | PH | MECH | 1377 | Storm/Sanitary sewer system | Piping | Entire building | 4 | 65000 | sf | 205644.8304 | 273507.6244 | 0 | 0 | 1961 | 40 | 2001 | Replace drainage piping with suitable material for this boiler room application |  | GF
CENTRAL ENERGY FACILITY | PH | MECH | 1378 | Storm/Sanitary sewer system | Sump pumps | Basement | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | unknown | 10 | 10 | Replace as a precautionary measure |  | GF
CENTRAL ENERGY FACILITY | PH | MECH | 1379 | Domestic cold water system | Piping | Entire building | 3 | 65000 | sf | 205644.8304 | 273507.6244 | 0 | 0 | 1961 | 40 | 2001 | Replace 100% of domestic system not to include boiler or chiller system water makeup |  | GF
CENTRAL ENERGY FACILITY | PH | MECH | 1380 | Domestic hot water system | Piping | Entire building | 3 | 65000 | sf | 205644.8304 | 273507.6244 | 0 | 0 | 1961 | 40 | 2001 | Replace 100% of domestic system |  | GF
CENTRAL ENERGY FACILITY | PH | ELEC | 1381 | Branch Circuit | Panel B | Room 002 Westinghouse | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1961 | 40 | 2001 | Needs Upgrade |  | GF
CENTRAL ENERGY FACILITY | PH | LSAF | 1382 | Life Safety | Emergency Lighting | Office area Battery Wallpacks | 3 | 10 | ea | 6327.5332 | 8415.6192 | 0 | 0 | Unknown |  | 0 |  |  | GF
CENTRAL ENERGY FACILITY | PH | ELEC | 1383 | Lighting | HPS Wallpacks | Exterior walls | 4 | 6 | ea | 3796.5199 | 5049.3715 | 0 | 0 | Unknown |  | 0 | Needs upgrade |  | GF
BOHANNON POOR MUSEUM | PM | ELEC | 1384 | Service | 100 A. Meter socket | Exterior | 4 | 1 | 1 | 10124.0532 | 13464.9907 | 0 | 0 | 1970 | 40 | 2010 | Past its life | includes replacement of socket only | GF
BOHANNON POOR MUSEUM | PM | ELEC | 1385 | Service | 100 A. Discconnect | Exterior | 4 | 1 | 1 | 10124.0532 | 13464.9907 | 0 | 0 | 1970 | 40 | 2010 | Past its life | includes replacement of dissconnect | GF
BOHANNON POOR MUSEUM | PM | ELEC | 1386 | Distribution | 100 A. QO panel | Front entrance | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | Past its life | includes replacement of panel and reusing feeders | GF
BOHANNON POOR MUSEUM | PM | ELEC | 1387 | Lighting | Wallpack | Front entrance | 4 | 1 | 1 | 632.7533 | 841.5619 | 0 | 0 | 1970 | 30 | 2000 | Past its life | replace wallpack only | GF
BOHANNON POOR MUSEUM | PM | ELEC | 1388 | Lighting | Postlight | Exterior | 4 | 1 | 1 | 632.7533 | 841.5619 | 0 | 0 | 1970 | 30 | 2000 | Past its life | replace postlight | GF
POWERS HALL | PO | ARCH | 1389 | Envelope | Windows | Building Exterior | 3 | 124 | ea | 123969.0313 | 164878.8116 | 0 | 0 | 1992 | 30 | 2022 | Windows updated within last 20 years. | Price is for replacing existing windows with new aluminum framed windows, new caulk, and minor finish patch around new windows | GF
POWERS HALL | PO | ARCH | 1390 | Envelope | Exterior Doors | Building Entrances | 3 | 11 | ea | 69602.8657 | 92571.8114 | 0 | 0 | 1960 | 30 | 1990 | Exterior doors to be replaced with new alum. doors to match new standard. | Price is for removing existing doors and replacing them with new aluminum entry doors. | GF
POWERS HALL | PO | ARCH | 1391 | Envelope | Exterior Walls | Brick | 3 | 1000 | sf | 31637.6662 | 42078.0961 | 0 | 0 | 1939 | 100 | 2039 | Brick in good condition but needs tuck pointing in areas and limestone repair. | Price is for tuckpointing existing brick | GF
POWERS HALL | PO | ARCH | 1392 | Envelope | Roof | Roof Areas 1A and 2 | 1 | 10041 | sf | 0 | 0 | 0 | 0 | 1998 | 15 | 2013 | Roof areas 1A and 2 are scheduled for replacement. |  | GF | 654291 | 2014-08-01 | 147840.38
POWERS HALL | PO | ARCH | 1393 | Envelope | Roof | Music Sec. #1 | 1 | 5962 | sf | 0 | 0 | 0 | 0 | Unknown | 30 | 30 | Roof Area is in need of major repair. |  | GF | 654043 | 2012-08-01 | 70368.35
POWERS HALL | PO | ARCH | 1394 | Envelope | Roof Gutter and flashing | Perimeter of Building | 4 | 900 | lf | 28473.8996 | 37870.2865 | 0 | 0 | Unknown | 30 | 30 |  | Write up says to remove tar for gutters and flashings at perimeter | GF
POWERS HALL | PO | ARCH | 1395 | Envelope | Roof | Walkway Canopy to Barnes | 4 | 105 | sf | 6643.9099 | 8836.4002 | 0 | 0 | Unknown | 30 | 30 |  | Price is for replacement of the canopy | GF
POWERS HALL | PO | ARCH | 1396 | Interior Structure | Toilet Rooms |  | 3 | 830 | sf | 105037.0518 | 139699.2789 | 0 | 0 | 1939 | 40 | 1979 | Finishes are original. | I added the total SF of the gang toilet rooms for both floors | GF
POWERS HALL | PO | ARCH | 1397 | Floor Finish | Marble floor | Entrance / Corridors | 3 | 2400 | sf | 75930.3989 | 100987.4306 | 0 | 0 | 1939 | 80 | 2019 | Original 1939 marble floor to be replaced. | Price is for removing old marble floor and replacing it with new | GF
POWERS HALL | PO | ARCH | 1398 | Floor Finish | Composite Tile | Corridor on 2nd Floor | 3 | 2,400 /2 fl | sf | 24297.7277 | 32315.9778 | 0 | 0 | 1960 | 15 | 1975 | Corridor tile in need of replacement. | price is for removing existing floor and replacing it with new VCT | GF
POWERS HALL | PO | ARCH | 1399 | Floor Finish | Entire First Floor |  | 4 | 17130 | sf | 108390.6445 | 144159.5571 | 0 | 0 | Unknown | 40 | 40 |  |  | GF
POWERS HALL | PO | ARCH | 1400 | Ceiling Finish | Acoustical Tile | Interior Corridors | 3 | 2,400 / 3 fl | sf | 41002.4154 | 54533.2125 | 0 | 0 | 1960 | 20 | 1980 | Corridor ceilings replaced with 2' x 2' lay-in ceiling tile. | price is for replacing existing ceiling with new ACT system | GF
POWERS HALL | PO | ARCH | 1401 | Ceiling Finish | Acoustical Tile | Lobby | 4 | 2460 | sf | 14009.1586 | 18632.1809 | 0 | 0 | Unknown | 20 | 20 | Replace Lobby Ceiling | price is for replacing existing ceiling with new ACT system | GF
POWERS HALL | PO | ARCH | 1402 | Ceiling Finish | Plaster replacement | Various | 4 | 250 | sf | 26892.0163 | 35766.3817 | 0 | 0 | Unknown | 20 | 20 |  | Corridor plaster quantity per Arch. Email from 11-6-12 | GF
POWERS HALL | PO | ARCH | 1403 | Ceiling Finish | Plaster replacement | Ballroom 243 | 4 | 400 | sf | 43027.2261 | 57226.2107 | 0 | 0 | Unknown | 20 | 20 |  | Assuming Approx 10% replacement | GF
POWERS HALL | PO | ADAC | 1404 | BF/ADA Compliance | Exterior Doors | Building Exterior | 3 | 11 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1954 | 30 | 1984 | Provide power assist operator. | Price is for adding 1 automatic door operator at each entry | GF
POWERS HALL | PO | ADAC | 1405 | BF/ADA Compliance | Interior Doors | Offices / Classrooms | 3 | 137 | ea | 86687.2054 | 115293.9832 | 0 | 0 | Unknown |  | 0 | Classroom hardware is knob-style. | price is for replacing existing door hardware with ADA accessible hardware | GF
POWERS HALL | PO | EH&S | 1406 | Environmental Health & Safety | Asbestos abatement | Allowance for arch items | 3 |  |  | 109339.7744 | 145421.9 | 0 | 0 | 1960 |  | 1960 |  |  | GF
POWERS HALL | PO | MECH | 1407 | Ventilation/Terminal Units | AHU/Steam Heat | AHU-1, Penthouse | 4 | 10800 | cfm | 136674.7181 | 181777.375 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life | Unit information was taken off of sheet M-3 dated 11-14-60. Price is for removing old unit and replacing it with the same capacity unit. | GF
POWERS HALL | PO | MECH | 1408 | Ventilation/Terminal Units | Terminal units | Finned tube radiation, Entire Bldg. | 4 | 1480 | lf | 524425.9552 | 697486.5204 | 0 | 0 | 1960 | 25 | 1985 | Replace nearing end of useful life | Quantity based on engineers comments in 11-7-12 email. | GF
POWERS HALL | PO | MECH | 1409 | Steam System | Insulation | Entire system | 3 | 39250 | sf | 59605.3632 | 79275.133 | 0 | 0 | 1960 |  | 1960 | Evaluate older pipe insulation for possible replacement | Need to verify quantity . Building mechanical from Barns Kitchen and Barns Hall as mixture of heating water and steam. | GF
POWERS HALL | PO | MECH | 1410 | Steam System | Piping | Entire building | 3 | 39250 | sf | 149013.4079 | 198187.8325 | 0 | 0 | 1960 | 50 | 2010 | Replace nearing end of useful life | Need to verify quantity . Building mechanical from Barns Kitchen and Barns Hall as mixture of heating water and steam. piping | GF
POWERS HALL | PO | MECH | 1411 | Building Management | HVAC Control | Hybrid and straight pneumatic | 4 | 39250 | sf | 198684.5438 | 264250.4433 | 0 | 0 | Unknown | 20 | 20 | Replace with DDC system | Price is for replacing existing controls with DDC system | GF
POWERS HALL | PO | MECH | 1412 | Storm/Sanitary Sewer System | Piping | Entire building | 3 | 39250 | sf | 124177.8399 | 165156.5271 | 0 | 0 | 1939 | 40 | 1979 | Replace with future renovations projects | Price is for removing old piping and replacing it with new pipes | GF
POWERS HALL | PO | MECH | 1413 | Domestic cold water system | Piping | Entire building | 3 | 39250 | sf | 173848.9759 | 231219.1379 | 0 | 0 | 1960 | 40 | 2000 | Appears to be in good condition | Price is for removing old piping and replacing it with new pipes. Some architectural demo and patching/replacement of finishes was included | GF
POWERS HALL | PO | MECH | 1414 | Domestic hot water system | Piping | Entire building | 3 | 39250 | sf | 173848.9759 | 231219.1379 | 0 | 0 | 1939 | 40 | 1979 | Good condition | Price is for removing old piping and replacing it with new pipes. Some architectural demo and patching/replacement of finishes was included | GF
POWERS HALL | PO | EH&S | 1415 | Environmental Health and Safety | Asbestos abatement | Allowance for mech items | 3 | 49565 | sf | 250899.3482 | 333696.1331 | 0 | 0 | 1960 |  | 1960 |  |  | GF
POWERS HALL | PO | ELEC | 1416 | Ice melt equipment | Ice melt equipment | Room A - 2nd Floor | 3 | 1 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 2000 | 40 | 2040 | 1 of 3 not working |  | GF
POWERS HALL | PO | LSAF | 1417 | Life Safety | Fire Alarm | Room 243 | 3 | 38900 | sf | 246141.0432 | 327367.5874 | 0 | 0 | 1960 | 40 | 2000 | Does not meet code, replace | price is for installing new fire alarm in the building | GF
POWERS HALL | PO | LSAF | 1418 | Life Safety | Area of Refuge | Allowance | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | GF
POWERS HALL | PO | ELEC | 1419 | Distribution | Panel LP2C | Room 237 | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Obsolete, full, replace |  | GF
POWERS HALL | PO | ELEC | 1420 | Distribution | Panel LP1C |  | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Electrical |  | GF
POWERS HALL | PO | ELEC | 1421 | Distribution | PanelLP1G/Lp1D |  | 5 | 2 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 1967 | 40 | 2007 | Obsolete, full, replace |  | GF
POWERS HALL | PO | LSAF | 1422 | Life Safety | Emergency Lighting | Corridors | 5 | 6650 | sf | 42078.0961 | 55963.8678 | 0 | 0 | 1967 | 15 | 1982 | Does not meet code, replace |  | GF
POWERS HALL | PO | ELEC | 1423 | Lighting | Lighting | 90% of facility | 4 | 35010 | sf | 265832.3266 | 353556.9944 | 0 | 0 | Unknown |  | 0 | Replace/energy savings | price is for replacing existing light fixtures for 90% of the building. | GF
RONAN HALL | RN | ARCH | 1424 | Envelope | Windows | Building Exterior | 4 | 280 | ea | 279930.0707 | 372306.994 | 0 | 0 | 1954 | 30 | 1984 | Windows are broken, failing and require replacement immediately. | price includes removing old windows and replacing with new aluminum framed windows, new caulk and minor finish patch around new windows | GF
RONAN HALL | RN | ARCH | 1425 | Envelope | Exterior Doors | Building Entrances | 3 | 11 | ea | 69602.8657 | 92571.8114 | 0 | 0 | 1954 | 30 | 1984 | Exterior doors to be replaced with new alum. doors to match new standard. | price includes removing old door and replacing them with new aluminum entry doors | GF
RONAN HALL | RN | ARCH | 1426 | Envelope | Exterior Walls | Brick | 3 | 500 | sf | 15818.8331 | 21039.048 | 0 | 0 | 1954 | 100 | 2054 | Brick in good condition but needs tuck pointing in areas. | price is for tuckpointing existing brick wall | GF
RONAN HALL | RN | ARCH | 1427 | Envelope | Roof | Roof Area 4 | 4 | 1599 | sf | 46541.538 | 61900.2456 | 0 | 0 | 1998 | 15 | 2013 | Roof Area #4 is scheduled for immediate replacement. | price includes removing old roof and replacing it with new roof system | GF
RONAN HALL | RN | ARCH | 1428 | Envelope | Foundation |  | 4 | 1348 | sf | 4264.7574 | 5672.1274 | 0 | 0 | 1954 | 100 | 2054 | Waterproofing to be applied to exterior and interior of wall. Check drainage. | exterior | GF
RONAN HALL | RN | ARCH | 1429 | Interior Structure | Toilet Rooms | All | 3 | 947 | sf | 47937.3919 | 63756.7312 | 0 | 0 | 1954 | 40 | 1994 | Finishes are original. | Price is for removing and replacing existing finishes | GF
RONAN HALL | RN | ARCH | 1430 | Interior Structure | Interior Walls | Lower Level Interior | 5 | 1178 | lf | 126715.1807 | 168531.1904 | 0 | 0 | 1954 | 40 | 1994 | Lower level walls to be demolished and rebuilt if lower level is to be used. | Demo & Replace | GF
RONAN HALL | RN | ARCH | 1431 | Floor Finish | Carpet | First Floor / Lower Level | 5 | 1811 | sf | 12605.079 | 16764.755 | 0 | 0 | Unknown | 15 | 15 | Carpet to be replaced. | Qty is for removal according to the 2011 demo plan. Didn't find new carpet locations for replacement quantities | GF
RONAN HALL | RN | ARCH | 1432 | Ceiling Finish | Acoustical Tile | Lower Level Rooms | 5 | 15855 | sf | 90290.7356 | 120086.6784 | 0 | 0 | 1954 | 20 | 1974 | Ceiling needs complete replacement if lower level is to be used. | Based on quantity from 2011 dwgs | GF
RONAN HALL | RN | EH&S | 1433 | Environmental Health & Safety | Asbestos Abatement | Allowance for arch finishes | 5 |  |  | 126136.8442 | 167762.0028 | 0 | 0 | 1954 |  | 1954 | includes walls, flooring and ceiling allowances |  | GF
RONAN HALL | RN | ADAC | 1434 | BF/ADA Compliance | Exterior Doors | Building Exterior | 3 |  | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1954 | 30 | 1984 | Exterior doors to be replaced with new alum. doors to match new standard | Price is for 5 new automatic door openers (one at each entry) | GF
RONAN HALL | RN | ADAC | 1435 | BF/ADA Compliance | Interior Doors | Offices / Classrooms | 3 | 124 | ea | 78461.4122 | 104353.6783 | 0 | 0 | Unknown | 40 | 40 | Renovated area have accessible hardware. | Price is for replacing existing door hardware with ADA compliant hardware | GF
RONAN HALL | RN | ADAC | 1436 | BF/ADA Compliance | Toilet Rooms | Interior | 3 | 947 | sf | 119843.4796 | 159391.8279 | 0 | 0 | 1954 | 40 | 1994 | Toilet rooms do not meet current barrier free requirements. | price is from an earlier estimate we did on the basement toilet rooms. Was part of a larger renovation project we priced earlier in the summer for CMU | GF
RONAN HALL | RN | MECH | 1437 | Ventilation/Terminal Units | AHU/Split DX/Steam Heat | AHU-1, South basement | 4 | 15 | Tons | 66439.0991 | 88364.0017 | 0 | 0 | 1954 | 30 | 1984 | Replace with unit properly sized to load requirements | price is for replacing existing unit with a new one of the same capacity | GF
RONAN HALL | RN | MECH | 1438 | Ventilation/Terminal Units | Terminal units | Steam fin tube radiation, Basement | 4 | 68 | lf | 24095.2466 | 32046.678 | 0 | 0 | 1954 | 25 | 1979 | Replace nearing end of useful life |  | GF
RONAN HALL | RN | MECH | 1439 | Ventilation/Terminal Units | Unit Vent/Chilled Cool/Steam Heat | Basement level rooms | 3 | 3 | ea | 58846.0592 | 78265.2587 | 0 | 0 | 1954 | 20 | 1974 | Replace nearing end of useful life |  | GF
RONAN HALL | RN | MECH | 1440 | Steam System | Piping, Basement level | Basement level rooms | 4 |  |  | 0 | 0 | 0 | 0 | 1954 | 50 | 2004 | Replace nearing end of useful life | Prices are for replacing existing piping in basement only. (See breakout below) | GF
RONAN HALL | RN | MECH | 1441 | Steam System |  | Steam 3"-6" | 4 | 2114 | lf | 56938.9406 | 75728.7911 | 0 | 0 | 1954 |  | 1954 |  |  | GF
RONAN HALL | RN | MECH | 1442 | Steam System |  | Chilled Water | 4 | 2114 | lf | 27894.2976 | 37099.4157 | 0 | 0 | 1954 |  | 1954 |  |  | GF
RONAN HALL | RN | MECH | 1443 | Steam System |  | Condensate Return 3" | 4 | 2114 | lf | 39539.4897 | 52587.5213 | 0 | 0 | 1954 |  | 1954 |  |  | GF
RONAN HALL | RN | MECH | 1444 | Steam System |  | Hot water Return 1" | 4 | 358 | lf | 10832.7369 | 14407.5401 | 0 | 0 | 1954 |  | 1954 |  |  | GF
RONAN HALL | RN | MECH | 1445 | Building Management | HVAC Control | Hot Water 1.5" | 4 | 323 | lf | 14715.3113 | 19571.364 | 0 | 0 | 2009 | 20 | 2029 | Good condition |  | GF
RONAN HALL | RN | MECH | 1446 | Building Management | HVAC Control | Pneumatic | 4 | 60000 | sf | 303721.5957 | 403949.7223 | 0 | 0 | 1954 | 20 | 1974 | Replace with DDC system | Price is for replacing existing pneumatic controls with new DDC controls | GF
RONAN HALL | RN | MECH | 1447 | Storm/Sanitary Sewer System | Piping | Entire building | 3 | 1391 | lf | 44007.9937 | 58530.6316 | 0 | 0 | 1954 | 40 | 1994 | Replace remaining older piping | price is for replacing existing storm/sanitary piping only. No architectural finishes are included | GF
RONAN HALL | RN | EH&S | 1448 | Environmental Health & Safety | asbestos abatement | pipe insulation | 4 | 6700 | lf | 169577.8909 | 225538.5949 | 0 | 0 | 1954 |  | 1954 |  |  | GF
RONAN HALL | RN | MECH | 1449 | Heating | Ice melt equipment | Room A - 2nd Floor | 3 | 1 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 2000 | 40 | 2040 | 1 of 3 not working |  | GF
RONAN HALL | RN | LSAF | 1450 | Life Safety | Fire Alarm | Room 243/ verify room number | 3 | 1 | sf | 6327.5332 | 8415.6192 | 0 | 0 | 1960 | 40 | 2000 | Grandfathered, recommend replacement | Is this item the main panel only? Price is for replacing main fire alarm panel | GF
RONAN HALL | RN | LSAF | 1451 | Life Safety | Area of Refuge | Allowance | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | GF
RONAN HALL | RN | ELEC | 1452 | Distribution | Panel LP2C | Room 237/ verify room number | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Obsolete, full, replace |  | GF
RONAN HALL | RN | ELEC | 1453 | Distribution | Panel LP1C |  | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1967 | 40 | 2007 | Electrical |  | GF
RONAN HALL | RN | ELEC | 1454 | Distribution | PanelLP1G/Lp1D |  | 4 | 2 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 1967 | 40 | 2007 | Obsolete, full, replace |  | GF
RONAN HALL | RN | LSAF | 1455 | Life Safety | Emergency Lighting | Corridors/ FF & SF | 4 | 20 | ea | 12655.0665 | 16831.2384 | 0 | 0 | 1967 | 15 | 1982 | Grandfathered, recommend replacement | FF & SF | GF
RONAN HALL | RN | ELEC | 1456 | Lighting | Lighting | 90% of facility | 3 | 54000 | sf | 136674.7181 | 181777.375 | 0 | 0 | Unknown | 20 | 20 | Replace/energy savings | Price is for replacing about 300 lights. Building has gone through a major renovation recently does 90% of light fixture still need to be replaced? | GF
ROSE RYAN | RO | MECH | 1457 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-1A/124 | 3 | 8200 | cfm | 103771.5452 | 138016.1551 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1458 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-2A/124 | 3 | 7200 | cfm | 91116.4787 | 121184.9167 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1459 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-1D/144 | 3 | 9500 | cfm | 120223.1316 | 159896.7651 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1460 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-4D/144 | 3 | 15450 | cfm | 195520.7772 | 260042.6337 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1461 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-8A/018 | 3 | 9000 | cfm | 113895.5984 | 151481.1458 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1462 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-8F/018 | 3 | 9000 | cfm | 113895.5984 | 151481.1458 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1463 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-11B/130A | 3 | 28000 | cfm | 354341.8616 | 471274.676 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1464 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-11D/144 | 3 | 40850 | cfm | 516959.466 | 687556.0898 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1465 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-13C/144 | 3 | 4965 | cfm | 62832.4051 | 83567.0988 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1466 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-17B/124 | 3 | 9000 | cfm | 113895.5984 | 151481.1458 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1467 | Ventilation/Terminal Units | AHU/DX Cool/HW Heat | AHU-20C/124 | 3 | 2.5 | Tons | 14236.9498 | 18935.1432 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers and condensing unit |  | GF
ROSE RYAN | RO | MECH | 1468 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-39A/124 | 3 | 9000 | cfm | 113895.5984 | 151481.1458 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1469 | Ventilation/Terminal Units | AHU/No Cool/HW Heat | AHU-40A/124 | 3 | 10000 | cfm | 126550.6649 | 168312.3843 | 0 | 0 | 1973 | 30 | 2003 | Replace economizer dampers |  | GF
ROSE RYAN | RO | MECH | 1470 | C Store Location |  |  | 3 |  |  | 0 | 0 | 0 | 0 | Unknown | 20 | 20 | The cooling needs of this area should be evaluated along with the feasibility of installing a dedicated system serving only the C Store. |  | GF
ROSE RYAN | RO | MECH | 1471 | C Store Location | Terminal units | HW Cabinet Heater/Entrances | 3 | 3 | ea | 15945.3838 | 21207.3604 | 0 | 0 | 1973 | 20 | 1993 | Good condition, no reported problems |  | GF
ROSE RYAN | RO | MECH | 1472 | Storm/Sanitary sewer system | Lift pumps | Rooms 6 and 070 | 3 | 2 | ea | 45558.2394 | 60592.4583 | 0 | 0 | 1973 | 10 | 1983 | Replace as a precautionary measure |  | GF
ROSE RYAN | RO | MECH | 1473 | Domestic cold water system | Piping | Entire building | 3 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | unknown | 40 | 40 | Good condition, no reported problems. Add boost pumps | price is for adding a system booster pump | GF
ROSE RYAN | RO | MECH | 1474 | Domestic hot water system | Heater/Steam | Entire building/Pool mechanical room | 3 | 1 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 1973 | 24 | 1997 | Evauate building needs, replace heater and install mixing valve for scald protection. | price is for replacing water heater | GF
ROSE RYAN | RO | MECH | 1475 | Fire protection system | Piping | Booster Pump | 3 |  |  | 0 | 0 | 0 | 0 | 1973 | 40 | 2013 | Good condition, no reported problems. Investigate the necessity of a system booster pump. | anything to price? | GF
ROSE RYAN | RO | ELEC | 1476 | Distribution | Panel F General Electric - 1972 | Room 013 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1477 | Distribution | Panel L General Electric - 1972 | Room 013 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1478 | Branch Circuit Condition | Panel LL | Room 013 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1479 | Branch Circuit Condition | Panel R | Room 018 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1480 | Branch Circuit Condition | Different Panel F | Room 018 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1481 | Branch Circuit Condition | Unlabeled General Electric Motor Control Center | Pool water treatment room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1482 | Branch Circuit Condition | Panel EC | Custodial closet | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1483 | Branch Circuit Condition | Panel MSPD | Room 144 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1484 | Branch Circuit Condition | Panel EE | Room 144 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1485 | Branch Circuit Condition | Panel E | Room 144 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1486 | Branch Circuit Condition | Panel MSPDD | Room 144 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1487 | Branch Circuit Condition | Panel D | Room 139 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1488 | Branch Circuit Condition | Panel DD | Room 139 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1489 | Branch Circuit Condition | Panel MSPA | Room 127B | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1490 | Branch Circuit Condition | Panel-B | Room 128 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1491 | Branch Circuit Condition | Panel B | Room 128 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1492 | Branch Circuit Condition | Panel BB | Room 128 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1493 | Branch Circuit Condition | Panel B | Room 127D | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1494 | Branch Circuit Condition | Different Panel MSPA | Room 127D | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1972 | 40 | 2012 | Needs Upgrade |  | GF
ROSE RYAN | RO | ELEC | 1495 | Lighting | 4 foot, 2 lamp, surface fixtures with eggcrate diffusers | Basement passages | 3 | 22 | ea | 9744.4012 | 12960.0536 | 0 | 0 | Unknown | 20 | 20 | Could be upgraded for better output and energy savings |  | GF
ROSE RYAN | RO | ELEC | 1496 | Lighting | 4 foot, 2 lamp surface mounted wraparound fixtures | room 134 | 3 | 18 | 1 | 7972.6919 | 10603.6802 | 0 | 0 | Unknown | 20 | 20 | Could be upgraded for better output and energy savings |  | GF
ROSE RYAN | RO | ELEC | 1497 | Lighting | 2x4, 2 lamp flourescent troffers with acrylic lenses | offices | 3 | 54 | 1 | 23918.0757 | 31811.0406 | 0 | 0 | Unknown | 20 | 20 | Could be upgraded for better output and energy savings |  | GF
ROSE RYAN | RO | ELEC | 1498 | Lighting | 8 foot T-12 HO fixtures | Room 150 | 3 | 30 | 1 | 30372.1596 | 40394.9722 | 0 | 0 | Unknown | 20 | 20 |  |  | GF
ROSE RYAN | RO | ELEC | 1499 | Lighting | 2x4, 2 lamp flourescent troffers with acrylic lenses | Corridors | 3 | 130 | ea | 57580.5525 | 0 | 0 | 0 | Unknown | 20 | 20 | Could be upgraded for better output and energy savings |  | GF
ROSE RYAN | RO | ELEC | 1500 | Lighting | 4 foot, 2 lamp surface mounted wraparound fixtures | Equipment room | 3 | 8 | ea | 3543.4186 | 4712.7468 | 0 | 0 | Unknown | 20 | 20 | Could be upgraded for better output and energy savings |  | GF
ROSE RYAN | RO | ELEC | 1501 | Lighting | 1000 watt Metal Halaide Wall Wash fixtures (22 of them) | Perimiter walls around pool | 3 | 22 | ea | 41761.7194 | 55543.0868 | 0 | 0 | Unknown | 20 | 20 | Replace for energy savings |  | GF
ROSE RYAN | RO | ELEC | 1502 | Lighting controls | General Electric contactors for pool lights | Pool Mechanical Room | 4 |  |  | 0 | 0 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade | What should be priced for these items? | GF
ROSE RYAN | RO | SUST | 1503 | Lighting/Controls | No visible lighting control |  | 3 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | energy savings |  | GF
ROSE RYAN | RO | LSAF | 1504 | Life Safety | Simplex 4010 Fire Alarm system | Building | 3 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | Unknown | 40 | 40 | Would have to be upgraded with renovation |  | GF
ROSE RYAN | RO | LSAF | 1505 | Life Safety | Emergency Lighting |  | 3 | 40 | ea | 25310.133 | 33662.4769 | 0 | 0 | Unknown | 20 | 20 | only in pool area |  | GF
ROSE RYAN SAC | RO | ARCH | 1506 | Envelope | Windows |  | 4 | 260 | lf | 5062.0266 | 6732.4954 | 0 | 0 | 1973/1990 | 30 | 30 | Re-caulk windows. Glass in good condition. | Price is for 2 people, 2 days with a lift to recaulk 260 lnft. | GF
ROSE RYAN SAC | RO | ARCH | 1507 | Envelope | Glass block |  | 4 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 1973/1990 | 30 | 30 | Re-caulk glass block at roof area to make watertight. | Price is for 2 people, 3 days and a lift | GF
ROSE RYAN SAC | RO | ARCH | 1508 | Envelope | Exterior Doors |  | 4 | 14 | ea | 88585.4654 | 117818.669 | 0 | 0 | 1973/1990 | 30 | 30 | Replace all exterior doors with new campus standard. Add new actuator. |  | GF
ROSE RYAN SAC | RO | ARCH | 1509 | Envelope | Roof/Penetrations |  | 4 | 17880 | sf | 520426.9542 | 692167.8491 | 0 | 0 | 1973/1990 | 30 | 30 | Roof leaks above gym & pool areas to be examined & damage repaired. |  | GF
ROSE RYAN SAC | RO | ARCH | 1510 | Interior Structure | Interior Doors | Wood& Hollow Met. | 4 | 125 | ea | 79094.1655 | 105195.2402 | 0 | 0 | 1973/1990 | 40 | 40 | 50% have accessible handicap door hardware, 50% of doors do not. Replace non-ADA accessible hardware. |  | GF
ROSE RYAN SAC | RO | ARCH | 1511 | Ceiling Finishes | Lay-in Ceiling Tile |  | 4 | 1 | allw | 632.7533 | 841.5619 | 0 | 0 | 1973/1990 | 20 | 20 | Repair stained ceiling tile @ offices. See Photo A31. |  | GF
ROSE RYAN SAC | RO | ARCH | 1512 | Ceiling Finishes |  |  | 4 |  |  | 0 | 0 | 0 | 0 | 1973/1990 | 20 | 20 | Repair roof leaks from standing seam metal roof. | Has this been fixed - Is this deferred maintenance? | GF
ROSE RYAN SAC | RO | ARCH | 1513 | Ceiling Finishes | Lay-in Ceiling Tile |  | 4 | 1775 | sf | 10108.2344 | 13443.9517 | 0 | 0 | 1973/1990 | 20 | 20 | Replace ceiling tile from entrance to Rose Hall into corrridors. |  | GF
ROSE RYAN SAC | RO | ARCH | 1514 | Fixed Equipment/Furnishings | Pool | Natatorium 131 | 4 |  |  | 0 | 0 | 0 | 0 | 1973/1990 | 40 | 40 | Renovate pool, repair cracking concrete walls, finishes, tile @ apron |  | GF
ROSE RYAN SAC | RO | ADAC | 1515 | BF/ADA Compliance | Interior Door Hardware |  | 3 |  |  | 0 | 0 | 0 | 0 | 1973 | 30 | 2003 | 50% have ADA-accessible door hardware, 50% of doors do not. Replace with ADA-accessible hardware. |  | GF
ROSE RYAN SAC | RO | ADAC | 1516 | BF/ADA Compliance | Pool Access SAC | Pool Lift | 4 | 1 | ea | 12655.0665 | 16831.2384 | 0 | 0 | Unknown |  | 0 | Add a lift allowance to SAC Pool |  | GF
ROSE RYAN SAC | RO | ADAC | 1517 | BF/ADA Compliance | Hot Tub Access SAC | Handrails | 4 | 20 | lf | 1265.5066 | 1683.1238 | 0 | 0 | Unknown |  | 0 | Add rails to SAC hot tub |  | GF
ROSE RYAN SAC | RO | MECH | 1518 | Ventilation/Terminal Units | AHU/DX Cool/HW Heat | AHU Pool Dry-O-Tron/210 | 4 |  |  | 0 | 0 | 0 | 0 | 1988 | 15 | 2003 | Replace unit repeated failures reported. Model # DS 140-43 |  | GF
ROSE RYAN SAC | RO | MECH | 1519 | Heating Water System | Heat Exchanger/Steam | Entire system | 4 |  |  | 0 | 0 | 0 | 0 | 1988 | 25 | 2013 | Replace heat exchangers, head sealing surfaces have failed and are reported in poor condition. (No data plate visible) |  | GF
ROSE RYAN SAC | RO | MECH | 1520 | Building Management | HVAC Control | Pneumatic & DDC | 3 |  |  | 0 | 0 | 0 | 0 | 1988 | 25 | 2013 | Replace air compress and air drier and connect system to central plant air located in Rose Rm. 18. |  | GF
ROSE RYAN SAC | RO | MECH | 1521 | Storm/Sanitary sewer system | Lift pumps | Basement Mech. Rm. 040 | 3 |  |  | 0 | 0 | 0 | 0 | 1988 | 10 | 1998 | Replace as a precautionary measure | hold on OPC; Confirm with CMU. | GF
ROSE RYAN SAC | RO | MECH | 1522 | Domestic cold water system | Piping | Entire building | 1 |  |  | 0 | 0 | 0 | 0 | 1988 | 40 | 2028 | Replace galvanized mains, add boost pump. |  | GF | 654054 | 2013-08-19 | 93468.54
ROSE RYAN SAC | RO | MECH | 1523 | Domestic hot water system | Piping | Entire building | 1 |  |  | 0 | 0 | 0 | 0 | 1988 | 40 | 2028 | Replace galvanized mains. |  | GF | 654054 | 2013-08-19 | See above
ROSE RYAN SAC | RO | SUST | 1524 | Lighting/Controls | Occupancy Sensors | Smaller Rooms | 3 | 50000 | sf | 63275.3324 | 84156.1921 | 0 | 0 | Unknown |  | 0 | Could be upgraded for energy savings | allowance until we get further detail about areas that need to be served | GF
ROSE RYAN SAC | RO | LSAF | 1525 | Life Safety | National Tme Model 7000 Fire Alarm System | Building | 3 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | Unknown | 40 | 40 | Would have to be upgraded with renovation | Price is for replacing main panel | GF
ROWE HALL | RW | ARCH | 1526 | Envelope | Windows | Exterior | 3 | 9760 | sf | 679323.969 | 903500.8788 | 0 | 0 | 1958 | 30 | 1988 |  |  | GF
ROWE HALL | RW | ARCH | 1527 | Envelope | Roof/Penetrations | Asphalt | 3 | 9000 | sf | 261959.8763 | 348406.6355 | 0 | 0 | 2006 | 30 | 2036 | Repairs required over museum area. |  | GF
ROWE HALL | RW | ARCH | 1528 | Envelope | Roof/Penetrations | Roof over Lab | 4 | 1200 | sf | 34927.9835 | 46454.2181 | 0 | 0 | 2006 | 30 | 2036 | Water leaking from Mech. Roof above into Lab, structure damaged. | Price is based off of roof area for Lab room 207 from drawing 7 dated 2/15/57 | GF
ROWE HALL | RW | ARCH | 1529 | Envelope | Roof/Penetrations | Soffits | 4 | 3700 | sf | 23411.873 | 31137.7911 | 0 | 0 | 1958 | 30 | 1988 | Repair water damage to soffits at front of building. | Price is for cleaning and repainting soffit area | GF
ROWE HALL | RW | ARCH | 1530 | Interior Structure | Interior Doors | Classroom | 3 | 115 | ea | 72766.6323 | 96779.621 | 0 | 0 | 1958 | 40 | 1998 | Wood painted doors with wire glass and non-accessible hardware. |  | GF
ROWE HALL | RW | ARCH | 1531 | Interior Structure |  | Stairwell | 3 | 5 | ea | 5062.0266 | 6732.4954 | 0 | 0 | 1958 | 40 | 1998 | Remove hardware on doors to exit stair. | Price is for replacing existing hardware with new ADA compliant hardware and closers | GF
ROWE HALL | RW | ARCH | 1532 | Interior Structure | Elevators | Interior | 3 | 1 | ea | 227791.1968 | 302962.2917 | 0 | 0 | 1976 | 30 | 2006 | Elevator is in need of mechanical repair. 2000 lb. capacity. | price is for replacing elevator | GF
ROWE HALL | RW | ARCH | 1533 | Interior Structure | Ceiling Finishes | Corridor Ceiling | 3 | 8440 | sf | 69425.6947 | 92336.174 | 0 | 0 | 1958 | 20 | 1978 | Corridor ceiling 12" x 12" spline. Fair condition. Replace within 5 years. | Unit cost was increased because of the added demo for the splined ceiling | GF
ROWE HALL | RW | ADAC | 1534 | BF/ADA Compliance | Interior Door Hardware | Classrooms | 3 |  |  | 0 | 0 | 0 | 0 | 1958 | 30 | 1988 | Door hardware is not ADA-accessible. | same as above | GF
ROWE HALL | RW | ADAC | 1535 | BF/ADA Compliance | Interior Door Clearances | Toilet 122 | 1 |  |  | 0 | 0 | 0 | 0 | 1958 | 30 | 1988 | Men 122 interior door not ADA accessible. Other rooms accessible. | same as above | GF | 654090 | 2014-04-01 | 132098.49 | This project was completed together with project #'s 1546,1547,1548
ROWE HALL | RW | LSAF | 1536 | Life Safety | Exit Hardware |  | 5 | 4 | ea | 5062.0266 | 6732.4954 | 0 | 0 | 1958 |  | 1958 | replace hardware/modify doors |  | GF
ROWE HALL | RW | EH&S | 1537 | Environmental Health & Safety | Asbestos abatement | Allowance for spline ceiling | 3 | 8440 | sf | 106808.7611 | 142055.6523 | 0 | 0 | 1973 |  | 1973 |  |  | GF
ROWE HALL | RW | MECH | 1538 | Chilled Water System | Pumps | System/2nd Floor Mech. Rm. | 3 | 2 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1980 | 20 | 2000 | Replace reaching end of useful life |  | GF
ROWE HALL | RW | MECH | 1539 | Chilled Water System | Piping | Entire system | 3 | 47427 | sf | 297094.9599 | 395136.2967 | 0 | 0 | 1958 | 40 | 1998 | Replace reaching end of useful life, failures reported |  | GF
ROWE HALL | RW | MECH | 1540 | Heating Water System | Pumps | System/2nd Floor Mech. Rm. | 3 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1980 | 20 | 2000 | Replace reaching end of useful life |  | GF
ROWE HALL | RW | MECH | 1541 | Heating Water System | Piping | Entire system | 3 | 47427 | sf | 498159.2258 | 662551.7703 | 0 | 0 | 1958 | 40 | 1998 | Replace reaching end of useful life, failures reported |  | GF
ROWE HALL | RW | MECH | 1542 | Steam System | Piping | Entire system | 3 | 47427 | sf | 180057.5515 | 239476.5435 | 0 | 0 | 1958 | 50 | 2008 |  |  | GF
ROWE HALL | RW | MECH | 1543 | Steam System | Boiler | Entire Bldg./Boiler Rm. | 3 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1996 | 25 | 2021 | Replace multiple failures reported |  | GF
ROWE HALL | RW | MECH | 1544 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 47427 | sf | 180057.5515 | 239476.5435 | 0 | 0 | 1958 | 40 | 1998 | Replace reaching end of useful life, failures reported |  | GF
ROWE HALL | RW | MECH | 1545 | Storm/Sanitary sewer system | Sump pumps | S. Entry Mech. Rm. | 4 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown | 10 | 10 | Replace as precautionary measure |  | GF
ROWE HALL | RW | MECH | 1546 | Domestic cold water system | Piping | Entire building | 1 | 47427 | sf | 0 | 0 | 0 | 0 | 1958 | 40 | 1998 | Replace reaching end of useful life, failures reported |  | GF | 654090 | 2014-04-01 | 132098.49 | This project was completed together with project #'s 1535,1547,1548
ROWE HALL | RW | MECH | 1547 | Domestic hot water system | Piping | Entire building | 1 | 47427 | sf | 0 | 0 | 0 | 0 | 1958 | 40 | 1998 | Replace reaching end of useful life, failures reported |  | GF | 654090 | 2014-04-01 | 132098.49 | This project was completed together with project #'s 1535,1546,1548
ROWE HALL | RW | MECH | 1548 | Domestic hot water system | Heater/Steam | Entire building/Boiler Rm. | 1 | 1 | ea | 0 | 0 | 0 | 0 | 1958 | 24 | 1982 | Replace reaching end of useful life |  | GF | 654090 | 2014-04-01 | 132098.49 | This project was completed together with project #'s 1535,1546,1547
ROWE HALL | RW | EH&S | 1549 | Environmental Health & Safety | Asbestos abatement | allowance for mech | 4 | 47427 | sf | 240076.7353 | 319302.058 | 0 | 0 | 1958 |  | 1958 |  |  | GF
ROWE HALL | RW | ELEC | 1550 | Branch Circuit | Exit Panel | Basement mech. Room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1551 | Branch Circuit | Outside Lights Panel | Basement mech. Room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1552 | Branch Circuit | Basement lights panel | Basement mech. Room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1553 | Branch Circuit | Panel LP1A | 1st floor corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1554 | Branch Circuit | Panel LP2A | 2nd floor corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1555 | Branch Circuit | Panel D | room 216 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1556 | Branch Circuit | Panel LP2B | 2nd floor corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1557 | Branch Circuit | Panel 2C | 2nd floor mech. Room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1558 | Branch Circuit | Unmarked Square D QO Panel | room 121 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1995 | 40 | 2035 | Full needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1559 | Branch Circuit | Panel A | room 121 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1560 | Branch Circuit | Panel b | room 121 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1561 | Branch Circuit | 480 voltmotor control center | 2nd floor mech. Room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1562 | Branch Circuit | Panel C | 1st floor corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1563 | Branch Circuit | Panel 2B | 2nd floor corridor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Needs upgrade |  | GF
ROWE HALL | RW | ELEC | 1564 | Lighting | 1x4 recessed fluorescents | corridors | 3 | 68 | ea | 30119.0582 | 40058.3475 | 0 | 0 | Unknown | 20 | 20 | would need upgrade with renovation |  | GF
ROWE HALL | RW | ELEC | 1565 | Lighting | 4 foot pendant fluorescents | classrooms | 3 | 218 | ea | 96558.1573 | 128422.3492 | 0 | 0 | Unknown | 20 | 20 | would need upgrade with renovation |  | GF
ROWE HALL | RW | ELEC | 1566 | Lighting | 12x12 recessed under canopy fixtures | Exterior | 3 |  |  | 0 | 0 | 0 | 0 | Unknown | 20 | 20 | would need upgrade with renovation |  | GF
ROWE HALL | RW | ELEC | 1567 | Lighting | Controls | building | 4 | 47500 | sf | 60111.5658 | 79948.3825 | 0 | 0 | Unknown |  | 0 | no visible controls |  | GF
ROWE HALL | RW | LSAF | 1568 | Life Safety | Egress lighting | building | 3 | 47500 | sf | 120223.1316 | 159896.7651 | 0 | 0 | Unknown | 20 | 20 | would need upgrade with renovation | Capital Improvement? | GF
ROWE HALL | RW | LSAF | 1569 | Life Safety | emergency power | building | 4 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | none |  | GF
ROWE HALL | RW | LSAF | 1570 | Life Safety | Simplex 4002 Fire Alarm | Building | 3 | 47500 | sf | 300557.8291 | 399741.9127 | 0 | 0 | Unknown | 40 | 40 | would need upgrade with renovation |  | GF
ROWE HALL | RW | LSAF | 1571 | Life Safety | Area of Refuge | Allowance | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | GF
LOT1 AUCTION | L1 | ARCH | 1572 | Envelope | Exterior Doors | Insulated Door | 3 | 1 | ea | 1898.26 | 2524.6858 | 0 | 0 | 1986 | 30 | 2016 |  | Prie is for replacing 1 door with a new HM door | GF
LOT1 AUCTION | L1 | ARCH | 1573 | Envelope | Exterior Wall System | Metal Panels | 3 | 500 | sf | 18982.5997 | 25246.8576 | 0 | 0 | 1986 | 30 | 2016 | Uninsulated metal panels on wood studs. | Price is for replacing 500 sf of meatl wall panel and wood framing | GF
LOT1 AUCTION | L1 | ARCH | 1574 | Envelope | Roof/Penetrations | Standing Seam | 3 | 60 | lf | 6327.5332 | 8415.6192 | 0 | 0 | 1986 | 30 | 2016 | Replace vent at peak to keep out weather, birds, and debris. | Price is for removing existing roof vent and replacing it with a new aluminum vebt | GF
LOT1 AUCTION | L1 | ARCH | 1575 | Interior Structure | Partitions | Wood Studs | 3 | 500 | sf | 3796.5199 | 5049.3715 | 0 | 0 | 1986 | 30 | 2016 | Partitions are wood stud with no wall face. | Price is for replacing 500 sf of wood framing for wall | GF
LOT1 AUCTION | L1 | ELEC | 1576 | Service | PVC conduit & GFCI Recptacle | Exterior | 4 | 1 | 1 | 6327.5332 | 8415.6192 | 0 | 0 | 1986 | 30 | 2016 | Where the service enters the building; it should be upgraded | price is for replacing conduit and updating existing GFCI with a new fixture | GF
LOT1 AUCTION | L1 | ELEC | 1577 | Lighting | 8 foot "Slimline" fixtures | Interior | 3 | 2880 | 1 | 18223.2957 | 24236.9833 | 0 | 0 | 1986 | 20 | 2006 | Should be upgraded for energy savings and better light output. | Price is for replacing lights with 40 new fixtures. I could not find any electrical drawing so budget is from a SF cost. | GF
LOT1 AUCTION | L1 | ELEC | 1578 | Lighting | HPS Wallpaks | Exterior | 3 | 10 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 1986 | 20 | 2006 | Should be upgraded for energy savings and better light output. | price is for replacing 10 wallpacks with new ones. | GF
SALT STORAGE | S1 |  | 1579 | [6 empty] | 0 | 0 | 0 | 0 | Unknown |  | 0 |  |  | GF
DOW SCIENCE | SC | ARCH | 1580 | Envelope | Exterior Doors | First Floor | 3 | 10 | ea | 63275.3324 | 84156.1921 | 0 | 0 | 1992 | 30 | 2022 | Replace exterior doors. |  | GF
DOW SCIENCE | SC | ARCH | 1581 | Envelope | Interior Vestibule Doors | First Floor | 3 | 4 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1992 | 30 | 2022 | Replace interior vestibule doors. |  | GF
DOW SCIENCE | SC | ARCH | 1582 | Envelope | Roof/Penetrations | Second & Third Fl. | 1 | 67852 | sf | 0 | 0 | 0 | 0 | 1992 | 30 | 2022 | Roof needs repair to prevent leaks and ponding. |  | GF | 654042 | August, 2013 | 919792 | work included all roof section (1,2,and) also the east, west, and north canopies were completed.
DOW SCIENCE | SC | ARCH | 1583 | Envelope | Covered Canopy | Bet. Brooks & Dow | 3 | 1735 | sf | 54891.3509 | 73005.4967 | 0 | 0 | 1992 | 30 | 2022 | Repair roof leaks and replace finishes as required. |  | GF
DOW SCIENCE | SC | MECH | 1584 | Ventilation/Terminal Units | Terminal Unit | Lab Hood/All Labs | 3 |  |  | 0 | 0 | 0 | 0 | 1991 | 20 | 2011 | Replace reaching end of useful life | Is this the same item as above? No - do you need more specifications? Yes, the price above is for replacing all VAV boxes in the building | GF
DOW SCIENCE | SC | MECH | 1585 | Building Management | HVAC Control | Lab Hood system | 3 |  |  | 0 | 0 | 0 | 0 | 1991 | 25 | 2016 | Replace reaching end of useful life, failures reported |  | GF
DOW SCIENCE | SC | MECH | 1586 | Ventilation/Terminal Units | AHU/CHW Cool/Steam Heat | AHU-1/Rm. 339 | 4 | 80000 | cfm | 101240.5319 | 134649.9074 | 0 | 0 | 30 | 2021 | 2051 | from drawings dated M17.2 6-1-1989 |  | GF
DOW SCIENCE | SC | MECH | 1587 | Ventilation/Terminal Units | AHU/CHW Cool/Steam Heat | AHU-2/Rm. 339 | 4 | 80000 | cfm | 101240.5319 | 134649.9074 | 0 | 0 | 30 | 2021 | 2051 | from drawings dated M17.2 6-1-1989 |  | GF
DOW SCIENCE | SC | MECH | 1588 | Ventilation/Terminal Units | AHU/CHW Cool/HW Heat | AHU-3/2nd Fl. Mech. Rm. | 3 | 28300 | cfm | 35813.8382 | 47632.4047 | 0 | 0 | 30 | 2021 | 2051 | from drawings dated M17.2 6-1-1989 |  | GF
DOW SCIENCE | SC | MECH | 1589 | Ventilation/Terminal Units | AHU/CHW Cool/Steam Heat | AHU-4/2nd Fl. Mech. Rm. | 4 | 35525 | cfm | 44957.1237 | 59792.9745 | 0 | 0 | 30 | 2021 | 2051 | from drawings dated M17.2 6-1-1989 |  | GF
DOW SCIENCE | SC | MECH | 1590 | Ventilation/Terminal Units | Terminal Unit | Fan VAV HW Reheat/All Labs | 2 | 843 | ea | 8001165.7863 | 10641550.4958 | 0 | 0 | 20 | 2011 | 2031 | Price is for replacing 843 VAV boxes with new units and reconnecting to existing piping. Quantity was taken from sheet M 17.1 dated 6-1-1989 |  | GF
DOW SCIENCE | SC | MECH | 1591 | Building Management | HVAC Control | Lab Hood system | 3 | 203556 | sf | 1030405.8855 | 1370439.8277 | 0 | 0 | 25 | 2016 | 2041 |  |  | GF
DOW SCIENCE | SC | MECH | 1592 | Storm/Sanitary sewer system | Sewage Lift pump | Rm. 020 | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown | 10 | 10 | Replace float switches with external mechanical |  | GF
DOW SCIENCE | SC | MECH | 1593 | Domestic cold water system | Booster pump | Entire system/Rm. 176 | 2 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 20 | 2011 | 2031 |  |  | GF
SATELLITE ENERGY FACILITY | SF | ARCH | 1594 | Envelope | Exterior Wall System |  | 3 | 800 | sf | 12655.0665 | 16831.2384 | 0 | 0 | 2006 | 100 | 2106 | Repair efflorescence on brick, stone cap at top of wall. | Price is for powerwashing damaged area and includes 200 sf of brick repair/replacement if needed | GF
SLOAN HALL | SL | ARCH | 1595 | Envelope | Windows | Alum. insul Glass | 3 | 8940 | lf | 56568.1472 | 75235.6358 | 0 | 0 | 2000 | 30 | 2030 | All windows need caulk and weatherproofing. | Price is for removing and replacing caulk on the inside and outside of windows | GF
SLOAN HALL | SL | ARCH | 1596 | Envelope | Concrete Landing | Entry Door | 1 | 1 | ea | 0 | 0 | 0 | 0 | Unknown |  | 0 | Concrete and Brick Landing require repair | Price is for removing damages portion of landing and replacing concrete. Also include removing damaged brick and replacing it with new. | GF | 654055 | 2014-02-10 | 183962.68 | This project also included downspout and foundation foot drain repairs
SLOAN HALL | SL | ARCH | 1597 | Envelope | Exterior Wall System | Brick Repair | 4 | 3000 | sf | 94912.9987 | 126234.2882 | 0 | 0 | 1941 | 100 | 2041 | Repair brick around windows and tuck point. | Price is for tuck-pointing about 3,000 of brick around windows. | GF
SLOAN HALL | SL | ARCH | 1598 | Envelope | Roof/Penetrations | Second floor wells | 1 | 450 | sf | 0 | 0 | 0 | 0 | 1941 | 30 | 1971 | Window wells leak, damage to interior of building. | Price is for repairing window wells. Includes apply membrane to existing well area and re-sloping it to the drainage points. | GF | 654055 | 2014-02-10 | 183962.68 | This project also included downspout and foundation foot drain repairs
SLOAN HALL | SL | ARCH | 1599 | Wall Finishes | Painted plaster | offices | 4 | 1000 | sf | 22779.1197 | 30296.2292 | 0 | 0 | 1941 | 10 | 1951 | Repair damaged plaster around windows and ceilings. | Not same as above. This describes damage to walls from water leaks. Ceiling also has damage from water leaks. | GF
SLOAN HALL | SL | ARCH | 1600 | Ceiling Finishes | Drywall / Plaster | offices, lobbies | 4 | 250 | sf | 11073.1832 | 14727.3336 | 0 | 0 | 1941 | 20 | 1961 | Repairs have been done over the years. Damage in rooms | Price is for removing 250 sf of damaged plaster ceiling and replacing it with new plaster ceiling finish. Some new framing is included. | GF
SLOAN HALL | SL | ADAC | 1601 | BF/ADA Compliance | Interior Door Hardware | Wood | 3 | 180 | ea | 113895.5984 | 151481.1458 | 0 | 0 | 1941 | 30 | 1971 | Doors have knob-type hardware. | Price is for removing existing door hardware and replacing it with ADA compliant hardware | GF
SLOAN HALL | SL | ADAC | 1602 | BF/ADA Compliance | Toilet Rooms |  | 3 | 1560 | sf | 197419.0372 | 262567.3195 | 0 | 0 | 1990 | 20 | 2010 | Some toilet rooms are ADA-accessible. Modify others for ADA access. | Price is for renovations of existing bathrooms to meet ADA codes | GF
SLOAN HALL | SL | EH&S | 1603 | Environmental Health & Safety | asbestos abatement | allowance | 3 | 20000 | sf | 151860.7978 | 201974.8611 | 0 | 0 | Unknown |  | 0 | Allowance for door replacement, partition and ceiling, finish replacement. Averaged SF costs to get a $6/SF unit cost. |  | GF
SLOAN HALL | SL | MECH | 1604 | Building Management | HVAC Control | N. & 3rd all | 5 | 13850 | sf | 111699.1936 | 148559.9275 | 0 | 0 | 1941 | 25 | 1966 | No control, upgrade to local or preferably DDC if feasible. | Price is for replacing existing controls for the health service addition and the entire third floor with new DDC controls | GF
SLOAN HALL | SL | MECH | 1605 | Storm/Sanitary sewer system | Sump pumps | Simplex/Rm. 020A | 3 | 1 | ea | 36292.1568 | 48268.5685 | 0 | 0 | Unknown | 10 | 10 | Replace pump in 020A as a precautionary measure | Price is for replacing existing pump with a new unit. | GF
SLOAN HALL | SL | MECH | 1606 | Domestic cold water system | Piping | Entire building | 4 | 39250 | sf | 253238.605 | 336807.3447 | 0 | 0 | 1941 | 40 | 1981 | Replace nearing end of useful life. Brown water reports are common |  | GF
SLOAN HALL | SL | MECH | 1607 | Domestic hot water system | Piping | Entire building | 4 | 39250 | sf | 253238.605 | 336807.3447 | 0 | 0 | 1941 | 40 | 1981 | Replace nearing end of useful life. Brown water reports are common |  | GF
SLOAN HALL | SL | MECH | 1608 | Domestic hot water system | Heater/Electric | Rm. 020 | 3 |  |  | 0 | 0 | 0 | 0 | 2005 | 12 | 2017 | Replace nearing end of useful life. Consider replacement with steam heat exchanger |  | GF
SLOAN HALL | SL | EH&S | 1609 | Environmental Health & Safety | asbestos abatement | allowance | 4 | 48134 | sf | 243655.5881 | 324061.9322 | 0 | 0 | Unknown |  | 0 |  |  | GF
SLOAN HALL | SL | ELEC | 1610 | Branch Circuits | Frank Adams | Room 002 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1941 | 40 | 1981 | Needs Upgrade |  | GF
SLOAN HALL | SL | ELEC | 1611 | Branch Circuits | Old signal panels (3) | Room 002 | 4 | 1 | 1 | 28473.8996 | 37870.2865 | 0 | 0 | 1941 | 40 | 1981 | Needs to be removed |  | GF
SLOAN HALL | SL | ELEC | 1612 | Branch Circuits | Panel 020A | Room 020A | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1941 | 40 | 1981 | Needs Upgrade |  | GF
SLOAN HALL | SL | ELEC | 1613 | Branch Circuits | Unmarked Square D QO Panel | Mail Room | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | OK |  | GF
SLOAN HALL | SL | ELEC | 1614 | Branch Circuits | Unmarked General Electric | By Room 120 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs Upgrade |  | GF
SLOAN HALL | SL | ELEC | 1615 | lighting | Small Wall packs | Exterior | 3 | 3 | 1 | 1898.26 | 2524.6858 | 0 | 0 | Unknown | 20 | 20 | needs upgrade | price is for replacing 3 wall packs with new fixtures | GF
SLOAN HALL | SL | ELEC | 1616 | lighting | Exterior Canopies (2) | Exterior | 3 | 4 | ea | 2531.0133 | 3366.2477 | 0 | 0 | Unknown |  | 0 | Needs Upgrade | Price is for replacing 4 canopy lights with new fixtures | GF
SLOAN HALL | SL | LSAF | 1617 | Life Safety | Simplex 4002 Fire Alarm | Room 002 | 3 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | Unknown |  | 0 | Needs upgrade if renovated | Price is for replacing main fire alarm panel. If complete system renovation is required price will need to be adjusted | GF
SLOAN HALL | SL | LSAF | 1618 | Life Safety | Area of Refuge | Allowance | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | GF
SLOAN HALL | SL | LSAF | 1619 | Life Safety | Egress lighting | Bld. | 3 | 30 | ea | 18982.5997 | 25246.8576 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade if renovated |  | GF
SMITH HALL | SM | ARCH | 1620 | Envelope | Exterior Doors |  | 3 | 11 | ea | 69602.8657 | 92571.8114 | 0 | 0 | 1960 | 30 | 1990 | Replace to match new campus standard. | Price is to replace existing entry doors with new alumn framed entry doors | GF
SMITH HALL | SM | ARCH | 1621 | Envelope | Exterior Wall System |  | 3 | 500 | sf | 15818.8331 | 21039.048 | 0 | 0 | 1934 | 100 | 2034 | Tuck point areas needing repair. | Price is for repairing 500 sf of damaged brick/mortar and replacing it with new. | GF
SMITH HALL | SM | ARCH | 1622 | Envelope | Exterior Wall System | South façade | 4 | entire south façade |  | 129966.4604 | 172855.3923 | 0 | 0 | Unknown | 100 | 100 | Remove ivy, tuck point and seal - refer to photos | Price is for removing ivy some tuckpointing ad sealing of area. The price does include tuck pointing and sealing south façade | GF
SMITH HALL | SM | ARCH | 1623 | Interior Structure | Partitions | Corridor Public | 3 | 1000 | sf | 18982.5997 | 25246.8576 | 0 | 0 | 1934 | 40 | 1974 | Plaster walls in good condition, minor repair needed. | Price is for repairing 1,000 sf of plaster wall finish. Includes replastering damaged areas, sanding and repainting areas. | GF
SMITH HALL | SM | ARCH | 1624 | Interior Structure | Interior Doors |  | 3 | 80 | ea | 45558.2394 | 60592.4583 | 0 | 0 | 1960 | 40 | 2000 | Doors show wear but in good condition. | Price includes patch and repair of existing doors and restaining existing doors in place. No new frames or hardware are included in this price. | GF
SMITH HALL | SM | ARCH | 1625 | Interior Structure | Toilet Rooms |  | 3 | 675 | sf | 85421.6988 | 113610.8594 | 0 | 0 | 2010 | 40 | 2050 | Toilet fixtures and plumbing replaced in 2010. | Price is for remodeling bathroom areas to meet ada codes | GF
SMITH HALL | SM | ARCH | 1626 | Floor Finishes | Carpet | Corridor Public | 3 | 3200 | sf | 22272.917 | 29622.9796 | 0 | 0 | 1996 | 15 | 2011 | Carpet worn but in good condition, should be replaced within 3-5 years. | price is for replacing existing corridor carpet with new carpet. | GF
SMITH HALL | SM | ARCH | 1627 | Ceiling Finishes | Plaster ceilings | Corridor | 3 | 30 | sf | 1898.26 | 2524.6858 | 0 | 0 | 1934 | 30 | 1964 | Repair ceiling damage in room 114C. | Price is for repairing about 30 sf of plaster ceiling in room 114C | GF
SMITH HALL | SM | EH&S | 1628 | Environmental Health & Safety | Asbestos Abatement | Allowance | 3 |  |  | 45431.6887 | 60424.146 | 0 | 0 | Unknown |  | 0 | Allowance for plaster wall and ceiling repairs, adhesive below carpeting, and toilet rooms. |  | GF
SMITH HALL | SM | ADAC | 1629 | BF/ADA Compliance | Interior Door Hardware | Office entry | 3 | 80 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1960 | 30 | 1990 | Mixture of accessible and non-accessible hardware. | How many should be priced? Price is for replacing all of the interior door hardware to ADA compliant hardware | GF
SMITH HALL | SM | MECH | 1630 | Ventilation/Terminal Units | AHU/DX Cool/Steam Heat | AHU-1, Basement Mech. Rm. | 3 | 20 | Tons | 113895.5984 | 151481.1458 | 0 | 0 | 1934 | 30 | 1964 | Replace nearing end of useful life |  | GF
SMITH HALL | SM | MECH | 1631 | Ventilation/Terminal Units | Terminal units/Cast Iron | Steam Radiation, Bldg. Perimeter | 3 | 570 | lf | 346242.6191 | 460502.6834 | 0 | 0 | 1934 | 25 | 1959 | Replace nearing end of useful life | Price is for replacing old radiant heat terminal units with new radiant ceiling panels. I couldn't find any mechanical drawings so quantity was taken from the outside perimeter of the building. | GF
SMITH HALL | SM | MECH | 1632 | Steam System | PRV Station | Entire System, Basement Mech. Rm. | 3 | 1 | ea | 132878.1981 | 176728.0035 | 0 | 0 | 1934 | 50 | 1984 | Replace nearing end of useful life |  | GF
SMITH HALL | SM | MECH | 1633 | Steam System | Piping | Entire System, Basement Mech. Rm. | 3 | 25350 | sf | 88221.6322 | 117334.7709 | 0 | 0 | 1934 | 50 | 1984 | Replace nearing end of useful life | Price is for replacing steam piping throughout the building. | GF
SMITH HALL | SM | MECH | 1634 | Building Management | HVAC Control | Hybrid, Pneumatic/DDC | 3 | 25350 | sf | 160402.9677 | 213335.9471 | 0 | 0 | 1980 | 25 | 2005 | Replace with new DDC | Price is for replacing existing controls with new DDC Controls | GF
SMITH HALL | SM | MECH | 1635 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 25350 | sf | 88221.6322 | 117334.7709 | 0 | 0 | 1934 | 40 | 1974 | Replace all drainage piping failures reported | Price is for replacing existing drainage pipe. | GF
SMITH HALL | SM | MECH | 1636 |  | Heater/Steam | Basement Mech. Rm. | 3 | 1 | ea | 31637.6662 | 42078.0961 | 0 | 0 | 1970 | 24 | 1994 | Replace nearing end of useful life. Connect first floor restroom to building domestic hot water system | What is being replaced? Domestic hot water heater? Replacing steam storage domestic water heater and eliminating one electric domestic water heater. | GF
SMITH HALL | SM | EH&S | 1637 | Environmental Health & Safety | Asbestos abatement | Asbestos abatement | allowance for mech items | 25350 | sf | 128322.3742 | 170668.5861 | 0 | 0 | 1934 |  | 1934 |  |  | GF
SMITH HALL | SM | ELEC | 1638 | Distribution | 240 volt I-Line panel | Basement | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | OK |  | GF
SMITH HALL | SM | ELEC | 1639 | Distribution | 120/208 QO | Basement | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | Retrofitted |  | GF
SMITH HALL | SM | ELEC | 1640 | Branch Circuit | Panel LPA | by room 104 | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1996 | 40 | 2036 | full |  | GF
SMITH HALL | SM | ELEC | 1641 | Branch Circuit | panel A | by room 208 | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1996 | 40 | 2036 | full |  | GF
SMITH HALL | SM | ELEC | 1642 | Lighting | Wall packs | Exterior | 4 | 4 | ea | 2531.0133 | 3366.2477 | 0 | 0 | Unknown | 20 | 20 | old and yellowed | Price is for replacing 4 exterior wall packs light fixtures and replacing them with new. (Assumed there are 2 at each entry) | GF
SMITH HALL | SM | LSAF | 1643 | Life Safety | Fire Alarm | Basement | 3 | 1 | 1 | 6327.5332 | 8415.6192 | 0 | 0 | Unknown | 40 | 40 | this would have to be upgraded with a renovation | Price is for upgrading main fire alarm panel. If entire system needs to be upgraded price needs to be adjusted | GF
SMITH HALL | SM | LSAF | 1644 | Life Safety | Area of Refuge |  | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | GF
SMITH HALL | SM | LSAF | 1645 | Life Safety | egress lighting | Bld. | 3 | 18 | ea | 11389.5598 | 15148.1146 | 0 | 0 | Unknown | 20 | 20 | they are in some rooms - not in corridors | Price is for adding 18 wall mounted egress lights to the corridors | GF
SPECIAL OLYMPICS | SO | ARCH | 1646 | Envelope | Exterior Doors | Overhead | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | 1988 | 30 | 2018 | Overhead door needs to be replaced. | Price is for removing old door and replacing with new OH door. | GF
SPECIAL OLYMPICS | SO | ADAC | 1647 | BF/ADA Compliance | Interior Door Hardware | knob-style | 3 | 38 | ea | 24044.6263 | 31979.353 | 0 | 0 | 1988 | 30 | 2018 |  | Price is for replacing existing door hardware for ADA compliant hardware. | GF
SPECIAL OLYMPICS | SO | ELEC | 1648 | Branch Circuits | Panel LPA | Electrical room | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1996 | 40 | 2036 | appears full |  | GF
SPECIAL OLYMPICS | SO | ELEC | 1649 | Branch Circuits | Panel LPC | Electrical room | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1996 | 40 | 2036 | appears full |  | GF
SPECIAL OLYMPICS | SO | ELEC | 1650 | Branch Circuits | Panel LPX | Electrical room | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1996 | 40 | 2036 | Fed from LINE side of main |  | GF
SPECIAL OLYMPICS | SO | ELEC | 1651 | Branch Circuits | panel LPB | Electrical room | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1996 | 40 | 2036 | appears full |  | GF
SPECIAL OLYMPICS | SO | ELEC | 1652 | Lighting | Recessed cans with Halogen floods |  | 3 | 38 | ea | 21640.1637 | 28781.4177 | 0 | 0 | Unknown | 20 | 20 | Change to CFL's or LED's | Price is for removing old fixtures and replacing them with new updated lights | GF
SPECIAL OLYMPICS | SO | ELEC | 1653 | Lighting | HPS wallpacks | Exterior | 3 | 4 | ea | 2531.0133 | 3366.2477 | 0 | 0 | Unknown | 20 | 20 | Yellowed-needs upgrade | price is for replacing existing light with updated fixtures | GF
SPECIAL OLYMPICS | SO | LSAF | 1654 | Life Safety | Egress lighting | Bld. | 3 | 20 | sf | 12655.0665 | 16831.2384 | 0 | 0 | Unknown | 20 | 20 | would need upgrade if renovated | Price is for adding about 20 wall mounted emergency lights | GF
KELLY/SHORTS STADIUM | ST | ARCH | 1655 | Envelope | SOG/ Concrete | Original stadium seating | 4 | 500 | lf | 12655.0665 | 16831.2384 | 0 | 0 | 1973 | 100 | 2073 | repair extensive cracking and spalling of concrete, 500 lineal FT, 20" wide |  | GF
KELLY/SHORTS STADIUM | ST | ARCH | 1656 | Envelope |  | Concrete step size | 3 | 9850 | sf | 436283.4171 | 580256.9448 | 0 | 0 | 1973 |  | 1973 | Steps vary in size at original seating aisles | Need to remove and replace 4 rings around stadium. Need to go 1 row above and 1 row below to average each riser for proper height. Row is 2'2" and riser is 8" per row. | GF
KELLY/SHORTS STADIUM | ST | ARCH | 1657 | Envelope |  | Concrete tunnel | 4 | 520 | lf | 19741.9037 | 26256.7319 | 0 | 0 | 1973 | 100 | 2073 | Water infiltration into tunnel needs to be repaired, patch 8 joints, 64 lineal FT at each location | Price is for removing and repairing 8 joint locations (520 lnft total) and adding waterproofing to each location | GF
KELLY/SHORTS STADIUM | ST | ARCH | 1658 | Envelope | Roof | Rusting metal gutter | 3 | 45 | lf | 1138.956 | 1514.8115 | 0 | 0 | 1973 | 30 | 2003 | Gutter should be replaced or repaired in 3 to 5 years, 45 lineal FT | Price is for removing existing gutter and replacing it with new aluminum gutter | GF
KELLY/SHORTS STADIUM | ST | ARCH | 1659 | Envelope | Exterior Walls | West stair towers | 2 | 7075 | sf | 0 | 0 | 0 | 0 | 1973 | 100 | 2073 | Water damage should be repaired and walls sealed | CMU Wall - Exterior and Interior side. Price is for applying spray on waterproofing to interior and exterior and repainting CMU walls | GF | 683993 | 2013-05-01 | 29792.96
KELLY/SHORTS STADIUM | ST | ARCH | 1660 | Envelope | Exterior walkway |  | 5 | 7500 | sf | 14236.9498 | 18935.1432 | 0 | 0 | 1973 | 30 | 2003 | Install anti pigeon measure, clean and repaint all steel, 750 lineal FT | How wide? How high up? Pigeon spikes, wire or netting? Price is for 7500 Sf of bird netting for the exterior walkway | GF
KELLY/SHORTS STADIUM | ST | ARCH | 1661 | Envelope | Stadium turf |  | 4 | 7200 | sy | 1002281.2658 | 1333034.0835 | 0 | 0 | 1973 | 30 | 2003 | Stadium turf is near the end of life for this product and should be replaced | May be discussion topic with CMU to determine scope? Let's put in an allowance for complete turf replacement. | GF
KELLY/SHORTS STADIUM | ST | ARCH | 1662 | Interior Structure | Floor Finishes | Carpet | 4 | 11280 | sf | 78512.0325 | 104421.0032 | 0 | 0 | 1973 | 15 | 1988 | Carpet in general needs to be replaced - suite and press level | Area was taken from the press box and club level floor plan. Price is for removing and replacing existing carpet in press box and suite areas. | GF
KELLY/SHORTS STADIUM | ST | ARCH | 1663 | Interior Structure | Casework | Suite level | 4 | 180 | lf | 102506.0385 | 136333.0313 | 0 | 0 | 1973 | 40 | 2013 | Casework and counters are damaged and showing signs of wear, 15 locations 12 ft of counter at each | Price is for removing existing casework and replacing it with new plastic laminate casework | GF
KELLY/SHORTS STADIUM | ST | ARCH | 1664 | Interior Structure | Visiting concessions |  | 4 | 1000 | sf | 126550.6649 | 168312.3843 | 0 | 0 | 1973 | 40 | 2013 | Building is outdated and in need of replacement, approx 1,000 SF | Price assumes existing concessions are will be used and includes renovation of existing concessions area. A budget of $100/sf was used for this item. Further discussion and scope clarification is needed to refine budget number | GF
KELLY/SHORTS STADIUM | ST | ARCH | 1665 | Interior Structure | Locker rooms |  | 3 | 2700 | sf | 341686.7951 | 454443.4375 | 0 | 0 | 1973 | 40 | 2013 | Locker rooms are too small, addition of approx 2,700 SF | Budget price of $100/sf was use for renovating locker rooms/ Adding Meeting room. Further detail is needed to refine budget. Price assumes that existing building space will be used and that no addition to the stadium is needed. | GF
KELLY/SHORTS STADIUM | ST | MECH | 1666 | Ventilation/Terminal Units | AHU/Electric Heat | AHU, N.E. Concession Mech. Rm. | 3 | 1600 | cfm | 20248.1064 | 26929.9815 | 0 | 0 | 1973 | 30 | 2003 | Replace unit reaching end of useful life |  | GF
KELLY/SHORTS STADIUM | ST | MECH | 1667 | Ventilation/Terminal Units | AHU/Hot Water Heat | AHU-4, Mech. Rm. Locker Facility | 3 | 9940 | cfm | 125791.3609 | 167302.51 | 0 | 0 | 1973 | 30 | 2003 | Replace unit reaching end of useful life |  | GF
KELLY/SHORTS STADIUM | ST | MECH | 1668 | Heating Water System | Pumps | Entire Locker Facility, Boiler Rm. | 3 | 2 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1973 | 10 | 1983 | Replace nearing end of useful life | Price is for replacing existing pumps with new base mounted VFD pumps | GF
KELLY/SHORTS STADIUM | ST | MECH | 1669 | Heating Water System | Piping | Entire system, Locker Facility | 3 | 6100 | sf | 64072.6016 | 85216.5602 | 0 | 0 | 1973 | 40 | 2013 | Replace all iron pipe, nearing end of useful life | Price is for replacing heat piping in current locker room area. | GF
KELLY/SHORTS STADIUM | ST | MECH | 1670 | Heating Water System | Insulation | Entire system, Locker Facility | 3 | 6100 | sf | 15439.1811 | 20534.1109 | 0 | 0 | 1973 |  | 1973 | Replace when piping system is upgraded | Unit price was increased to $2/sf because of the small area | GF
KELLY/SHORTS STADIUM | ST | ELEC | 1671 | Distribution | Original Indoor MDP | North Elect. Rm | 4 | 1 | 2000A | 259428.863 | 345040.3878 | 0 | 0 | 1973 | 50 | 2023 | 2000A Main, Branches: (1) 1200A, (1) 800A with the following branches (1) 600, (3) 200A, (2)100A, (6) 60A, (4)30A. | Price is for replacing 2 mdp and 16 branch panels with new and connecting to existing feeds | GF
KELLY/SHORTS STADIUM | ST | ELEC | 1672 | Distribution | Outdoor MDP |  | 4 | 1 | 1200A | 60744.3191 | 80789.9445 | 0 | 0 | Unknown | 40 | 40 | 1200 A Main, Branches: (1) 1200 A | Price is for replacing existing panel with a new 1200A panel and reconnecting to existing feeds | GF
KELLY/SHORTS STADIUM | ST | ELEC | 1673 | Panel H2 | 277/480V- 100A MLO | North Elect. Rm | 4 | 30 | ea | 284738.996 | 378702.8646 | 0 | 0 | Unknown | 40 | 40 | (30) 1P CIRCUIT BREAKERS |  | GF
KELLY/SHORTS STADIUM | ST | ELEC | 1674 | Panel L4 | 120/208 - 100A MCB | North Elect. Rm | 4 | 30 | ea | 284738.996 | 378702.8646 | 0 | 0 | Unknown | 40 | 40 | (30) -1P & (1) - 3P CIRCUIT BKRS |  | GF
KELLY/SHORTS STADIUM | ST | ELEC | 1675 | Panel P1 | 120/208 - 100A MLO | North Elect. Rm | 4 | 10 | ea | 94912.9987 | 126234.2882 | 0 | 0 | Unknown | 40 | 40 | (10) - 3P CIRCUIT BKRS |  | GF
KELLY/SHORTS STADIUM | ST | ELEC | 1676 | Panel L6 | 120/208 - 100A MLO | Ticket Booth | 4 | 16 | ea | 151860.7978 | 201974.8611 | 0 | 0 | Unknown | 40 | 40 | (12) - 1P CIRCUIT BKRS & (4) 3P CB'S |  | GF
THEUNISSEN STADIUM | TS | ARCH | 1677 | Envelope | Basement walls | Locker rom | 4 | 1 | ea | 94912.9987 | 126234.2882 | 0 | 0 | 2002 | 100 | 2102 | Wall needs to be water proofed as decribed in the narrative | Includes excavation, waterproofing, shoring and backfilling area. | GF
THEUNISSEN STADIUM | TS | ARCH | 1678 | Envelope | Outfield fence |  | 3 | 1 | ea | 10124.0532 | 13464.9907 | 0 | 0 | 2002 | 20 | 2022 | Plywood should be replaced |  | GF
THEUNISSEN STADIUM | TS | ARCH | 1679 | Envelope | Scoreboard |  | 1 | 1 | all | 0 | 0 | 0 | 0 | 2002 | 25 | 2027 | Is not working properly or at all | More description needed from CMU on requirements for accurate budget. Budget of $25,000 has been included as a place holder. OK | GF | 654010 | 2013-03-01 | 41922.5
THEUNISSEN STADIUM | TS | ARCH | 1680 | Envelope | Access to field | South end of concourse | 3 | 1 | ea | 94912.9987 | 126234.2882 | 0 | 0 | Unknown |  | 0 | Add stairs and ramp per narrative | Capital Improvement?confirm scope with CMU | GF
THEUNISSEN STADIUM | TS | ARCH | 1681 | Envelope | Sloped grass area | East of main stadium entry | 4 | 2240 | sf | 28347.3489 | 37701.9741 | 0 | 0 | 2002 |  | 2002 | Revised to tiered area as noted in narrative | includes removing existing grass, adding a layer of mulch | GF
THEUNISSEN STADIUM | TS | ARCH | 1682 | Envelope | Field grass |  | 3 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | Install field turf | Capital Improvement | GF
THEUNISSEN STADIUM | TS | ARCH | 1683 | Envelope | Stadium lights |  | 3 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | Install stadium lights | Capital Improvement | GF
THEUNISSEN STADIUM | TS | ARCH | 1684 | Envelope | Irrigate practice field |  | 1 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | Install full irrigation system |  | GF | 684332 | October, 2013 | 23475
THEUNISSEN STADIUM | TS | ARCH | 1685 | Envelope | Concrete curb | Edge or parking lot | 4 | 50 | lf | 1898.26 | 2524.6858 | 0 | 0 | 2002 |  | 2002 | Repair sub-grade and install new curb |  | GF
THEUNISSEN STADIUM | TS | ARCH | 1686 | Envelope | Benches | Dugouts | 3 | 40 | lf | 15186.0798 | 20197.4861 | 0 | 0 | 2002 | 30 | 2032 | Replace warping benches |  | GF
THEUNISSEN STADIUM | TS | ARCH | 1687 | Interior Structure | Floor Finishes | Carpet in press box | 4 | 500 | sf | 3480.1433 | 4628.5906 | 0 | 0 | 2002 | 15 | 2017 | Replace |  | GF
THEUNISSEN STADIUM | TS | ARCH | 1688 | Interior Structure | Fixed Equip/Furnishing |  | 3 |  |  | 0 | 0 | 0 | 0 | 2002 | 40 | 2042 | Missing three compartment sink in concessions | Capital Improvement | GF
THEUNISSEN STADIUM | TS | LSAF | 1689 | Life Safety (Arch) | Exit Stairs | Main entry | 4 | 4 | ea | 25310.133 | 33662.4769 | 0 | 0 | 2002 |  | 2002 | Stairs and hand rail inserts are cracking, see photos |  | GF
THEUNISSEN STADIUM | TS | ELEC | 1690 | Lighting/Controls | General | No Occup. Sensors | 3 | 25628 | sf | 32432.4044 | 43135.0978 | 0 | 0 | Unknown |  | 0 | Opportunities for energy savings, e.g. public restrooms where lights are on continuously. |  | GF
THEUNISSEN STADIUM | TS | LSAF | 1691 | Life Safety | Emergency Lighting | Battery Units | 3 | 12 | ea | 7593.0399 | 10098.7431 | 0 | 0 | Unknown |  | 0 | Normal battery maintenance |  | GF
UNIVERSITY ART GALLERY | UA | ARCH | 1692 | Envelope | Windows | Single Pane / Wood | 4 | 770 | sf | 34105.4042 | 45360.1876 | 0 | 0 | 1960 | 30 | 1990 | Single pane glazing in wood frame to be replaced. |  | GF
UNIVERSITY ART GALLERY | UA | ARCH | 1693 | Envelope | Exterior Doors | Alum. Entry Doors | 4 | 4 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1960 | 30 | 1990 | Alum. entry doors to be replaced to match new campus standard. |  | GF
UNIVERSITY ART GALLERY | UA | ARCH | 1694 | Envelope | Exterior Wall System | Glass / Roof / CMU | 3 |  |  | 0 | 0 | 0 | 0 | 1960 | 100 | 2060 | CMU wall base with windows and sharply angled roof. | What should be priced? Covered under windows - no pricing needed. | GF
UNIVERSITY ART GALLERY | UA | ARCH | 1695 | Envelope | Roof/Penetrations | Shingled High Pitch | 3 | 6300 | sf | 31890.7675 | 42414.7208 | 0 | 0 | 1989 | 30 | 2019 | Roof shingles worn and show staining. |  | GF
UNIVERSITY ART GALLERY | UA | ARCH | 1696 | Floor Finishes | Carpet | Offices | 4 | 490 | sf | 3410.5404 | 4536.0188 | 0 | 0 | 1989 | 15 | 2004 | Carpet in offices needs replacement. |  | GF
UNIVERSITY ART GALLERY | UA | ARCH | 1697 | Floor Finishes | Sealed Concrete | Exhibition Area | 3 | 1500 | sf | 28473.8996 | 37870.2865 | 0 | 0 | 1960 | 30 | 1990 | Floor has been resurfaced. Good condition but slip hazard in winter. | what should be priced? Provide allowance for exhibition area flooring to be replaced with non-skid product. | GF
UNIVERSITY ART GALLERY | UA | ADAC | 1698 | BF/ADA Compliance | Interior Door Hardware |  | 3 | 10 | ea | 6327.5332 | 8415.6192 | 0 | 0 | Unknown | 40 | 40 | knob-style hardware | replace | GF
UNIVERSITY ART GALLERY | UA | ADAC | 1699 | BF/ADA Compliance | Toilet Rooms |  | 3 | 80 | sf | 10124.0532 | 13464.9907 | 0 | 0 | Unknown |  | 0 | Not ADA accessible, should be renovated for accessibility. |  | GF
UNIVERSITY ART GALLERY | UA | MECH | 1700 | Ventilation/Terminal Units | Terminal units | Hot water radiation, First Floor | 3 | 175 | lf | 62009.8258 | 82473.0683 | 0 | 0 | 1989 | 25 | 2014 | Replace not enough capacity |  | GF
UNIVERSITY ART GALLERY | UA | MECH | 1701 | Chilled Water System | Pumps | AHU-1, Basement Mech. Rm. | 5 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1989 | 10 | 1999 | Replace nearing end of useful life |  | GF
UNIVERSITY ART GALLERY | UA | MECH | 1702 | Chilled Water System | Piping | AHU-1, Basement Mech. Rm. | 3 | 3330 | sf | 25284.8228 | 33628.8144 | 0 | 0 | 1989 | 40 | 2029 | Repair isolation valves in piping for AHU-1 | Unit costs increased because of small SF area | GF
UNIVERSITY ART GALLERY | UA | MECH | 1703 | Heating Water System | Insulation | N.W. radiation, Basement Mech. Rm. | 3 | 3330 | sf | 7374.74 | 9808.4042 | 0 | 0 | Unknown | 40 | 40 | Good condition, no reported problems | past useful life | GF
UNIVERSITY ART GALLERY | UA | MECH | 1704 | Building Management | HVAC Control | Hybrid and straight pneumatic | 3 | 3330 | sf | 25284.8228 | 33628.8144 | 0 | 0 | 1960 | 20 | 1980 | Replace with DDC system |  | GF
UNIVERSITY ART GALLERY | UA | MECH | 1705 | Storm/Sanitary Sewer System | Sump pump | Basement mechanical room | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | 1975 | 10 | 1985 | Replace as a precautionary measure |  | GF
UNIVERSITY ART GALLERY | UA | EH&S | 1706 | Environmental Health & Safety | Asbestos abatement | allowance for mech items | 3 | 5264 | sf | 26646.508 | 35439.8556 | 0 | 0 | 1960 |  | 1960 |  |  | GF
UNIVERSITY ART GALLERY | UA | ELEC | 1707 | Branch Circuit Condition | "Basement Panel" Bulldog Pushmatic | Room 002 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs up-grade |  | GF
UNIVERSITY ART GALLERY | UA | ELEC | 1708 | Branch Circuit Condition | Square D QO | Room 002 | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1989 | 40 | 2029 | All breakers in panel are off. Needs investigation |  | GF
UNIVERSITY ART GALLERY | UA | ELEC | 1709 | Branch Circuit Condition | Bulldog Pushmatic | Room 108 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs up-grade |  | GF
UNIVERSITY ART GALLERY | UA | ELEC | 1710 | Branch Circuit Condition | Branch Circuits in Gallery | Room 105 | 3 | 3330 |  | 21070.6857 | 28024.012 | 0 | 0 | Unknown | 40 | 40 | See note 1 below |  | GF
UNIVERSITY ART GALLERY | UA | ELEC | 1711 | Lighting | 12" square recessed fixture with incandescant lamps | Room 108 | 3 | 2 | ea | 885.8547 | 1178.1867 | 0 | 0 | Unknown | 20 | 20 | Needs Up-Grade |  | GF
UNIVERSITY ART GALLERY | UA | ELEC | 1712 | Lighting | Wall mounted incandescant fixture | Rest room | 3 | 3 | ea | 1328.782 | 1767.28 | 0 | 0 | Unknown | 20 | 20 | Needs Up-Grade |  | GF
UNIVERSITY ART GALLERY | UA | ELEC | 1713 | Lighting | Track Lighting using MR16 Halogen lamps | Room 105 | 3 | 12 | ea | 6833.7359 | 9088.8688 | 0 | 0 | Unknown | 20 | 20 | Could be upgraded for energy savings |  | GF
UNIVERSITY ART GALLERY | UA | ELEC | 1714 | Lighting | Surface mounted Incandescent fixture | Entrance | 3 | 2 | ea | 885.8547 | 1178.1867 | 0 | 0 | Unknown | 20 | 20 | Needs Up-Grade |  | GF
BOVEE UNIVERSITY CENTER | UC | ARCH | 1715 | Envelope | Windows | Single Pane Alum | 3 | 990 | sf | 56378.3212 | 74983.1672 | 0 | 0 | 1960 | 30 | 1990 | Single pane alum. curtainwall recommended to be replaced. | Includes removing of old window, new aluminum framed window, caulk and minor finish patch around. | GF
BOVEE UNIVERSITY CENTER | UC | ARCH | 1716 | Envelope | Exterior Doors | Alum. Curtainwall | 3 | 25 | ea | 158188.3311 | 210390.4803 | 0 | 0 | 1960 | 30 | 1990 | Aluminum entry doors to be replaced. | Includes removal and replacement of new aluminum Entry Doors. | GF
BOVEE UNIVERSITY CENTER | UC | ARCH | 1717 | Envelope | Exterior Wall System | Alum. Curtainwall | 3 | 16660 | sf | 1265000.446 | 1682450.5932 | 0 | 0 | 1960 | 100 | 2060 | Ext. wall is full height curtainwall with transom panels. | Includes removal and replacement of curtain wall system and transom panels, caulking and minor finish patch and repair around new curtain wall. Added money to the unit cost because of the areas that being replaced and the added manpower and lifting equipment that i thought would be needed. | GF
BOVEE UNIVERSITY CENTER | UC | ARCH | 1718 | Envelope | Roof/Penetrations | Roof | 5 | 7800 | sf | 276386.6521 | 367594.2473 | 0 | 0 | 1960 - 2001 | 30 | 30 | Dome roof scheduled to be replaced immediately. | Price is for removing old roof and replacing it with a new dome roof. Price is for roofing only does not include any new structure or architectural finishes. | GF
BOVEE UNIVERSITY CENTER | UC | ARCH | 1719 | Floor Finishes | non skid flooring | food prep area | 3 |  |  | 0 | 0 | 0 | 0 | Unknown | 20 | 20 | Need area of non-skid flooring - SF and location to be confirmed |  | GF
BOVEE UNIVERSITY CENTER | UC | ARCH | 1720 | Conveying Systems | Elevators | cylinder replacement | 1 | 1 | ea | 0 | 0 | 0 | 0 | 1960 | 30 | 1990 | Recommended by Otis for 2014. |  | GF | 654345 | 2016-01-04 | 34500
BOVEE UNIVERSITY CENTER | UC | MECH | 1721 | Ventilation/Terminal Units | AHU/Chilled Cool/Hot Water Heat | AHU-1, Room 128 | 3 | 12250 | cfm | 155024.5645 | 206182.6707 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life | Price includes removing old unit, replacing it with new unit the same size and reconnecting to existing mains. Mech information was taken from drawing M-9 dated 9-12-68 | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1722 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-2, Room 128 | 3 | 12160 | cfm | 153885.6085 | 204667.8593 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1723 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-3, Above Rm. 226 | 3 | 13970 | cfm | 176791.2788 | 235132.4008 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1724 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-4, Above Rm. 226 | 3 | 7245 | cfm | 91685.9567 | 121942.3224 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1725 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-5, Above Rm. 226 | 3 | 3000 | cfm | 37965.1995 | 50493.7153 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1726 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-6, Bookstore storage | 3 | 4300 | cfm | 54416.7859 | 72374.3252 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1727 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-7, Rm. 304 | 3 | 5500 | cfm | 69602.8657 | 92571.8114 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1728 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-8, West bookstore storage | 3 | 8400 | cfm | 106302.5585 | 141382.4028 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1729 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-9, Rm. 304 | 3 | 7600 | cfm | 96178.5053 | 127917.412 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1730 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-10, Rm. 129 | 3 | 12400 | cfm | 156922.8244 | 208707.3565 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1731 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-11, Rm. 129 | 3 | 15000 | cfm | 189825.9973 | 252468.5764 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1732 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-12, Rm. 304A | 3 | 7500 | cfm | 94912.9987 | 126234.2882 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1733 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-13, Rm. 304A | 3 | 7270 | cfm | 92002.3334 | 122363.1034 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1734 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-14, Rm. 304A | 3 | 13500 | cfm | 170843.3976 | 227221.7188 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1735 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-15, Rm. 302C | 3 | 6100 | cfm | 77195.9056 | 102670.5544 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1736 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-16, Rm. 302C | 3 | 800 | cfm | 10124.0532 | 13464.9907 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1737 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-17, Rm. 304A | 3 | 3200 | cfm | 40496.2128 | 53859.963 | 0 | 0 | 1960 | 30 | 1990 | Replace nearing end of useful life |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1738 | Ventilation/Terminal Units | AHU/Chilled Cool/Hot Water Heat | AHU, Rm. 117 storage | 5 | 2 | Tons | 11389.5598 | 15148.1146 | 0 | 0 | 1960 | 30 | 1990 | Replace no longer functional | Unit is approx 2 tons? Yes. | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1739 | Ventilation/Terminal Units | Terminal units | Steam fin tube radiation, Entire Bldg. | 3 | 750 | lf | 265756.3962 | 353456.007 | 0 | 0 | 1960 | 25 | 1985 | Replace nearing end of useful life | Price is for replacing fin tube units and reconnecting to existing piping | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1740 | Ventilation/Terminal Units | Terminal units | Steam unit heater, Various locations | 3 | 13 | ea | 49354.7593 | 65641.8299 | 0 | 0 | Unknown | 30 | 30 | Good condition | Need Replacement? No. | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1741 | Chilled Water System | CHWPumps | Entire building, Rms. 129 & 304 | 3 | 6 | ea | 151860.7978 | 201974.8611 | 0 | 0 | 1970 | 20 | 1990 | Replace nearing end of useful life | Based off of circulating pump schedule on M-8 dated 1/9/59. Price is for replacement of same capacity pumps | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1742 | Chilled Water System | CHWPiping | Entire building | 4 | 150800 | sf | 944650.093 | 1256384.6237 | 0 | 0 | 1970 | 40 | 2010 | Replace nearing end of useful life | price is for replacing existing chilled water piping only. No other piping or mechanical units are included with the price | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1743 | Chilled Water System | CHWInsulation | Entire system | 3 | 150800 | sf | 229006.0831 | 304578.0906 | 0 | 0 | 1970 |  | 1970 | Replace with system upgrade |  | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1744 | Steam System | PRV Station | Various Mech. Rms. | 3 | 2 | ea | 265756.3962 | 353456.007 | 0 | 0 | 1960 | 50 | 2010 | Good condition | How Many? Need more information on what to price. Quantity and size undetermined as system was originally sized for steam absorption chillers which are no longer in service. Price is for replacing 2 heat exchangers. It is assumed there is one on room 128 and one in 129 | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1745 | Building Management | HVAC Control | Hybrid and straight pneumatic | 4 | 150800 | sf | 763353.6105 | 1015260.3019 | 0 | 0 | 1960 | 25 | 1985 | Replace with DDC system | Price is for replacing existing pneumatic controls with new DDC controls | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1746 | Storm/Sanitary sewer system | SSPiping | Entire building | 4 | 150800 | sf | 267173.7637 | 355341.1057 | 0 | 0 | 1960 | 40 | 2000 | Replace all drainage piping failures reported | Price is for replacing sanitary/storm pipe only. No other piping was included in this price | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1747 | Storm/Sanitary sewer system | Sump pumps | Rms. 128 & 129 | 3 | 2 | ea | 45558.2394 | 60592.4583 | 0 | 0 | Unknown | 10 | 10 | Replace as precautionary measure | How Many? One duplex per room. | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1748 | Domestic hot water system | DHWPiping | Entire building | 4 | 150800 | sf | 267173.7637 | 355341.1057 | 0 | 0 | 1948 | 40 | 1988 | Continue to upgrade piping | price is for replacing domestic hot water pipe only. No other piping was included in this price. | GF
BOVEE UNIVERSITY CENTER | UC | MECH | 1749 | Domestic hot water system | Heater | Entire building | 4 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1960 | 24 | 1984 | Replace nearing end of useful life no data available | What is being replaced (Heat Exchangers)? Single heat exchanger similar to Aerco SW1B08 | GF
BOVEE UNIVERSITY CENTER | UC | EH&S | 1750 | Environmental Health & Safety | Asbestos abatement | allowance for mech items | 3 | 150800 | sf | 763353.6105 | 1015260.3019 | 0 | 0 | Unknown |  | 0 |  | assumes all related to 3,4 and 5 items | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1751 | Branch Circuit | Unmarked Square D QO | Room 223 | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1983 | 40 | 2023 | Appears full | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1752 | Branch Circuit | Panel LP1C | Room 212 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1753 | Branch Circuit | Panel LPE1 | Next to Room 210 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1754 | Branch Circuit | Panel LP1D | Mech Room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1755 | Branch Circuit | Panel 1 | Book Store | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1756 | Branch Circuit | Panel 2 | Book Store | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1757 | Branch Circuit | Unmarked Square D QO | Book Store | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1983 | 40 | 2023 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1758 | Branch Circuit | Unmarked Square D QO | Book Store | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1983 | 40 | 2023 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1759 | Branch Circuit | Unmarked Square D QO | Book Store | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1983 | 40 | 2023 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1760 | Branch Circuit | Panel LP9 | Book Store | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1983 | 40 | 2023 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1761 | Branch Circuit | Panel LPH | Book Store Storeroom | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1762 | Branch Circuit | Unmarked Square D I-Line panel | Mech Room | 3 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1763 | Branch Circuit | Panel LPT | Mech Room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1764 | Branch Circuit | Panel LPGE | By Room 121 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1765 | Branch Circuit | Panel LPGC | By Room 121 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1766 | Branch Circuit | Unmarked Square D Safeflex MCC | Room 129 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1767 | Branch Circuit | Unmarked Square D Safeflex MCC | Room 129 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1768 | Branch Circuit | Unmarked Square D QO Panel | Room 129 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1769 | Branch Circuit | Panel LP-10 | Room 129 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1770 | Branch Circuit | Panel LPZ | Room 129 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1771 | Branch Circuit | Panel PPB | Rotunda Mech.room | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1772 | Branch Circuit | Panel LP1A | By room 226 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1773 | Branch Circuit | Panel LP-1B | By room 226 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1774 | Branch Circuit | Panel PPE | Kitchen | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1775 | Branch Circuit | Unmarked Old GE panel | Room 304 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1776 | Branch Circuit | Unmarked Square D Safeflex MCC | Room 304A | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1777 | Branch Circuit | Unmarked Square D Safeflex MCC | Room 304A | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1778 | Branch Circuit | Unmarked Square D QO | Room 304A | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Needs Upgrade | price includes replacing panel only, reusing existing feeders | GF
BOVEE UNIVERSITY CENTER | UC | ELEC | 1779 | Lighting | Four foot surface mount wraparounds | Corridor | 3 | 70 | 1 | 31004.9129 | 41236.5341 | 0 | 0 | Unknown | 20 | 20 | Upgrade with renovation | Price is for replacing corridor wraparound fixtures with new fixture. Count was taken from corridors from the ground and first floors. | GF
BOVEE UNIVERSITY CENTER | UC | LSAF | 1780 | Life Safety | Battery pack Egress lighting | Bld. | 3 | 30 | ea | 9491.2999 | 12623.4288 | 0 | 0 | Unknown | 20 | 20 | Upgrade with renovation | Price is for 30 wall mounted emergency lights | GF
MARGO JONKER VARSITY SOFTBALL | VS | ARCH | 1781 | Envelope | Dugout walls | Entry/exit | 4 | 24 | lf | 15186.0798 | 20197.4861 | 0 | 0 | 1997 | 40 | 2037 | Remove CMU wall and replace with poured concrete (24' +/-) | Price is for rermoving existing CMU walls, pouring new concrete walls, waterproofing new walls and painting. Does not include new foundation for wall - assumes reusing existing CMU wall footing | GF
MARGO JONKER VARSITY SOFTBALL | VS | ARCH | 1782 | Envelope | Dugout heating | Visitors | 4 |  |  | 0 | 0 | 0 | 0 | n/a | n/a | 0 | Install heating to match home team - Cap Project? |  | GF
MARGO JONKER VARSITY SOFTBALL | VS | ARCH | 1783 | Envelope | Out door batting cages |  | 4 |  |  | 0 | 0 | 0 | 0 | 1997 | 40 | 2037 | Replace cage structure, netting and concrete slab with turf topping |  | GF
MARGO JONKER VARSITY SOFTBALL | VS | ARCH | 1784 | Envelope | Pitching bullpen |  | 4 |  |  | 0 | 0 | 0 | 0 | 1997 | 40 | 2037 | Reconfigure or add protective fence - Cap Proj? |  | GF
MARGO JONKER VARSITY SOFTBALL | VS | ARCH | 1785 | Interior Structure | Floor Finishes |  | 4 | 500 | sf | 3796.5199 | 5049.3715 | 0 | 0 | 1997 | 15 | 2012 | Carpet in press box should be replaced |  | GF
MARGO JONKER VARSITY SOFTBALL | VS | ELEC | 1786 | Exterior Lighting | Building Mounted |  | 4 | 12 | ea | 7593.0399 | 10098.7431 | 0 | 0 | 1997 | 20 | 2017 | Six 100W MH in the front, lenses are bad. Replace with new. Add six new along the back for security |  | GF
MARGO JONKER VARSITY SOFTBALL | VS | COMM | 1787 | Communications/Security |  |  | 4 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1997 | 10 | 2007 | Sound system speakers need replacement | May need to discuss more detail with CMU | GF
MARGO JONKER VARSITY SOFTBALL | VS | LSAF | 1788 | Life Safety | Emergency Lighting | Emerg. Battery Units | 3 | 5 | ea | 949.13 | 1262.3429 | 0 | 0 | 1997 | 20 | 2017 | Normal battery replacement |  | GF
WARRINER HALL | WA | ARCH | 1789 | Envelope | Windows | Building Exterior | 3 | 145 | ea | 220198.1569 | 292863.5486 | 0 | 0 | 1992 | 30 | 2022 | Windows need balances replaced. | Price is for replacing balances and refinishing 50% of the windows in the offices. Windows in the stairways were not included | GF
WARRINER HALL | WA | ARCH | 1790 | Envelope | Exterior Doors | Building Entrances | 3 | 11 | ea | 69602.8657 | 92571.8114 | 0 | 0 | 1956 | 30 | 1986 | Exterior doors to be replaced with new alum. doors to match new standard. | Price is for removing old doors and replacing them with new alum framed entry doors | GF
WARRINER HALL | WA | ARCH | 1791 | Envelope | Exterior Walls | Brick | 3 | 500 | sf | 15818.8331 | 21039.048 | 0 | 0 | 1928 | 100 | 2028 | Brick refurbished 2007. Tuck pointing and masonry repair required. |  | GF
WARRINER HALL | WA | ARCH | 1792 | Envelope | Roof | Roof Areas | 4 | 11580 | sf | 337055.0408 | 448283.2043 | 0 | 0 | 1987 | 30 | 2017 | Roof Areas 02, 03, 05, 06, 08 and 09 scheduled to be repaired. | Price is for removing and replacing existing roof in areas 02,03,05,06,08,09. (About 11,580 SF) | GF
WARRINER HALL | WA | ARCH | 1793 |  | Toilet Rooms |  | 3 | 1820 | sf | 172741.6575 | 229746.4045 | 0 | 0 | 1948 | 40 | 1988 | Finishes are original. | Price is for updating bathroom finishes only. No abatement was included | GF
WARRINER HALL | WA | ARCH | 1794 | Floor Finish | Composite Tile | Corridors | 3 | 9555 | sf | 60459.5801 | 80411.2416 | 0 | 0 | 1960 |  | 1960 | Corridor tile in need of replacement. | Price is for removing existing VCT in the corridors and replacing it with new. No abetment included | GF
WARRINER HALL | WA | ARCH | 1795 | Floor Finish | Carpet | Offices | 3 |  |  | 0 | 0 | 0 | 0 | Unknown | 15 | 15 |  |  | GF
WARRINER HALL | WA | ARCH | 1796 | Ceiling Finish | Acoustical Tile | Interior Corridors | 3 | 9555 | sf | 78597.4542 | 104534.6141 | 0 | 0 | 1960 | 20 | 1980 | Corridor ceilings replaced with 2' x 2' lay-in ceiling tile. | price is for removing existing corridor ceiling and replacing it with ACT Ceiling | GF
WARRINER HALL | WA | ADAC | 1797 | BF/ADA Compliance | Exterior Doors | Building Exterior | 3 | 6 | ea | 45558.2394 | 60592.4583 | 0 | 0 | 1956 | 30 | 1986 | Exterior access path meets ADA requirements, doors to be replaced. | Price is for adding automatic openers to 6 doors | GF
WARRINER HALL | WA | ADAC | 1798 | BF/ADA Compliance | Interior Doors | Offices / Classrooms | 3 | 211 | ea | 133510.9514 | 177569.5654 | 0 | 0 | Unknown | 40 | 40 | Classroom hardware does not meet ADA requirements. |  | GF
WARRINER HALL | WA | EH&S | 1799 | Environmental Health and Safety | Asbestos abatement for arch items | Allowance | 3 | 19110 | sf | 157194.9084 | 209069.2281 | 0 | 0 | Unknown |  | 0 |  |  | GF
WARRINER HALL | WA | MECH | 1800 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU Pres., Basement Mech. Rm. | 3 | 12510 | cfm | 158314.8818 | 210558.7927 | 0 | 0 | >30 years | 30 | 30 | Replace nearing end of useful life | Price is for replacing existing unit with a new unit the same size and reconnect to existing mains. Information was taken from mechanical drawings dated 10-5-83 | GF
WARRINER HALL | WA | MECH | 1801 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | Auditorium, Basement Mech. Rm. | 4 | 1 | ea | 253101.3297 | 336624.7686 | 0 | 0 | 1928 | 30 | 1958 | Replace nearing end of useful life | Cannot find information on Units, what should be replaced? This is the original built up ventilation unit for the auditorium. It should be replaced with new equipment sized to handle the auditorium. Budget price based off of AHU 2 and 3. Further discussion is needed to define scope and requirements | GF
WARRINER HALL | WA | MECH | 1802 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-2, East attic | 3 | 14610 | cfm | 184890.5214 | 245904.3934 | 0 | 0 | aprox. 1989 | 30 | 30 | Replace with new unit sized for the current space requirements. |  | GF
WARRINER HALL | WA | MECH | 1803 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-3, West attic | 3 | 15670 | cfm | 198304.8918 | 263745.5062 | 0 | 0 | aprox. 1989 | 30 | 30 | Replace with new unit sized for the current space requirements. |  | GF
WARRINER HALL | WA | MECH | 1804 | Ventilation/Terminal Units | AHU/Chilled Cool/Steam Heat | AHU-4, Center attic | 3 | 1 | ea | 253101.3297 | 336624.7686 | 0 | 0 | aprox. 1989 | 30 | 30 | Replace with new unit sized for the current space requirements. | Cannot find information on Units, what should it be replaced with? This unit is a multi zone unit with 3 hp supply fan and 1.5 hp return fan. Capacity was reported to be an issue with AHU-2, 3 & 4. Budget price based off of AHU 2 and 3. Further discussion is needed to define scope and requirements | GF
WARRINER HALL | WA | MECH | 1805 | Ventilation/Terminal Units | Terminal units | Steam radiation, Entire Bldg. | 3 | 350 | lf | 212605.117 | 282764.8056 | 0 | 0 | 1928 | 25 | 1953 | Replace nearing end of useful life | Quantity was taken from mechanical drawings dated 5-15-56 | GF
WARRINER HALL | WA | MECH | 1806 | Chilled Water System | Pumps | Entire building, Basement Mech. Rm. | 3 | 3 | ea | 75930.3989 | 100987.4306 | 0 | 0 | >30 years | 20 | 20 | Replace nearing end of useful life |  | GF
WARRINER HALL | WA | MECH | 1807 | Chilled Water System | Insulation | Entire system | 3 | 76000 | sf | 115414.2064 | 153500.8945 | 0 | 0 | >30 years |  | 0 | Replace nearing end of useful life | Price is for replacing insulation for chilled water system | GF
WARRINER HALL | WA | MECH | 1808 | Steam System | Insulation | Entire system | 4 | 76000 | sf | 115414.2064 | 153500.8945 | 0 | 0 | 1928 |  | 1928 | Replace pipe insulation with fiberglass |  | GF
WARRINER HALL | WA | MECH | 1809 | Steam System | Piping | Entire building | 4 | 76000 | sf | 254873.039 | 338981.1419 | 0 | 0 | 1928 | 50 | 1978 | Replace nearing end of useful life, failures reported |  | GF
WARRINER HALL | WA | MECH | 1810 | Building Management | HVAC Control | Hybrid and straight pneumatic | 3 | 76000 | sf | 384714.0212 | 511669.6482 | 0 | 0 | Unknown | 20 | 20 | Replace with DDC system |  | GF
WARRINER HALL | WA | MECH | 1811 | Storm/Sanitary Sewer System | Piping | Entire building | 4 | 76000 | sf | 254873.039 | 338981.1419 | 0 | 0 | 1928 | 40 | 1968 | Replace original drainage piping, failures reported |  | GF
WARRINER HALL | WA | MECH | 1812 | Storm/Sanitary Sewer System | Sump pump | Basement mechanical rooms | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown | 10 | 10 | Replace as precautionary measure |  | GF
WARRINER HALL | WA | MECH | 1813 | Domestic cold water system | Piping | Entire building | 4 | 76000 | sf | 254873.039 | 338981.1419 | 0 | 0 | 1928 | 40 | 1968 | Replace nearing end of useful life, failures reported |  | GF
WARRINER HALL | WA | MECH | 1814 | Domestic hot water system | Piping | Entire building | 4 | 76000 | sf | 254873.039 | 338981.1419 | 0 | 0 | 1928 | 40 | 1968 | Replace nearing end of useful life, failures reported |  | GF
WARRINER HALL | WA | MECH | 1815 | Domestic hot water system | Heater/Steam | Entire building | 3 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1956 | 24 | 1980 | Replace nearing end of useful life | What is being replaced. Domestic hot water heater? Replacing domestic hot water heater similar to AMERCO SW1B08. | GF
WARRINER HALL | WA | MECH | 1816 | Fire protection system | Piping | Stage area & stairwells | 3 | 76000 | sf | 0 | 0 | 0 | 0 | Unknown | 40 | 40 | Good condition, when feasible extend coverage to entire structure | Is this part of our scope? No, only if scope of future renovation would require it. | GF
WARRINER HALL | WA | EH&S | 1817 | Environmental Health and Safety | Asbestos abatement for mech items | allowance | 4 | 76000 | sf | 384714.0212 | 511669.6482 | 0 | 0 | Unknown |  | 0 |  |  | GF
WARRINER HALL | WA | ELEC | 1818 | Distribution | Unmarked Panel | Basement | 3 | 2 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 1970 | 40 | 2010 | Full |  | GF
WARRINER HALL | WA | ELEC | 1819 | Distribution | Panel 1 | Basement | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | Full |  | GF
WARRINER HALL | WA | ELEC | 1820 | Distribution | Panel 2 | Basement | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | Full |  | GF
WARRINER HALL | WA | ELEC | 1821 | Distribution | Panel 3 | Basement | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | Full |  | GF
WARRINER HALL | WA | ELEC | 1822 | Distribution | Panel 4 | Basement | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Full |  | GF
WARRINER HALL | WA | ELEC | 1823 | Branch Circuit Condition | Panel LPA | Basement | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | Full |  | GF
WARRINER HALL | WA | ELEC | 1824 | Branch Circuit Condition | Panel MLO | Basement | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade |  | GF
WARRINER HALL | WA | ELEC | 1825 | Branch Circuit Condition | Unmarked Panel | Room A | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade |  | GF
WARRINER HALL | WA | ELEC | 1826 | Branch Circuit Condition | Unmarked Panel | Room A | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade |  | GF
WARRINER HALL | WA | ELEC | 1827 | Branch Circuit Condition | Unmarked Panel | By Room 121 | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade |  | GF
WARRINER HALL | WA | ELEC | 1828 | Branch Circuit Condition | Unmarked Panel | By Room 121 | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade |  | GF
WARRINER HALL | WA | ELEC | 1829 | Branch Circuit Condition | Unmarked Panel | By room 215 | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade |  | GF
WARRINER HALL | WA | ELEC | 1830 | Branch Circuit Condition | Unmarked Panel | By room 215 | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade |  | GF
WARRINER HALL | WA | ELEC | 1831 | Branch Circuit Condition | Unmarked Panel | By room 204 | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade |  | GF
WARRINER HALL | WA | ELEC | 1832 | Branch Circuit Condition | Unmarked Panel | By room 204 | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade |  | GF
WARRINER HALL | WA | ELEC | 1833 | Branch Circuit Condition | Unmarked Panel | By room 304 | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade |  | GF
WARRINER HALL | WA | ELEC | 1834 | Branch Circuit Condition | Unmarked Panel | By room 319 | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1960 | 40 | 2000 | Needs upgrade |  | GF
WARRINER HALL | WA | ELEC | 1835 | Lighting | 4 Foot fluorescent Strip Lights (hidden) | !st Floor Corridor | 3 |  |  | 0 | 0 | 0 | 0 | Unknown | 20 | 20 | Couldn’t see if they were T-8 lamps |  | GF
WARRINER HALL | WA | ELEC | 1836 | Lighting | 2x4 Surface mounted Fluorescent Parabolic Fixtures | 1st Floor offices | 3 | 275 | ea | 121805.0149 | 162000.6699 | 0 | 0 | Unknown | 20 | 20 | Could be upgraded for energy savings |  | GF
WARRINER HALL | WA | ELEC | 1837 | Lighting | 4 Foot surface mounted wraparound fluorescent fixtures | 2nd Floor Offices | 3 | 214 | ea | 94786.448 | 126065.9758 | 0 | 0 | Unknown | 20 | 20 | Could be upgraded for energy savings |  | GF
WARRINER HALL | WA | ELEC | 1838 | Lighting | 4 Foot fluorescent Strip Lights (hidden) | 2nd Floor Corridor | 3 |  |  | 0 | 0 | 0 | 0 | Unknown | 20 | 20 | Couldn’t see if they were T-8 lamps |  | GF
WARRINER HALL | WA | ELEC | 1839 | Lighting | 2x4 Fluorescent troffers | 3rd Floor offices | 3 | 220 | ea | 97444.0119 | 129600.5359 | 0 | 0 | Unknown | 20 | 20 | Could be upgraded for energy savings |  | GF
WARRINER HALL | WA | ELEC | 1840 | Lighting | 2x2 surface mounted fluorescent fixtures | 3rd Floor Corridor | 3 | 60 | ea | 26575.6396 | 35345.6007 | 0 | 0 | Unknown | 20 | 20 | Could be upgraded for energy savings |  | GF
WARRINER HALL | WA | ELEC | 1841 | Lighting | 4 Foot fluorescent Strip Lights (hidden) | 4th Floor Corridor | 3 |  |  | 0 | 0 | 0 | 0 | Unknown | 20 | 20 | Couldn’t see if they were T-8 lamps |  | GF
WARRINER HALL | WA | SUST | 1842 | Lighting Controls | Occupancy Sensors | Building | 3 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | Only in a few locations |  | GF
WARRINER HALL | WA |  | 1843 | Life Safety | Egress Lighting | Building | 3 | 60 | ea | 37965.1995 | 50493.7153 | 0 | 0 | Unknown | 20 | 20 | Needs Upgrade with Renovation |  | GF
WEST HALL | WE | ARCH | 1844 | Envelope | Windows | Alum. Single Pane | 4 | 1015 | sf | 70646.9087 | 93960.3885 | 0 | 0 | 1955 | 30 | 1985 | Replace single pane aluminum windows. | Double check any glazed brick | GF
WEST HALL | WE | ARCH | 1845 | Envelope | Exterior Doors | Alum. / H.M. | 3 | 4 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1955 | 30 | 1985 | Replace alum. doors. H.M. doors to remain. |  | GF
WEST HALL | WE | ARCH | 1846 | Envelope | Roof/Penetrations | Composite / Conc. | 4 | 2650 | sf | 77132.6302 | 102586.3982 | 0 | 0 | 1948-1955 | 30 | 30 |  |  | GF
WEST HALL | WE | ARCH | 1847 | Interior Structure | Toilet Rooms | First Floor | 3 | 80 | sf | 10124.0532 | 13464.9907 | 0 | 0 | 1948-1990 | 30 | 30 | One toilet room is ADA accessible, one is not. | Renovate non ADA-accessible toilet. | GF
WEST HALL | WE | EH&S | 1848 | Environmental Health & Safety | Asbestos Abatement | Allowance for arch items | 3 |  |  | 10724.6326 | 14263.7614 | 0 | 0 | Unknown |  | 0 |  |  | GF
WEST HALL | WE | ADAC | 1849 | BF/ADA Compliance | Entry Doors |  | 3 | 1 | ea | 7593.0399 | 10098.7431 | 0 | 0 | Unknown | 40 | 40 |  | add automatic opener at front door. One exists at rear door. | GF
WEST HALL | WE | MECH | 1850 | Ventilation/Terminal Units | AHU/Split DX/Steam Heat | AHU-1, Up Mech. Rm. | 3 | 15 | tons | 85421.6988 | 113610.8594 | 0 | 0 | 1985 | 15 | 2000 | Replace nearing end of useful life |  | GF
WEST HALL | WE | MECH | 1851 | Ventilation/Terminal Units | RTU/DX Cool/Steam Heat | RTU-1, South roof | 4 | 5 | tons | 28473.8996 | 37870.2865 | 0 | 0 | 1992 | 15 | 2007 | Replace nearing end of useful life |  | GF
WEST HALL | WE | MECH | 1852 | Ventilation/Terminal Units | Terminal units | Steam radiation, First Floor | 3 | 50 | lf | 18982.5997 | 25246.8576 | 0 | 0 | 1957 | 25 | 1982 | Replace nearing end of useful life |  | GF
WEST HALL | WE | MECH | 1853 | Building Management | HVAC Control | Hybrid and straight pneumatic | 3 | 9168 | sf | 69612.5178 | 92585.7534 | 0 | 0 | 1985 | 20 | 2005 | Replace with DDC system. Unit price is increased because of the small SF area |  | GF
WEST HALL | WE | MECH | 1854 | Storm/Sanitary Sewer System | Piping | Entire building | 3 | 9168 | sf | 46408.7027 | 61723.4781 | 0 | 0 | 1948 | 40 | 1988 | Good condition, no reported problems |  | GF
WEST HALL | WE | MECH | 1855 | Storm/Sanitary Sewer System | Sump pump | Basement Mech. Rm. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown | 10 | 10 | Replace as a precautionary measure |  | GF
WEST HALL | WE | MECH | 1856 | Domestic cold water system | Piping | Entire building | 3 | 9168 | sf | 46408.7027 | 61723.4781 | 0 | 0 | 1928 | 40 | 1968 | Replace remaining iron water piping with future building renovation |  | GF
WEST HALL | WE | MECH | 1857 | Domestic hot water system | Piping | Entire building | 3 | 9168 | sf | 46408.7027 | 61723.4781 | 0 | 0 | 1928 | 40 | 1968 | Replace remaining iron water piping with future building renovation |  | GF
WEST HALL | WE | EH&S | 1858 | Environmental Health & Safety | asbestos abatement | allowance for mech items | 3 | 9168 | sf | 46408.6598 | 61723.5176 | 0 | 0 | 1928 |  | 1928 |  |  | GF
WEST HALL | WE | ELEC | 1859 | Branch Circuit | Old Westinghouse 480 volt panel | Room 113 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1957 | 40 | 1997 | Needs upgrade |  | GF
WEST HALL | WE | ELEC | 1860 | Branch Circuit | Unmarked Square D QO | Room 101C | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1957 | 40 | 1997 | Needs upgrade |  | GF
WEST HALL | WE | ELEC | 1861 | Branch Circuit | Old Westinghouse 120/240 volt panel | Room 113 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1957 | 40 | 1997 | Needs upgrade |  | GF
WEST HALL | WE | ELEC | 1862 | Branch Circuit | Panel PP-2 | Room 113 | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1957 | 40 | 1997 | Needs upgrade |  | GF
WEST HALL | WE | ELEC | 1863 | Lighting | 2x4 fluorescent troffers with T-12's & T-8's | Interior | 3 | 9168 | sf | 92817.4054 | 123446.9562 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade |  | GF
WEST HALL | WE | ELEC | 1864 | Lighting | Wall mounted fixtures | Exterior | 3 | 8 | ea | 5062.0266 | 6732.4954 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade |  | GF
WEST HALL | WE | ELEC | 1865 | Lighting | Controls | Bld | 3 | 9168 | sf | 17456.4845 | 23145.9021 | 0 | 0 | Unknown |  | 0 | None |  | GF
WEST HALL | WE | LSAF | 1866 | Life Safety | Egress Lighting | Bld | 3 | 12 | sf | 7593.0399 | 10098.7431 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
WEST HALL | WE | LSAF | 1867 | Life Safety | Emergency power | Bld | 3 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | None | Capital improvement | GF
WEST HALL | WE | LSAF | 1868 | Life Safety | Fire Alarm | Building | 3 | 9168 | sf | 58010.8248 | 77154.397 | 0 | 0 | Unknown | 40 | 40 | Needs upgrade with renovation |  | GF
WEST HALL | WE | ELEC | 1869 | Security |  | Building | 3 | 9168 | sf | 34806.7952 | 46292.8767 | 0 | 0 | Unknown |  | 0 | Determine areas needed - price is an allowance |  | GF
WEST HALL | WE | LSAF | 1870 | Life Safety | Area of Refuge | Allowance | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | GF
WIGHTMAN HALL | WI | ARCH | 1871 | Envelope | Windows | Original building | 3 | 146 | ea | 145963.5369 | 194131.504 | 0 | 0 | 1990 | 100 | 2090 | Repair windows to be fully operable. |  | GF
WIGHTMAN HALL | WI | ARCH | 1872 | Envelope | Exterior Doors | Building Exterior | 3 | 13 | ea | 82257.9322 | 109403.0498 | 0 | 0 | 1990 | 30 | 2020 | Consider replacement to match new campus standard. |  | GF
WIGHTMAN HALL | WI | ARCH | 1873 | Envelope | Exterior Walls | Brick | 3 | 500 | sf | 15818.8331 | 21039.048 | 0 | 0 | 1946 | 100 | 2046 | Brick in good condition but needs tuck pointing in areas. |  | GF
WIGHTMAN HALL | WI | ARCH | 1874 | Envelope | Roof | Partial Roof Area 10 | 4 | 3000 | sf | 87319.9588 | 116135.5452 | 0 | 0 | 1990 | 1-3 years | 1990 | Roof report indicates a portion of Roof Area 10 is scheduled to be replaced. | Replacement Scheduled | GF
WIGHTMAN HALL | WI | ARCH | 1875 | Interior Structure | Toilet Rooms | Second Floor | 3 | 270 | sf | 34168.6795 | 45444.3438 | 0 | 0 | 1946 | 30 | 1976 | Finishes are original. | Price Complete Renovation. Price is for renovation to make bathrooms ADA compliant | GF
WIGHTMAN HALL | WI | ARCH | 1876 | Floor Finish | Terrazzo Floor | First Floor Corridor | 3 | 2500 | sf | 50620.2659 | 67324.9537 | 0 | 0 | 1946 | 40 | 1986 | Repair cracks in terrazzo floor. |  | GF
WIGHTMAN HALL | WI | ARCH | 1877 | Floor Finish | Resilient Tile | Second Floor corridor | 3 | 1090 | sf | 6207.3101 | 8255.7224 | 0 | 0 | 1969 | 30 | 1999 | Consider replacement. |  | GF
WIGHTMAN HALL | WI | ARCH | 1878 | Ceiling Finish | Acoustical Tile | Corridors, Classrooms, Offices | 3 | 13500 | sf | 111048.2084 | 147694.1172 | 0 | 0 | 1969 | 20 | 1989 | Consider installing new acoustical lay-in ceiling in corridors. | Unit price was increased because of the added demo of the plaster ceiling | GF
WIGHTMAN HALL | WI | ARCH | 1879 | Fixed Equipment / Furn. | Display Cases | First Floor Corridor | 4 | 3 | ea | 1898.26 | 2524.6858 | 0 | 0 | Unknown |  | 0 | Consider removing and patching opening. |  | GF
WIGHTMAN HALL | WI | ADAC | 1880 | BF/ADA Compliance | Interior Doors | Classrooms / Offices | 3 | 22 | ea | 13920.5731 | 18514.3623 | 0 | 0 | Varies |  | 0 | Hardware is knob-type. |  | GF
WIGHTMAN HALL | WI | ADAC | 1881 | BF/ADA Compliance | Toilet Rooms |  | 3 | 5 | ea | 0 | 0 | 0 | 0 | 1946 | 30 | 1976 | First floor toilet rooms are ADA-accessible. | Same as above | GF
WIGHTMAN HALL | WI | EH&S | 1882 | Environmental Health & Safety | Asbestos Abatement | Allowance for arch items | 3 |  |  | 174981.6043 | 232725.5337 | 0 | 0 | Unknown |  | 0 |  |  | GF
WIGHTMAN HALL | WI | MECH | 1883 | Ventilation/Terminal Units | AHU/Split DX/Steam Heat | SAF-1, Attic above Rm.291 | 4 | 40 | Tons | 155201.7354 | 206418.3081 | 0 | 0 | 1948 | 30 | 1978 | Replace nearing end of useful life |  | GF
WIGHTMAN HALL | WI | MECH | 1884 | Ventilation/Terminal Units | RTU/DX | RTU-1, Roof above Rm 150 | 4 | 55 | Tons | 213402.3862 | 283825.1736 | 0 | 0 | 1989 | 15 | 2004 | Replace nearing end of useful life |  | GF
WIGHTMAN HALL | WI | MECH | 1885 | Ventilation/Terminal Units | RTU/DX | RTU-4, Roof above Rm 113 | 4 | 10 | Tons | 38800.4338 | 51604.577 | 0 | 0 | 1989 | 15 | 2004 | Replace nearing end of useful life |  | GF
WIGHTMAN HALL | WI | MECH | 1886 | Ventilation/Terminal Units | RTU/DX | RTU-5, Roof above Rm 110 | 4 | 20 | Tons | 77600.8677 | 103209.154 | 0 | 0 | 1989 | 15 | 2004 | Replace nearing end of useful life |  | GF
WIGHTMAN HALL | WI | MECH | 1887 | Ventilation/Terminal Units | RTU/DX/Nat. Gas Heat | RTU-6, Roof above Rm 161 | 4 | 17 | Tons | 65960.7375 | 87727.7809 | 0 | 0 | 1985 | 15 | 2000 | Replace nearing end of useful life |  | GF
WIGHTMAN HALL | WI | MECH | 1888 | Ventilation/Terminal Units | AHU | Abandoned, Old welding shop | 4 |  |  | 6479.394 | 8617.5941 | 0 | 0 | 1989 | 30 | 2019 | Remove with future renovation |  | GF
WIGHTMAN HALL | WI | MECH | 1889 | Ventilation/Terminal Units | Terminal units | Steam fin tube radiation, Entire Bldg. | 3 | 26 | ea | 98709.5186 | 131283.6597 | 0 | 0 | 1948 | 25 | 1973 | Good condition | performing past useful life | GF
WIGHTMAN HALL | WI | MECH | 1890 | Ventilation/Terminal Units | Terminal units | Steam unit heater, Various locations | 3 | 8 | ea | 32396.9702 | 43087.9704 | 0 | 0 | Unknown | 20 | 20 | Good condition | performing past useful life | GF
WIGHTMAN HALL | WI | MECH | 1891 | Steam System | PRV Station |  | 4 | 1 | ea | 132878.1981 | 176728.0035 | 0 | 0 | 1948 | 50 | 1998 | Good condition |  | GF
WIGHTMAN HALL | WI | MECH | 1892 | Steam System | Insulation | Entire building | 4 | 47700 | sf | 72437.6006 | 96342.0088 | 0 | 0 | 1948 |  | 1948 | Good condition | performing past useful life | GF
WIGHTMAN HALL | WI | MECH | 1893 | Steam System | Piping | Entire building | 4 | 47700 | sf | 150911.6679 | 200712.5182 | 0 | 0 | 1948 | 50 | 1998 | Good condition | performing past useful life | GF
WIGHTMAN HALL | WI | MECH | 1894 | Building Management | HVAC Control | Hybrid and straight pneumatic | 4 | 47700 | sf | 241458.6686 | 321140.0292 | 0 | 0 | 1948--1970 | 20 | 20 | Replace with DDC system |  | GF
WIGHTMAN HALL | WI | MECH | 1895 | Storm/Sanitary sewer system | Piping | Entire building | 4 | 47700 | sf | 150911.6679 | 200712.5182 | 0 | 0 | 1948 | 40 | 1988 | Replace with future renovations |  | GF
WIGHTMAN HALL | WI | MECH | 1896 | Storm/Sanitary sewer system | Sump pump | Basement Mech. Rm. | 4 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | 1948 | 10 | 1958 | Replace nearing end of useful life |  | GF
WIGHTMAN HALL | WI | MECH | 1897 | Domestic hot water system | Piping | Entire building | 4 | 47700 | sf | 172039.3014 | 228812.2708 | 0 | 0 | 1948 | 40 | 1988 | Continue to upgrade piping |  | GF
WIGHTMAN HALL | WI | MECH | 1898 | Domestic hot water system | Heater | Entire building | 4 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1948 | 24 | 1972 | Replace heater | What is the scope and quantity? | GF
WIGHTMAN HALL | WI | MECH | 1899 | Natural gas piping system | Piping | 2 services, serve various locations | 3 |  |  | 0 | 0 | 0 | 0 | 1989 | 40 | 2029 | Good condition, repaint exterior piping | O&M item? | GF
WIGHTMAN HALL | WI | EH&S | 1900 | Environmental Health & Safety | Asbestos abatement | allowance for mech | 3 | 47700 | sf | 241458.6686 | 321140.0292 | 0 | 0 | 1948 |  | 1948 |  |  | GF
WIGHTMAN HALL | WI | ELEC | 1901 | Distribution | Panel D 1 | Basement | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1940 | 40 | 1980 | needs replacement |  | GF
WIGHTMAN HALL | WI | ELEC | 1902 | Distribution | Old Panels | Basement | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1950 | 40 | 1990 | needs replacement |  | GF
WIGHTMAN HALL | WI | ELEC | 1903 | Branch Circuits | 2 abandoned Switches | Basement | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 | needs removal |  | GF
WIGHTMAN HALL | WI | ELEC | 1904 | Branch Circuits | Old fire Alarm | Basement | 4 | 47700 | sf | 301823.3357 | 401425.0365 | 0 | 0 | 1950 | 40 | 1990 | grandfathered under prior code |  | GF
WIGHTMAN HALL | WI | ELEC | 1905 | Branch Circuits | Simplex Fire Alarm | Basement | 3 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 1970 | 40 | 2010 | only feeds part of bld |  | GF
WIGHTMAN HALL | WI | ELEC | 1906 | Branch Circuits | unmarked panel | 190 | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | Full |  | GF
WIGHTMAN HALL | WI | ELEC | 1907 | Branch Circuits | Panel MM | 119 | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1980 | 40 | 2020 | Full |  | GF
WIGHTMAN HALL | WI | ELEC | 1908 | Branch Circuits | Panel KPL | 113 | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1980 | 40 | 2020 | Full |  | GF
WIGHTMAN HALL | WI | ELEC | 1909 | Branch Circuits | Panel KKR | 115 | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1980 | 40 | 2020 | Full |  | GF
WIGHTMAN HALL | WI | ELEC | 1910 | Branch Circuits | unmarked panel | 199 | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1955 | 40 | 1995 | full |  | GF
WIGHTMAN HALL | WI | ELEC | 1911 | Branch Circuits | Panel FF | 135 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 1980 | 40 | 2020 | 2 spares |  | GF
WIGHTMAN HALL | WI | ELEC | 1912 | Branch Circuits | Panel CC | 144B | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1980 | 40 | 2020 | Full |  | GF
WIGHTMAN HALL | WI | ELEC | 1913 | Branch Circuits | Panel 1-B 1200 A.main | 150 | 3 | 1 | ea | 60744.3191 | 80789.9445 | 0 | 0 | 1980 | 40 | 2020 | Full |  | GF
WIGHTMAN HALL | WI | ELEC | 1914 | Branch Circuits | Panel AAR | 150 | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1980 | 40 | 2020 | Full |  | GF
WIGHTMAN HALL | WI | ELEC | 1915 | Branch Circuits | Panel AAL | 150 | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1980 | 40 | 2020 | Full |  | GF
WIGHTMAN HALL | WI | ELEC | 1916 | Branch Circuits | Panel C | 150 | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1980 | 40 | 2020 | Full |  | GF
WIGHTMAN HALL | WI | ELEC | 1917 | Branch Circuits | Panel G | 225 mens RR | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 40 | 2010 | Full |  | GF
WIGHTMAN HALL | WI | ELEC | 1918 | Branch Circuits | Panel LL | 290 | 3 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1980 | 40 | 2020 | Full |  | GF
WIGHTMAN HALL | WI | LSAF | 1919 | Life Safety | Emergency Lighting | BLD | 3 | 20 | ea | 12655.0665 | 16831.2384 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade with renovation |  | GF
WIGHTMAN HALL | WI | LSAF | 1920 | Life Safety | Area of Refuge | Allowance | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 |  |  | GF
WIGHTMAN HALL | WI | LSAF | 1921 | Life Safety | Lighting | BLD | 3 | 680 | ea | 301190.5824 | 400583.4746 | 0 | 0 | Unknown | 20 | 20 | Could be upgraded for energy savings |  | GF
BEDDOW HALL | BE | ARCH | 1922 | Envelope | Windows | Exterior windows | 4 | 5330 | sf | 370983.2741 | 493407.7545 | 0 | 0 | 1962 | 30 | 1992 | Replace all exterior windows and windows in stair towers |  | SF
BEDDOW HALL | BE | ARCH | 1923 | Conveying Systems | Elevators & Lifts |  | 3 | 1 | ea | 227791.1968 | 302962.2917 | 0 | 0 | 1962 | 30 | 1992 | Otis had no maintenance suggestions in the May 1, 2013 maintenance plan. | Price is for replacemement of elevator | SF
BEDDOW HALL | BE | MECH | 1924 | Ventilation/Terminal Units | AHU/No Cool/Steam Heat | AHU-1/Basement Mech. Rm. | 3 | 6000 | cfm | 75930.3989 | 100987.4306 | 0 | 0 | 1962 | 30 | 1992 | Replace reaching end of useful life | Mechanical information was taken from mech drawings dated 7-10-61 | SF
BEDDOW HALL | BE | MECH | 1925 | Ventilation/Terminal Units | Terminal units | Steam Cabinet Heaters/Entrance | 3 | 7 | ea | 37205.8955 | 49483.841 | 0 | 0 | 1962 | 20 | 1982 | Replace reaching end of useful life |  | SF
BEDDOW HALL | BE | MECH | 1926 | Heating Water System | Insulation | Entire system | 3 | 65688 | sf | 99754.0978 | 132672.2852 | 0 | 0 | 1962 |  | 1962 | Good condition, reported to be some ACM |  | SF
BEDDOW HALL | BE | MECH | 1927 | Steam System | Piping | Entire system | 3 | 65688 | sf | 236916.7867 | 315098.286 | 0 | 0 | 1962 | 50 | 2012 | Replace condensate piping, failures observed |  | SF
BEDDOW HALL | BE | MECH | 1928 | Building Management | HVAC Control | Pneumatic | 3 | 65688 | sf | 332514.0169 | 442243.0955 | 0 | 0 | 1962 | 25 | 1987 | Replace with DDC |  | SF
BEDDOW HALL | BE | MECH | 1929 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rm. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | unknown | 10 | 10 | Replace entire duplex unit as precautionary measure |  | SF
BEDDOW HALL | BE | MECH | 1930 | Domestic cold water system | Piping | Entire building | 3 | 65688 | sf | 236916.7867 | 315098.286 | 0 | 0 | 1962 | 40 | 2002 | Good condition, no reported problems. Reported galvanized/copper mix |  | SF
BEDDOW HALL | BE | MECH | 1931 | Domestic hot water system | Piping | Entire building | 3 | 65688 | sf | 236916.7867 | 315098.286 | 0 | 0 | 1962 | 40 | 2002 | Good condition, no reported problems. Reported galvanized/copper mix |  | SF
BEDDOW HALL | BE | MECH | 1932 | Fire protection system | Piping | Control Valve | 3 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 1962 | 40 | 2002 | Replace control valve in tunnel | One Valve? | SF
BEDDOW HALL | BE | EH&S | 1933 | Environmental Health and Safety | asbestos abatement for mech | allowance | 3 | 65688 | sf | 332514.0169 | 442244.1679 | 0 | 0 | Unknown |  | 0 |  |  | SF
BEDDOW HALL | BE | ELEC | 1934 | Distribution | Main Dist. Panel |  | 1 | 1 | ea | 0 | 0 | 0 | 0 | 1962 | 50 | 2012 | 1200A, 120/240, (12) 125A/2P CB's | Price is for a 1200A MDP | SF | 654076 | 2014-08-01 | 3021847.86 | Part of South Quad Improvements included FCA project #'s 2373,2374,2390,2391,2392,2228,2229,1934,1935,1936,2257
BEDDOW HALL | BE | ELEC | 1935 | Distribution | Panelboards | Bsmnt Vault | 1 | 12 | total | 0 | 0 | 0 | 0 | 1962 | 50 | 2012 | Replace with 125A Panelboard |  | SF | 654076 | 2014-08-01 | 3021847.86 | Part of South Quad Improvements included FCA project #'s 2373,2374,2390,2391,2392,2228,2229,1934,1935,1936,2257
BEDDOW HALL | BE | LSAF | 1936 | Life Safety | Fire Alarm | Building | 1 | 65688 | sf | 0 | 0 | 0 | 0 | unknown |  | 0 | Complete building upgrade |  | SF | 654076 | 2014-08-01 | 3021847.86 | Part of South Quad Improvements included FCA project #'s 2373,2374,2390,2391,2392,2228,2229,1934,1935,1936,2257
| BE | LSAF | 1937 | Life Safety | Area of Refuge | allowance |  |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | SF |  |  |  | Building fully sprinkled not required
BARNES KITCHEN | BF | ARCH | 1938 | Envelope | Roof | Replace roof and flashings | 4 | 8500 | sf | 247406.5498 | 329050.7113 | 0 | 0 | Unknown | 30 | 30 | This should be done in 2 to 4 years |  | SF
BARNES KITCHEN | BF | MECH | 1939 | Ventilation/Terminal Units | Termianal units | Steam Convectors/Various | 3 | 11 | ea | 41761.7194 | 55543.0868 | 0 | 0 | 1960 | 25 | 1985 | Good condition, no reported problems | Quantity was taken from mechanical drawings dated 3-14-50 | SF
BARNES KITCHEN | BF | MECH | 1940 | Heating Water System | Pumps | Powers Hall/Barnes Kitchen Basement Mech. Rm. | 3 | 2 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1960 | 20 | 1980 | Replace reaching end of useful life. Consider consolidation of services for Powers Hall | Quantity was taken from mechanical drawings dated 3-14-50. Price is for 2 VFD base mounted pumps | SF
BARNES KITCHEN | BF | MECH | 1941 | Heating Water System | Piping | Powers Hall/Barnes Kitchen Basement Mech. Rm. | 3 | 10294 | sf | 108124.6736 | 143806.5987 | 0 | 0 | 1960 | 40 | 2000 | Replace reaching end of useful life. Consider consolidation of services for Powers Hall |  | SF
BARNES KITCHEN | BF | MECH | 1942 | Steam System | PRV Station | Entire system/Barnes Kitche Basement Mech. Rm. | 3 | 1 | ea | 107568.0651 | 143065.5266 | 0 | 0 | 1960 | 50 | 2010 | Good condition, no reported problems |  | SF
BARNES KITCHEN | BF | MECH | 1943 | Steam System | Piping | Entire system | 3 | 1 | ea | 31637.6662 | 42078.0961 | 0 | 0 | 1960 | 50 | 2010 | Good condition, no reported problems | Pricing is for replacing steam piping for PRV station only. | SF
BARNES KITCHEN | BF | MECH | 1944 | Storm/Sanitary sewer system | Piping | Entire building | 4 | 10294 | sf | 78163.2674 | 103956.0089 | 0 | 0 | 1960 | 40 | 2000 | Replace all, reaching end of useful life failures reported |  | SF
BARNES KITCHEN | BF | MECH | 1945 | Storm/Sanitary sewer system | Sump pumps | Barnes Kitchen Basement Mech. Rm. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown | 10 | 10 | Replace as a precautionary measure |  | SF
BARNES KITCHEN | BF | MECH | 1946 | Storm/Sanitary sewer system | Lift pump | Barnes Kitchen Basement Mech. Rm. | 3 | 1 | ea | 31637.6662 | 42078.0961 | 0 | 0 | Unknown | 10 | 10 | Replace as a precautionary measure |  | SF
BARNES KITCHEN | BF | MECH | 1947 | Domestic cold water system | Piping | Entire building | 3 | 10294 | sf | 78163.2674 | 103956.0089 | 0 | 0 | 1960 | 40 | 2000 | Replace entire system |  | SF
BARNES KITCHEN | BF | MECH | 1948 | Domestic hot water system | Piping | Entire building | 4 | 10294 | sf | 78163.2674 | 103956.0089 | 0 | 0 | 1960 | 40 | 2000 | Replace entire system, failure Immanent |  | SF
BARNES KITCHEN | BF | MECH | 1949 | Domestic hot water system | Heater/Steam | Entire building/Barnes Kitchen Basement Mech. Rm. | 4 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1960 | 24 | 1984 | Replace reaching end of useful life. Aerco steam heat exchanger similar to a model SW1B+07 |  | SF
BARNES KITCHEN | BF | EH&S | 1950 | Environmental Health and Safety | asbestos abatement | allowance for mech items | 4 | 10294 | sf | 104217.0035 | 138608.6147 | 0 | 0 | 1960 |  | 1960 |  |  | SF
BARNES KITCHEN | BF | ELEC | 1951 | Lighting/Controls | Exterior (Fixed to Bldg) | Loading/entry | 4 | 4 | ea | 2531.0133 | 3366.2477 | 0 | 0 | 1980 (est) | 20 | 20 | Replace 4 surface mt M-H w/LED |  | SF
BARNES KITCHEN | BF | ELEC | 1952 | Lighting/Controls | Controls | Manual | 3 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 |  | Same as below? | SF
BARNES KITCHEN | BF | LSAF | 1953 | Life Safety | Fire Alarm |  | 3 | 10294 | sf | 65135.6272 | 86630.3842 | 0 | 0 | Unknown | 40 | 40 |  |  | SF
BARNES KITCHEN | BF | LSAF | 1954 | Life Safety | Area of Refuge | allowance | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 |  |  | SF
BARNES KITCHEN | BF | LSAF | 1955 | Life Safety | Emergency Lighting |  | 4 | 10 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 2005 | 10 | 2015 |  |  | SF
BARNES KITCHEN | BF | LSAF | 1956 | Life Safety | Emergency Power |  | 5 | 1 | lot | 63275.3324 | 84156.1921 | 0 | 0 | Unknown |  | 0 |  | What needs to be priced. Allowance of 50,000 has been included for now. Capital Project? | SF
BARNES KITCHEN | BF | COMM | 1957 | IT | Distribution System | Basement | 4 | 1 | lot | 6327.5332 | 8415.6192 | 0 | 0 | Unknown |  | 0 | Install enclosed conditioned rack |  | SF
BARNES KITCHEN | BF | SUST | 1958 | Energy/Sustainability | Lighting Controls |  | 3 | 10294 | sf | 26054.4225 | 34652.3604 | 0 | 0 | Unknown |  | 0 | Upgrade to automatic controls | Unit price has been adjusted because of the small SF area | SF
BARNES HALL | BN | ARCH | 1959 | Envelope | Roof | Flat roof areas | 1 | 18200 | sf | 0 | 0 | 0 | 0 | Unknown | 30 | 30 | Shold be considered for replacement in 3 to 5 years |  | SF | 654295/654296 | 2014-08-01 | 242348.68
BARNES HALL | BN | ARCH | 1960 | Envelope |  | Attic space | 3 |  |  | 0 | 0 | 0 | 0 | 1951 |  | 1951 | Wood rafter attic space is not sprinkled | capital improvement | SF
BARNES HALL | BN | ARCH | 1961 | Envelope | Exterior Walls | Main entries and gable ends | 4 | 1200 | sf | 37965.1995 | 50493.7153 | 0 | 0 | 1951 | 100 | 2051 | Repair 1,200 SF of brick and mortar joints |  | SF
BARNES HALL | BN | ARCH | 1962 | Envelope |  | Gable end walls | 4 | 1500 | sf | 56947.7992 | 75740.5729 | 0 | 0 | 1951 | 100 | 2051 | Tuck point and seal gable end walls. Approx 1,500 SF |  | SF
BARNES HALL | BN | ARCH | 1963 | Interior Structure | Horizontal plumbing | refer to mech | 4 | 1 | allw | 31637.6662 | 42078.0961 | 0 | 0 | 1951 |  | 1951 | Horizontal plumbing in toilet rooms backs up constantly into the space | $25,000 allowance | SF
BARNES HALL | BN | MECH | 1964 | Ventilation/Terminal Units | Terminal units | Fin Tube Steam/Entire Origianl Building | 3 | 70 | lf | 24803.9303 | 32989.2273 | 0 | 0 | 1950 | 25 | 1975 | Good condition, no reported problems |  | SF
BARNES HALL | BN | MECH | 1965 | Ventilation/Terminal Units | Terminal units | Fin Tube HW/Entire Addition | 3 | 325 | lf | 115161.105 | 153164.2697 | 0 | 0 | 1955 | 20 | 1975 | Good condition, no reported problems |  | SF
BARNES HALL | BN | MECH | 1966 | Heating Water System | Pumps | Barnes System/Basement Mech. Rm. | 3 | 2 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1955 | 20 | 1975 | Consider replacement of system components located in mechanical room as they are reaching end of useful life | Price is for 2 base mounted pumps. | SF
BARNES HALL | BN | MECH | 1967 | Heating Water System | Pumps | Powers System/Basement Mech. Rm. | 3 | 2 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1955 | 20 | 1975 | Consider replacement of system components located in mechanical room as they are reaching end of useful life. Also consider consolidation as Powers is currently supplied from Barns Kitchen also. | Price is for 2 base mounted pumps. | SF
BARNES HALL | BN | MECH | 1968 | Heating Water System | Piping | Entire Barnes system | 3 | 52464 | sf | 551065.9426 | 732918.1756 | 0 | 0 | 1955 | 40 | 1995 | Consider replacement of system components located in mechanical room as they are reaching end of useful life |  | SF
BARNES HALL | BN | MECH | 1969 | Heating Water System | Piping | Entire Powers system | 3 | 39250 | sf | 412270.4285 | 548319.6699 | 0 | 0 | 1960 | 40 | 2000 | Consider replacement of system components located in mechanical room as they are reaching end of useful life. Also consider consolidation as Powers is currently supplied from Barnes Kitchen also. |  | SF
BARNES HALL | BN | MECH | 1970 | Storm/Sanitary sewer system | Piping | Entire building and addition | 4 | 52464 | sf | 182582.5804 | 242834.6389 | 0 | 0 | 1951 | 40 | 1991 | Replace all, reaching end of useful life failures reported |  | SF
BARNES HALL | BN | MECH | 1971 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rm. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown | 10 | 10 | Replace as precautionary measure |  | SF
BARNES HALL | BN | MECH | 1972 | Domestic hot water system | Heater/Steam | Entire building/Basement Mech. Rm. | 3 | 52464 | sf | 182582.5804 | 242834.6389 | 0 | 0 | 1951 | 24 | 1975 | Replace reaching end of useful life |  | SF
BARNES HALL | BN | MECH | 1973 | Domestic hot water system | Heater/Electric | R.M. Apartment/Laundry Room | 3 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1995 | 12 | 2007 | Replace reaching end of useful life or connect to building domestic hot water system |  | SF
BARNES HALL | BN | ELEC | 1974 | Distribution | 800A 120/240 Main Panel | Trumbull Basement | 5 | 1 | ea | 40496.2128 | 53859.963 | 0 | 0 | 1951 | 40 | 1991 |  |  | SF
BARNES HALL | BN | ELEC | 1975 | Distribution | 100A EM Panel | Trumbull Basement | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1951 | 40 | 1991 |  |  | SF
BARNES HALL | BN | ELEC | 1976 | Distribution | Demo abandoned elec | Basement | 5 | 1 | lot | 12655.0665 | 16831.2384 | 0 | 0 | 1951 | 40 | 1991 | Demo abandoned disconnects, feeders | Price is for 2 workers for 2 days plus some patch and repair work | SF
BARNES HALL | BN | ELEC | 1977 | Distribution | Panelboards | Throughout | 5 | 6 | ea | 56947.7992 | 75740.5729 | 0 | 0 | 1951-1980 | 40 | 40 | Replace (6) panelboards |  | SF
BARNES HALL | BN | ELEC | 1978 | Branch Circuit Condition | Assumed original | Throughout | 5 | 52464 | sf | 172623.6866 | 229588.6452 | 0 | 0 | 1951 | 40 | 1991 | Replace branch circuit wiring |  | SF
BARNES HALL | BN | ELEC | 1979 | Lighting/Controls | Basement Fluorescent | Basement | 4 | 75 | ea | 33219.5495 | 44182.0009 | 0 | 0 | 1980 (est) | 30 | 30 | Replace service area fluorescents |  | SF
BARNES HALL | BN | ELEC | 1980 |  | Public Space Fluorescent | Throughout | 3 | 300 | ea | 132878.1981 | 176728.0035 | 0 | 0 | Unknown | 20 | 20 |  | Price is for replacing lights in public spaces only (corridors, bathrooms, stairways) | SF
BARNES HALL | BN | ELEC | 1981 | Lighting Controls | Interior Controls | Manual | 3 | 52464 | sf | 66394.0556 | 88303.4076 | 0 | 0 | Unknown |  | 0 |  |  | SF
BARNES HALL | BN | ELEC | 1982 | Lighting Controls | Exterior Controls | Photocell | 3 | 52464 | sf | 31637.6662 | 42078.0961 | 0 | 0 | Unknown |  | 0 |  |  | SF
BARNES HALL | BN | LSAF | 1983 | Life Safety | Fire Alarm | Simplex 4100 | 3 | 52464 | sf | 331967.7041 | 441517.0464 | 0 | 0 | Unknown | 40 | 40 |  |  | SF
BARNES HALL | BN | LSAF | 1984 | Life Safety | Emergency Lighting | Battery Units | 5 | 50 | sf | 31637.6662 | 42078.0961 | 0 | 0 | 1990 | 10 | 2000 |  | Price is for about 50 emergency lights | SF
BARNES HALL | BN | LSAF | 1985 | Life Safety | Emergency Power | Tapped | 5 | 52464 | sf | 199181.0943 | 264910.2227 | 0 | 0 | 1951 | 30 | 1981 |  | capital improvement? | SF
CAREY RESIDENTIAL HALL | CA | ARCH | 1986 | Envelope | Exterior Walls | Brick cracking | 3 | 3100 | sf | 98076.7653 | 130442.0978 | 0 | 0 | 1969 | 100 | 2069 | Areas of brick cracked by movement 10% of brick | Price is for removing damaged brick and replace it with new brick | SF
CAREY RESIDENTIAL HALL | CA | ARCH | 1987 | Envelope | Exterior Walls | Mortar joints in brick | 3 | 24800 | sf | 980767.6527 | 1304420.9781 | 0 | 0 | 1969 | 100 | 2069 | Mortar joints should be tuckpointed (80%) and the systems sealed 100%) | Price is for removing old mortar and repointing it with new for 80% of brick area and sealing 100% of the area | SF
CAREY RESIDENTIAL HALL | CA | ARCH | 1988 | Envelope | Exterior Walls | Exposed concrete columns | 3 | 9 | ea | 3758.5547 | 4998.8778 | 0 | 0 | 1969 | 100 | 2069 | Repair concrete columns, area 36" high x 18" wide 2" deep concrete patch in 9 locations | price is for patching about 4.5 sf of concrete on 9 columns. | SF
CAREY RESIDENTIAL HALL | CA | ARCH | 1989 | Envelope | Windows |  | 4 | 4300 | sf | 299292.3224 | 398058.7888 | 0 | 0 | 1969 | 30 | 1999 | Replacement of all original windows is recommended | Price includes removing old windows, replacing them with new aluminum framed windows, new caulk and minor patching of existing finishes around window. | SF
CAREY RESIDENTIAL HALL | CA | ARCH | 1990 | Interior Structure | Floor Finishes | General finishes | 3 | 55000 | sf | 382815.7612 | 509144.9624 | 0 | 0 | Unknown | 15 | 15 | Flooring should be replaced on upper floors and living quarters | price is for removing existing flooring and replacing it with carpet. No abatement was included | SF
CAREY RESIDENTIAL HALL | CA | ARCH | 1991 | Conveying Systems | Elevators & Lifts |  | 4 | 2 | ea | 390376.6272 | 519200.9142 | 0 | 0 | 1969 | 30 | 1999 | Comprehensive repairs or replacement in 3 to 5 years | Otis recommends this work for 2017. | SF
CAREY RESIDENTIAL HALL | CA | ADAC | 1992 | Barrier Free Compliance | Doors & Hardware |  | 3 | 225 | ea | 142369.498 | 189351.4323 | 0 | 0 | 1969 |  | 1969 | Replacement is required to comply with current codes | Price is for replacing existing hardware with new ADA compliant hardware | SF
CAREY RESIDENTIAL HALL | CA | ADAC | 1993 | Barrier Free Compliance | Toilet Rooms |  | 3 | 8350 | sf | 1056698.0517 | 1405408.4087 | 0 | 0 | 1969 |  | 1969 | Design and construction is necessary to comply with current codes | Price is for renovation of bathroom areas to comply with ADA codes | SF
CAREY RESIDENTIAL HALL | CA | MECH | 1994 | Ventilation/Terminal Units | Terminal units/Unit Ventilator | UV, Elevator Lobby Area | 3 | 4 | ea | 141736.7447 | 188509.8704 | 0 | 0 | 1969 | 20 | 1989 | Replace nearing end of useful life, alternately replace the 4 units with a single air handler. | Price is for replacing existing Unit Ventilators with new and reconnect to existing piping and ductwork | SF
CAREY RESIDENTIAL HALL | CA | MECH | 1995 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 63900 | sf | 202164.6871 | 268879.0339 | 0 | 0 | 1969 | 40 | 2009 | Replace all drainage piping | Price is for replacing storm and sanitary piping only. No other piping was figured. Some demo and patching of finishes is included | SF
CAREY RESIDENTIAL HALL | CA | ELEC | 1996 | Service | Abandoned Primary Switch | Basement | 5 | 1 | ea | 3543.4186 | 4712.7468 | 0 | 0 | 1969 |  | 1969 |  | Price is for 2 workers for 2 days to remove switch | SF
CAREY RESIDENTIAL HALL | CA | ELEC | 1997 | Service | Abandoned Transformer | Basement | 5 | 1 | ea | 10124.0532 | 13464.9907 | 0 | 0 | 1969 |  | 1969 |  | Price is for 3 workers for 3 days to remove transformer | SF
CAREY RESIDENTIAL HALL | CA | ELEC | 1998 | Distribution | Main Panelboard 480V | Carey Dining Basement | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 |  |  | SF
CAREY RESIDENTIAL HALL | CA | ELEC | 1999 | Distribution | Main Panelboard 120/240V | Carey Dining Basement | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 |  |  | SF
CAREY RESIDENTIAL HALL | CA | ELEC | 2000 | Distribution | Floor Panels, Dorm | Ground through 8th | 4 | 9 | ea | 85421.6988 | 113610.8594 | 0 | 0 | 1969 | 40 | 2009 |  |  | SF
CAREY RESIDENTIAL HALL | CA | ELEC | 2001 | Distribution | Floor Panels, Kitchenette | Ground through 8th | 4 | 9 | ea | 85421.6988 | 113610.8594 | 0 | 0 | 1969 | 40 | 2009 |  |  | SF
CAREY RESIDENTIAL HALL | CA | ELEC | 2002 | Branch Circuit Condition | Functional | Throughout | 3 | 14 | ea | 343129.4727 | 456362.1987 | 0 | 0 | Unknown |  | 0 | Price re-wiring of building when panels are replaced. | Price is based on write-up description stating 2 panels for every residential floor and rewiring throughout the hall | SF
CAREY RESIDENTIAL HALL | CA | ELEC | 2003 |  | Controls |  | 3 | 63900 | sf | 80865.8749 | 107551.6136 | 0 | 0 | 1969 |  | 1969 | Manual controls for interior lights |  | SF
CAREY RESIDENTIAL HALL | CA | COMM | 2004 | Communications/Security |  |  | 3 |  | sf | 0 | 0 | 0 | 0 | Unknown |  | 0 |  |  | SF
CAREY RESIDENTIAL HALL | CA | LSAF | 2005 | Life Safety | Fire Alarm | Sleeping Rooms | 5 | 55000 | sf | 348014.3284 | 462859.0568 | 0 | 0 | Unknown | 40 | 40 | Consider adding horn/strobes in sleeping rooms |  | SF
CAREY RESIDENTIAL HALL | CA | LSAF | 2006 | Life Safety | . | Distributed Battery | 3 | 63900 | sf | 161731.7497 | 215103.2271 | 0 | 0 | Unknown |  | 0 | Consider re-use of 1/2 Corridor lighting as egress using generator |  | SF
CAREY RESIDENTIAL HALL | CA | LSAF | 2007 | Life Safety | Area of Refuge | Allowance | 5 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | allowance per S. Esch |  | SF
CELANI HALL | CE | ARCH | 2008 | Envelope | Windows |  | 4 | 2660 | sf | 185143.6227 | 246241.0182 | 0 | 0 | 2006 | 30 | 2036 | Replace all windows due to warping 50% of building | Price is for replacing 50% of the windows. It does not include windows at stairs | SF
CELANI HALL | CE | ARCH | 2009 | Envelope | Roof/Penetrations | Stand. Seam Roof | 3 | 80 | sf | 7593.0399 | 10098.7431 | 0 | 0 | 2006 | 30 | 2036 | Good condition except for small dent - see photo log | May have to see if canopy has to be completely replaced | SF
CELANI HALL | CE | ARCH | 2010 | Ceiling Finishes | Entry | painted gyp bd. | 3 | 20 | sf | 3163.7666 | 4207.8096 | 0 | 0 | 2006 | 10 | 2016 | small area needs repair (refer to photo) | Price is for patching of area and repainting | SF
CAREY DINING | CF | ARCH | 2011 | Envelope | Roof |  | 3 | 45100 | sf | 1312710.0467 | 1745904.3621 | 0 | 0 | Unknown | 30 | 30 | Roof should be considered for replacement in 3 to 5 years | Existing Roof has pavers covering the entire area. This price does not include paver only to remove old roof and replace it with a thermaco built up roof system. | SF
CAREY DINING | CF | ARCH | 2012 | Envelope | Exterior Walls | Cracking and shifted brick | 3 | 450 | sf | 42710.8494 | 56805.4297 | 0 | 0 | 1969 | 100 | 2069 | Brick should be repaired, 3 locations, 450 SF total | Price is for cutting out and replacing 450 SF of damaged brick. | SF
CAREY DINING | CF | ARCH | 2013 | Envelope |  | Tuckpoint and seal | 3 | 7800 | sf | 296128.5558 | 393850.9792 | 0 | 0 | 1969 |  | 1969 | System should be tuckpointed (75%) and sealed (100%) | Price is removing existing mortar to a depth of 1" and repainting it with new. Also includes sealing 100% of the brick | SF
CAREY DINING | CF | ARCH | 2014 | Envelope | Windows | Existing windows | 3 | 570 | sf | 39673.6334 | 52765.9325 | 0 | 0 | 1969 | 30 | 1999 | All existing windows should be replaced | Includes removing of old window, new aluminum framed window, caulk and minor finish patch around. | SF
CAREY DINING | CF | ARCH | 2015 | Envelope | Exterior Stairs | North west side of dining | 3 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 1969 | 40 | 2009 |  | Price is for removing existing stairs and replacing with new concrete stairs. | SF
CAREY DINING | CF | MECH | 2016 | Ventilation/Terminal Units | AHU/Steam Heat | AHU-8, Basement Mech. Rm. | 3 | 13500 | cfm | 170843.3976 | 227221.7188 | 0 | 0 | 1970 | 30 | 2000 | Replace nearing end of useful life, steam coil failures reported | Unit information was taken from drawing M-12 of the original tower drawings dated 8-23-67. Price is for removing old unit and replacing it with a new one of the same size and reconnecting to existing duct. | SF
CAREY DINING | CF | MECH | 2017 | Ventilation/Terminal Units | Terminal units/Cabinet Heater | Various | 3 | 3 | ea | 17084.3398 | 22722.1719 | 0 | 0 | 1970 | 20 | 1990 | Replace nearing end of useful life | Unit count was taken off of the M-11 drawings dated 8-23-67. Price is for removing old unit and replacing with a new cabinet heater reconnected to the existing pipes | SF
CAREY DINING | CF | MECH | 2018 | Heating Water System | Pumps | Old System, Basement Mech. Rm. | 3 | 4 | ea | 101240.5319 | 134649.9074 | 0 | 0 | 1970 | 20 | 1990 | Replace nearing end of useful life | remodel was done in 2003 that shows new pumps. Are these the pumps for this item? Price is for new VFD pumps. | SF
CAREY DINING | CF | MECH | 2019 | Building Management | HVAC Control | Hybrid and new DDC | 3 | 45100 | sf | 228297.3994 | 303635.5412 | 0 | 0 | 1970 | 25 | 1995 | Finish upgrade to new DDC system | Price is for replacing existing controls with new DDC controls | SF
CAREY DINING | CF | MECH | 2020 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 45100 | sf | 142685.8746 | 189772.2133 | 0 | 0 | 1970 | 40 | 2010 | Replace all drainage piping 90% original | Price is for replacing storm/sanitary piping. No other piping has been included. | SF
CAREY DINING | CF | MECH | 2021 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rm. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | 1970 | 10 | 1980 | Replace nearing end of useful life | verify quantity. Price is to replace one existing sump pump with new unit. | SF
CAREY DINING | CF | MECH | 2022 | Domestic hot water system | Heater/Steam | Basement Mech. Rm. | 3 | 5 | Units | 189825.9973 | 252468.5764 | 0 | 0 | 1970 | 24 | 1994 | Replace nearing end of useful life. No data available | what is being replaced (heat exchangers)? Price is to replace 5 existing tube in shell heat exchangers with new. | SF
CAREY DINING | CF | EH&S | 2023 | Environmental Health & Safety | Asbestos abatement | Allowance for mech items | 3 | 45100 | sf | 253607.5324 | 337298.0181 | 0 | 0 | Unknown |  | 0 |  |  | SF
CAREY DINING | CF | ELEC | 2024 | Distribution | Old Distribution | Basement | 5 | 5 | ea | 12655.0665 | 16831.2384 | 0 | 0 | 2000 | 40 | 2040 | Abandoned, demolish/remove | Is wiring already removed? Price is for removing abandoned panels only. No replacement panels for this item has been included | SF
CAREY DINING | CF | ELEC | 2025 | Distribution | Kitchen 480 | First Floor | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 | Obsolete, replace | Price is to remove and replace panel with new and reconnect to existing feeds | SF
CALKINS HALL | CL | ARCH | 2026 | Envelope | Roof | North and West roof need work | 3 | 9800 | sf | 285245.1986 | 379376.1142 | 0 | 0 | Unknown | 30 | 30 | 50% of roof should be replaced in 3 to 5 years |  | SF
CALKINS HALL | CL | ARCH | 2027 | Envelope | Exterior Walls | Step cracking in brick | 4 | 1500 | sf | 47456.4993 | 63117.1441 | 0 | 0 | 1958 | 100 | 2058 | 1,500 SF of wall need to be repaired from brick cracking |  | SF
CALKINS HALL | CL | ARCH | 2028 | Envelope |  | Tuck point and seal | 4 | 28130 | sf | 622977.2855 | 828559.7897 | 0 | 0 | 1958 | 100 | 2058 | Tuck point 50% of exterior and seal 100% of brick and mortar | Price is $25/SF for Tuckpointing and $5/sf for sealing | SF
CALKINS HALL | CL | ARCH | 2029 | Envelope | Windows | Replacement | 3 | 6650 | sf | 462859.0568 | 615602.5455 | 0 | 0 | 1958 | 30 | 1988 | All windows should be replaced |  | SF
CALKINS HALL | CL | ARCH | 2030 | Envelope | Exterior drainage | East side of resid wing | 4 | 5000 | sf | 189825.9973 | 252468.5764 | 0 | 0 | 1958 | 50 | 2008 | Regrade 5,000 SF and revise catch basin and underground drainage | Part of infrastructure? | SF
CALKINS HALL | CL | ARCH | 2031 | Interior Structure | Partitions/Walls | Settlement cracks | 3 | 2500 | sf | 31637.6662 | 42078.0961 | 0 | 0 | 1958 | 40 | 1998 | 2,500 SF of cracks need to be repaired | Price is for patching wall cracks and repainting of areas | SF
CALKINS HALL | CL | ARCH | 2032 | Interior Structure | Ceiling Finishes | Damaged tile | 4 | 5500 | sf | 41761.7194 | 55543.0868 | 0 | 0 | 1958 | 20 | 1978 | Replace 5,500 SF of damaged tile in resident rooms and corridors | Price is for replacing 2,500 SF of ceiling to match what is existing | SF
CALKINS HALL | CL | ARCH | 2033 | Conveying Systems | Elevators & Lifts | cylinder replacement | 4 |  |  | 40217.3723 | 53489.1052 | 0 | 0 | 1958 | 30 | 1988 | Otis recommends work to be done 2016. |  | SF
CALKINS HALL | CL | LSAF | 2034 | Life Safety (Arch) | Exit Stairs |  | 3 | 1 | allw | 25310.133 | 33662.4769 | 0 | 0 | 1958 | 40 | 1998 | Guard rail are too short - provide allowance for replacement at all egress stairs |  | SF
CALKINS HALL | CL | ADAC | 2035 | Barrier Free Compliance | Building Access |  | 3 | 1 | allw | 37965.1995 | 50493.7153 | 0 | 0 | 1958 | 30 | 1988 | Not accessible by current code - provide allowance | Price includes adding 4 automatic door operators to existing entrances and $6,000 for any additional modifications that would need to be made for accesibility | SF
CALKINS HALL | CL | MECH | 2036 | Ventilation/Terminal Units | AHU/No Cool/Steam Heat | AHU-1/Basement Mech. Rm. | 3 | 10000 | cfm | 126550.6649 | 168312.3843 | 0 | 0 | 1958 | 30 | 1988 | Replace reaching end of useful life | Could not find information on this unit. A budget for a 10,000 cfm unit has been included as a place holder until more information on the unit can be found. | SF
CALKINS HALL | CL | MECH | 2037 | Ventilation/Terminal Units | Terminal units | Fin Tube HW/Entire Building | 3 | 250 | lf | 88585.4654 | 117818.669 | 0 | 0 | 1958 | 25 | 1983 | Replace all reaching end of useful life failures reported |  | SF
CALKINS HALL | CL | MECH | 2038 | Ventilation/Terminal Units | Terminal units | HW Cabinet Heater/Main Entrance | 3 | 4 | ea | 22779.1197 | 30296.2292 | 0 | 0 | 1958 | 20 | 1978 | Replace all reaching end of useful life failures reported |  | SF
CALKINS HALL | CL | MECH | 2039 | Ventilation/Terminal Units | Terminal units | HW Convectors/Stairs, Corridors, Resident Rms. | 3 | 238 | ea | 903571.7472 | 1201750.4237 | 0 | 0 | 1958 | 25 | 1983 | Replace all reaching end of useful life failures reported |  | SF
CALKINS HALL | CL | MECH | 2040 | Heating Water System | Pumps | System/Basement Mech. Rm. | 3 | 2 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1958 | 20 | 1978 | Replace reaching end of useful life |  | SF
CALKINS HALL | CL | MECH | 2041 | Heating Water System | Insulation | Entire system | 3 | 68218 | sf | 103596.7337 | 137783.6451 | 0 | 0 | 1958 |  | 1958 | Replace reaching end of useful life. Reported ACM |  | SF
CALKINS HALL | CL | MECH | 2042 | Steam System | Piping | Entire system | 3 | 68218 | sf | 246041.3041 | 327235.3527 | 0 | 0 | 1958 | 50 | 2008 | Replace reaching end of useful life reported failures |  | SF
CALKINS HALL | CL | MECH | 2043 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 68218 | sf | 246041.3041 | 327235.3527 | 0 | 0 | 1958 | 40 | 1998 | Replace all, reaching end of useful life failures reported |  | SF
CALKINS HALL | CL | MECH | 2044 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rm. | 3 | 2 | ea | 45558.2394 | 60592.4583 | 0 | 0 | Unknown | 10 | 10 | Replace as precautionary measure |  | SF
CALKINS HALL | CL | MECH | 2045 | Domestic hot water system | Heater/Steam | Entire building/Basement Mech. Rm. | 3 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1958 | 24 | 1982 | Replace reaching end of useful life, add mixing valves for scald protection | Price is for replacing the hot water heater. Price may be adjusted depending on the size of the unit needed. | SF
CALKINS HALL | CL | EH&S | 2046 | Environmental Health and Safety | asbestos abatement | allowance for mech items | 3 | 68218 | sf | 345321.3731 | 459277.0295 | 0 | 0 | 1958 |  | 1958 |  |  | SF
CALKINS HALL | CL | ELEC | 2047 | Service | Transformers | Dry/Indoor Sub | 4 | 1 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1958 | 40 | 1998 | Shared w/Trout, replace w/OFPM |  | SF
CALKINS HALL | CL | ELEC | 2048 | Service | T - Switch | Oil/Indoor | 4 | 1 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 1958 | 40 | 1998 | Replace w/padmount switch |  | SF
CALKINS HALL | CL | ELEC | 2049 | Distribution | Main Switch gear | Indoor Sub | 4 | 1 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 1958 | 40 | 1998 | Replace w/MDP |  | SF
CALKINS HALL | CL | ELEC | 2050 | Distribution | 480 v. SW. & Transformer |  | 4 | 1 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 1958 | 40 | 1998 | Replace |  | SF
CALKINS HALL | CL | ELEC | 2051 | Distribution | 480V DP |  | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1958 | 40 | 1998 | Replace |  | SF
CALKINS HALL | CL | ELEC | 2052 | Distribution | Distribution Panels | Throughout | 4 | 6 | ea | 56947.7992 | 75740.5729 | 0 | 0 | Unknown |  | 0 |  | Based on 2 per floor | SF
CALKINS HALL | CL | ELEC | 2053 | Branch Circuit Condition | Assumed Original | Throughout | 4 | 68218 | sf | 310789.1286 | 413349.8627 | 0 | 0 | 1958 | 40 | 1998 |  | Price is based on pricing from Anspach with an additional $1/SF for architectural demo and repair. | SF
CALKINS HALL | CL | ELEC | 2054 | Lighting/Controls | Lobby Fixtures | First floor | 4 | 1500 | sf | 10440.4299 | 13885.7717 | 0 | 0 | 1980 (est) | 20 | 20 | Replace surface fixtures, can lights |  | SF
CALKINS HALL | CL | ELEC | 2055 | Lighting/Controls | Interior | Corridors, rooms | 3 | 360 | ea | 159453.8377 | 212073.6042 | 0 | 0 | 2000 | 25 | 2025 |  |  | SF
CALKINS HALL | CL | ELEC | 2056 | Lighting | Exterior (Fixed to Bldg) |  | 3 | 10 | ea | 6327.5332 | 8415.6192 | 0 | 0 | Unknown |  | 0 |  |  | SF
CALKINS HALL | CL | LSAF | 2057 | Life Safety | Fire Alarm | Edwards AC | 4 | 68218 | sf | 431651.6628 | 574096.7115 | 0 | 0 | 1958 | 30 | 1988 | Complete new system required | Capital Improvement? | SF
CALKINS HALL | CL | LSAF | 2058 | Life Safety | Area of Refuge | Allowance | 4 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | SF
CALKINS HALL | CL | LSAF | 2059 | Life Safety | Emergency Lighting |  | 4 | 30 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 2000 | 10 | 2010 |  | Price is for 30 wall mounted emergency lights | SF
CALKINS HALL | CL | LSAF | 2060 | Life Safety | Emergency Power | Tapped | 5 | 68218 | sf | 258991.298 | 344458.0402 | 0 | 0 | 1958 | 40 | 1998 | New system required | Capital Improvement? | SF
CALKINS HALL | CL | COMM | 2061 | IT | Distribution System | Retrofit | 3 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | by OIT? |  | SF
CALKINS HALL | CL | SUST | 2062 | Energy/Sustainability | Lighting Controls |  | 3 | 68218 | sf | 86330.0752 | 114818.9893 | 0 | 0 | Unknown |  | 0 | Upgrade to automatic controls |  | SF
COBB HALL | CO | ARCH | 2063 | Envelope | Exterior Walls | Brick | 3 | 20708 | sf | 575201.9428 | 765018.584 | 0 | 0 | 1970 | 100 | 2070 | Tuck point 80%, seal 100% | Price is for removing existing mortar and repointing with new for 80% of brick area. It also includes sealing 100% of the brick area | SF
COBB HALL | CO | ARCH | 2064 | Envelope | Exterior Walls | Expansion joints | 4 | 1900 | lf | 60111.5658 | 79948.3825 | 0 | 0 | 1970 | 30 | 2000 | Remove and re-install ALL expansion joint backer rod and caulk | Price is for replacing all existing expansion joints. Does not include adding any new joints. | SF
COBB HALL | CO | ARCH | 2065 | Envelope |  | Missing weeps | 4 | 75 | ea | 1898.26 | 2524.6858 | 0 | 0 | 1970 | - | 1970 | Install weeps and cavity vents | Price is for adding missing weeps | SF
COBB HALL | CO | ARCH | 2066 | Envelope |  | Concrete columns | 4 | 65 | sf | 26898.3438 | 35774.7973 | 0 | 0 | 1970 | 100 | 2070 | Repair concrete columns, area 36" high x 18" wide 2" deep concrete patch in 12 locations | Price is for patching about 4.5 SF of concrete on 12 columns | SF
COBB HALL | CO | ARCH | 2067 | Envelope | Windows - 4' * 4'6" |  | 5 | 247 | ea | 250064.1138 | 332585.2713 | 0 | 0 | 1970 | 30 | 2000 | Replace all original windows | Aluminum frame operable window unit. Includes demo existing, replace, repair sill, jamb and head finishes. | SF
COBB HALL | CO | ARCH | 2068 | Interior Structure | Interior Doors | Entry doors to resident rooms | 3 | 107 | ea | 47393.224 | 63032.9879 | 0 | 0 | 1970 | 40 | 2010 | Some frame movement in walls has required replacement of frames | Replacement of frames only. No new door or hardware. | SF
COBB HALL | CO | EH&S | 2069 | Environmental Health & Safety | asbestos abatement | allowance for floor finishes | 4 | 56500 | sf | 214503.377 | 285289.4913 | 0 | 0 | 1970 | 15 | 1985 | Carpet and VAT tile should be replaced and is past its useful life | includes removal of existing flooring and new carpet or VCT. No abetment costs included. Unit price of $5.50/sf was used | SF
COBB HALL | CO | ARCH | 2070 | Conveying Systems | Elevators & Lifts | Cylinder | 4 | 2 | ea | 390376.6272 | 519200.9142 | 0 | 0 | 1970 | 30 | 2000 | A major overhaul is needed. Otis Elevator proposed schedule indicates 2018. | Refer to Otis cylinder replacement scope outlined in proposal #TUQ4530. | SF
COBB HALL | CO | ADAC | 2071 | Barrier Free Compliance | Doors & Hardware | Hardware | 3 | 107 | ea | 67704.6057 | 90047.1256 | 0 | 0 | 1970 | 40 | 2010 | Hardware should be upgraded as part of a building wide campus plan | price is for replacing existing hardware and replacing it with ADA compliant hardware | SF
COBB HALL | CO | ADAC | 2072 | Barrier Free Compliance | Toilet Rooms | Resident Rooms | 3 | 18 | ea | 136674.7181 | 181777.375 | 0 | 0 | 1970 | 40 | 2010 | This work would require major re-work. | Double check quantity. There are about 94 total bathrooms but they might only need them on the first floor. | SF
COBB HALL | CO | EH&S | 2073 | Environmental Health & Safety | asbestos abatement | allowance for mechanical abatement | 3 | 67000 | sf | 339155.7818 | 451077.1899 | 0 | 0 | 1970 | 15 | 1985 |  |  | SF
COBB HALL | CO | MECH | 2074 | Ventilation/Terminal Units | AHU/DX Cool | AHU, 004A | 3 | 10 | Tons | 56947.7992 | 75740.5729 | 0 | 0 | 1997 | 15 | 2012 | Replace nearing end of useful life | Price includes removing and replacing existing unit and reconnecting to existing mains. | SF
COBB HALL | CO | MECH | 2075 | Ventilation/Terminal Units | Terminal units/Unit Ventilator | UV, Elevator Lobby Area | 3 | 4 | ea | 141736.7447 | 188509.8704 | 0 | 0 | 1970 | 20 | 1990 | Replace all units, nearing end of useful life | Could not find any information on these units from mech drawings dated 8-13-67. No information on units to add. Price is for replacing 4 unit ventilators with new units and reconnecting to existing piping | SF
COBB HALL | CO | MECH | 2076 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 67000 | sf | 211972.3637 | 281923.2437 | 0 | 0 | 1970 | 40 | 2010 | Replace all drainage piping | Price is for replacing drainage piping only. Some architectural demo and patching/replacing is included | SF
COBB HALL | CO | ELEC | 2077 | Distribution | DLP-1 | Bsmnt Vault - 600A | 4 | 1 | ea | 10908.6673 | 14508.5275 | 0 | 0 | 1970 | 50 | 2020 | (18) 2P BRANCHES |  | SF
COBB HALL | CO | ELEC | 2078 | Distribution | LPBA | Bsmnt Vault | 4 | 1 | ea | 1126.3009 | 1497.9802 | 0 | 0 | 1970 | 50 | 2020 | Replace with 125A Panelboard |  | SF
COBB HALL | CO | ELEC | 2079 | Distribution | LPBB | Bsmnt Vault | 4 | 1 | ea | 1126.3009 | 1497.9802 | 0 | 0 | 1970 | 50 | 2020 | Replace with 125A Panelboard |  | SF
COBB HALL | CO | ELEC | 2080 | Distribution | LPBC | Bsmnt Vault | 4 | 1 | ea | 1126.3009 | 1497.9802 | 0 | 0 | 1970 | 50 | 2020 | Replace with 125A Panelboard |  | SF
COBB HALL | CO | ELEC | 2081 | Distribution | LPX-1 | Bsmnt Vault | 4 | 1 | ea | 1126.3009 | 1497.9802 | 0 | 0 | 1970 | 50 | 2020 | Replace with 125A Panelboard |  | SF
COBB HALL | CO | ELEC | 2082 | Distribution | 30A - 2P CONTACTOR | Bsmnt Vault | 4 | 1 | ea | 601.1157 | 799.4838 | 0 | 0 | 1970 | 50 | 2020 | Replace |  | SF
COBB HALL | CO | ELEC | 2083 | Corridor Panelboards | (6) at 125A | Corridors | 4 | 6 | ea | 9757.0563 | 12976.8848 | 0 | 0 | 1970 | 50 | 2020 | Replace with 125A Panelboard |  | SF
COBB HALL | CO | ELEC | 2084 | Corridor Panelboards | (1) at 150A | Corridors | 4 | 1 | ea | 1626.176 | 2162.8141 | 0 | 0 | 1970 | 50 | 2020 | Replace with a 150A Panelboard |  | SF
COBB HALL | CO | ELEC | 2085 | Kitchen Power Panel | (1) 125A |  | 4 | 1 | ea | 2891.6827 | 3845.938 | 0 | 0 | Unknown |  | 0 | (26) 3P Branches |  | SF
COBB HALL | CO | ELEC | 2086 | Motor Control Center | (1) 125A |  | 4 | 1 | ea | 2891.6827 | 3845.938 | 0 | 0 | Unknown |  | 0 | (26) 3P Branches |  | SF
COBB HALL | CO | LSAF | 2087 | Life Safety | Emergency Lighting |  | 3 | 8500 | sf | 53784.0326 | 71532.7633 | 0 | 0 | Unknown |  | 0 | EBU's, not fully code compliant | price includes adding emergency lights throughout the building. Includes 100 emergency egress lights | SF
CAMPBELL HALL | CP | ARCH | 2088 | Envelope | Exterior Walls | Mortar condition | 3 | 36450 | sf | 1012464.3044 | 1346577.5249 | 0 | 0 | 2003 | 100 | 2103 | Mortar is loose granular and porous, seal 100% of building | Price is for tuck pointing 80% of brick and sealing 100% | SF
CAMPBELL HALL | CP | ARCH | 2089 | Envelope |  | Cast fabricated units | 3 | 350 | lf | 22146.3664 | 29454.6672 | 0 | 0 | 2003 |  | 2003 | Units are absorbing water and cracking, seal and replace damaged units, approx 350 lineal FT | Price is to cut out and replace 350 lnft of cast stone | SF
CAMPBELL HALL | CP | ARCH | 2090 | Interior Structure | Fixed Equip/Furnishing | Janitor closets | 3 | 5 | ea | 63275.3324 | 84156.1921 | 0 | 0 | 2003 |  | 2003 | Provide lighting and exhaust air in single room on each floor | Need more detail on what is needed to refine budget number | SF
CAMPBELL HALL | CP | MECH | 2091 | Ventilation/Terminal Units | Terminal units/Fan Coil | HVAC, Resident Rms. | 3 | 9 | ea | 113895.5984 | 151481.1458 | 0 | 0 | 2003 | 20 | 2023 | Replace zone damper system | Price is for adding 2 VAV boxes at each fan coil unit. Further clarification is needed to refine scope and budget | SF
CAMPBELL HALL | CP | MECH | 2092 | Building Management | Domestic Water Heater | Pneumatic | 4 | 1 | ea | 19615.3531 | 26088.4196 | 0 | 0 | 2005 | 25 | 2030 | Install building control grade air compressor | What should be priced? See line 23 Kesseler Hall. Price is for a 76.7 CFM Heavy Duty, pressure lubricated 120 gallon tank air compressor | SF
CAMPBELL HALL | CP | MECH | 2093 | Domestic hot water system | Heater/Steam | Basement Mech. Rm. | 4 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 2003 | 24 | 2027 | Replace failed heater | Price new domestic water heater? One of the 2 domestic water heaters has been a constant source of failures, price replacement of one domestic heat exchanger. | SF
EMMONS HALL | EM | ARCH | 2094 | Envelope | Windows |  | 3 | 7585 | sf | 527937.7362 | 702157.1891 | 0 | 0 | 1964 | 30 | 1994 | Age of windows should be considered for replacement |  | SF
EMMONS HALL | EM | ARCH | 2095 | Conveying Systems | Elevators & Llifts | cylinder replacement | 4 |  |  | 0 | 0 | 0 | 0 | 1964 | 30 | 1994 | Otis recommends scheduling this for 2016. | Refer to May 1, 2013 letter from Otis re: scope. | SF
EMMONS HALL | EM | ARCH | 2096 | Conveying Systems | Elevators & Llifts | modernization | 3 |  |  | 0 | 0 | 0 | 0 | 1964 | 30 | 1994 | Otis recommends scheduling this for 2022. | Refer to May 1, 2013 letter from Otis re: scope. | SF
EMMONS HALL | EM | ADAC | 2097 | Barrier Free Compliance | Doors & Hardware |  | 3 | 114 | ea | 72133.879 | 95938.059 | 0 | 0 | 1964 |  | 1964 | 50% of hardware could be replaced to lever style |  | SF
EMMONS HALL | EM | ADAC | 2098 | Barrier Free Compliance | Toilet Rooms |  | 3 | 120 | sf | 0 | 0 | 0 | 0 | 1964 |  | 1964 | Public rest rooms are not ADA accessible - assume gut and re-work |  | SF
EMMONS HALL | EM | MECH | 2099 | Ventilation/Terminal Units | Terminal units | HW Cabinet Heaters/Entrance | 3 | 5 | ea | 28473.8996 | 37870.2865 | 0 | 0 | 1964 | 20 | 1984 | Good condition, no reported problems | Price is for replacing 5 cabinet heaters at the dorm entrances and reconnect to existing piping. | SF
EMMONS HALL | EM | MECH | 2100 | Heating Water System | Piping | Entire system | 3 | 64000 | sf | 672237.1318 | 894075.3853 | 0 | 0 | 1964 | 40 | 2004 | Fair condition, reported restrictions from scale, chemical treatment program has been established. | Price is for replacing heating piping in the building. | SF
EMMONS HALL | EM | MECH | 2101 | Heating Water System | Insulation | Entire system | 3 | 64000 | sf | 97190.9106 | 129263.9111 | 0 | 0 | 1964 |  | 1964 | Good condition, reported to be some ACM | price is for insulation of new heat water piping | SF
EMMONS HALL | EM | MECH | 2102 | Steam System | Piping | Entire system | 3 | 64000 | sf | 222729.1702 | 296229.7963 | 0 | 0 | 1964 | 50 | 2014 | Good condition, no reported problems | Price is for replacing existing steam piping in the building and replacing it with new. | SF
EMMONS HALL | EM | MECH | 2103 | Building Management | HVAC Control | Pneumatic | 3 | 64000 | sf | 323969.7021 | 430879.7037 | 0 | 0 | 1964 | 25 | 1989 | Replace with DDC with future renovation | Price is for replacing pneumatic controls with new DDC controls | SF
EMMONS HALL | EM | MECH | 2104 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 64000 | sf | 222729.1702 | 296229.7963 | 0 | 0 | 1964 | 40 | 2004 | Good condition, reported that the base of some stacks have rotted out at grade level | Price is for replacing drainage piping in the building with new. | SF
EMMONS HALL | EM | MECH | 2105 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rm. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown | 10 | 10 | Replace as a precautionary measure | Price is for replacing 1 sump pump with a new one. | SF
EMMONS HALL | EM | MECH | 2106 | Domestic cold water system | Piping | Entire building | 3 | 64000 | sf | 222729.1702 | 296229.7963 | 0 | 0 | Unknown | 40 | 40 | Good condition, no reported problems | Need Pricing? Price is for replacing existing piping with new. | SF
EMMONS HALL | EM | MECH | 2107 | Domestic hot water system | Piping | Entire building | 3 | 64000 | sf | 222729.1702 | 296229.7963 | 0 | 0 | Unknown | 40 | 40 | Good condition, no reported problems | Need Pricing? Price is for replacing existing piping with new. | SF
EMMONS HALL | EM | EH&S | 2108 | Environmental Health and Safety | Asbestos abatement | Allowance | 3 | 64000 | sf | 349279.835 | 464542.1806 | 0 | 0 | 1964 |  | 1964 |  |  | SF
EMMONS HALL | EM | ELEC | 2109 | Branch Circuit Condition | ITE breaker Panels | Corridors | 4 | 9 | 1 | 85421.6988 | 113610.8594 | 0 | 0 | 1964 | 40 | 2004 | Needs upgrade | Price is for replacing existing panel with a new one and reconnecting to existing feeds | SF
EMMONS HALL | EM | ELEC | 2110 | Branch Circuit Condition | Emergency panel | Basement | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1964 | 40 | 2004 | Fed ahead of mains | Price is for replacing existing panel with a new one and reconnecting to existing feeds | SF
EMMONS HALL | EM | ELEC | 2111 | Branch Circuit Condition | Exhaust fan panel | Basement | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1964 | 40 | 2004 | Needs upgrade | Price is for replacing existing panel with a new one and reconnecting to existing feeds | SF
EMMONS HALL | EM | ELEC | 2112 | Lighting | 4 foot fluorescent wraparound fixtures | Resident rooms | 3 | 460 | ea | 203746.5704 | 270982.9387 | 0 | 0 | Unknown | 20 | 20 | needs upgrade if renovated | Price is for replacing resident room lights with new ones. | SF
EMMONS HALL | EM | ELEC | 2113 | Lighting | 4 foot surface mount fluorescent fixtures | Laundry rooms | 3 | 68 | ea | 30119.0582 | 40058.3475 | 0 | 0 | Unknown | 20 | 20 | needs upgrade if renovated | Price is for replacing existing laundry room lights for new fixtures | SF
EMMONS HALL | EM | ELEC | 2114 | Lighting | 4 foot fluorescent vandal resistant fixtures | Corridors | 3 | 140 | ea | 62009.8258 | 82473.0683 | 0 | 0 | Unknown | 20 | 20 | needs upgrade if renovated | Price is for replacing existing corridor lights for new fixtures | SF
EMMONS HALL | EM | LSAF | 2115 | Life Safety | Simplex model 4100U Fire Alarm System | Woldt Dining/Sleep Rms | 3 | 64000 | sf | 404962.1276 | 538599.6297 | 0 | 0 | Unknown | 25 | 25 | No horn/strobes in sleep rooms | Price is for adding audio/visual units to sleep rooms | SF
EMMONS HALL | EM | LSAF | 2116 | Life Safety | Wall mounted battery emergency lights | Corridors | 3 | 64 | ea | 40496.2128 | 53859.963 | 0 | 0 | Unknown | 25 | 25 | needs upgrade if renovated | Price is for replacing 64 wall mounted wall packs for egress lighting | SF
FABIANO HALL | FB | ARCH | 2117 | Envelope | Windows |  | 4 | 2660 | sf | 185143.6227 | 246241.0182 | 0 | 0 | 2006 | 30 | 2036 | Windows are warped and do not seal or work smoothly. 50% of Windows | Price is for replacing 50% of the windows. It does not include windows at stairs | SF
FABIANO HALL | FB | ARCH | 2118 | Envelope | Roof/Penetrations | Stand. Seam Roof | 3 | 80 | sf | 7593.0399 | 10098.7431 | 0 | 0 | 2006 | 30 | 2036 | Metal Roof needs repair - denting | May have to see if canopy has to be completely replaced | SF
FABIANO HALL | FB | ARCH | 2119 | Interior Structure | Stairs |  | 3 | 1 | ea | 4429.2733 | 5890.9334 | 0 | 0 | 2006 | 30 | 2036 | minor maintenance needed to secure stair railings. | Price is for reworking of stair railing | SF
HERRIG HALL | HE | ARCH | 2120 | Envelope | Windows | Alum. single pane | 3 | 7830 | sf | 544990.4383 | 724837.2829 | 0 | 0 | 1966 | 30 | 1996 | Windows are in good condition for age but should be replaced for energy savings and to update the building since they are almost 50 years old. | Price is for removing existing windows and replacing them with new aluminum framed windows. Price includes Caulking around new windows and minor patching of finishes around new units | SF
HERRIG HALL | HE | ARCH | 2121 | Envelope | Exterior Doors | Building Entrance | 3 | 20 | ea | 126550.6649 | 168312.3843 | 0 | 0 | 1966 | 30 | 1996 | Replace doors to match new campus standard exterior doors. | Price is for removing existing doors and replacing them with new aluminum framed entry doors | SF
HERRIG HALL | HE | ARCH | 2122 | Interior Structure | Partitions | CMU walls painted | 3 | 26500 | sf | 67071.8524 | 89205.5637 | 0 | 0 | 1966 | 40 | 2006 | Interior corridor walls to be repainted. | Price is for repainting interior corridor walls. $1.25/SF was added for wall patch and repair where needed | SF
HERRIG HALL | HE | ARCH | 2123 | Interior Structure | Interior Doors | Wood | 3 | 120 | ea | 75930.3989 | 100987.4306 | 0 | 0 | 1966 | 40 | 2006 | Hardware has been replaced on room entry doors. | Price is for replacing existing dorm entry doors with ADA compliant door hardware | SF
HERRIG HALL | HE | ARCH | 2124 | Floor Finishes | Corridor | Carpet | 3 | 8110 | sf | 56447.9241 | 75075.739 | 0 | 0 | 1990 | 15 | 2005 | Carpet in all corridors will need replacement within 3 years. | Price is for removing existing flooring and replacing it with carpet. No abatement is included | SF
HERRIG HALL | HE | ARCH | 2125 | Floor Finishes | Rooms | VCT | 3 | 27000 | sf | 170843.3976 | 227221.7188 | 0 | 0 | 1990 | 15 | 2005 | Student rooms need new flooring. | Price is for removing existing flooring and replacing it with Ceramic. No abatement is included | SF
HERRIG HALL | HE | ARCH | 2126 | Floor Finishes | Toilet Rooms - Rooms | Ceramic Tile | 3 | 3000 | sf | 56947.7992 | 75740.5729 | 0 | 0 | 1990 | 20 | 2010 | Floor to be replaced in next 10 years. | Price is for removing existing flooring and replacing it with VCT. No abatement is included | SF
HERRIG HALL | HE | ARCH | 2127 | Floor Finishes | Toilet Rooms | Public | 3 | 3000 | sf | 379651.9946 | 504937.1528 | 0 | 0 | 1966 | 20 | 1986 | Not ADA Accessible. Renovate toilet rooms to make them accessible. | Price is for renovating toilet rooms to comply with ADA codes | SF
HERRIG HALL | HE | ARCH | 2128 | Wall Finishes | Painted | Corridor | 3 | 26500 | sf | 67071.8524 | 89205.5637 | 0 | 0 | Unknown | 10 | 10 | Corridor walls have been painted but need repainting. | Price is for repainting walls. Some wall patch and repair is included | SF
HERRIG HALL | HE | ARCH | 2129 | Ceiling Finishes | 12" x 12" Spline Ceiling | Corridor | 3 | 8110 | sf | 75191.4181 | 100004.5861 | 0 | 0 | 1966 | 30 | 1996 | Replace ceilings in all corridors with 2' x 2' lay-in ceiling and lighting. | Price is for removing existing ceiling and replacing it with new ACT ceiling system. Unit price was increased because of the added demo for the splined ceiling | SF
HERRIG HALL | HE | ARCH | 2130 | Conveying Systems | Elevators | modernization | 3 | 1 | ea | 64347.7957 | 85582.5683 | 0 | 0 | 1990 | 30 | 2020 | Elevators have been updated from original. Otis recommends mondernization in 2022. |  | SF
HERRIG HALL | HE | ARCH | 2131 | Conveying Systems | Elevators | cylinder replacement | 4 | 1 | ea | 40217.3723 | 53489.1052 | 0 | 0 | Unknown |  | 0 | Otis recommends this work in 2016. |  | SF
HERRIG HALL | HE | EH&S | 2132 | Environmental Health & Safety | Asbestos abatement | allowance for ceiling | 3 | 8110 | sf | 115679.1048 | 153853.2094 | 0 | 0 | 1966 |  | 1966 |  |  | SF
HERRIG HALL | HE | MECH | 2133 | Ventilation/Terminal Units | AHU/No Cool/Steam Heat | AHU-6/Basement Mech. Rm. | 3 | 9000 | cfm | 113895.5984 | 151481.1458 | 0 | 0 | 1966 | 30 | 1996 | Good condition, no reported problems | This is unit #1 from drawing M-10 dated 4-9-65. Price is for replacing existing unit with a new one of the same capacity and reconnecting to existing mains | SF
HERRIG HALL | HE | MECH | 2134 | Ventilation/Terminal Units | AHU/No Cool/Steam Heat | AHU-7/Basement Mech. Rm. | 3 | 7350 | cfm | 93014.7387 | 123709.6024 | 0 | 0 | 1966 | 30 | 1996 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2135 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | RTU-1/Roof over Fitness Center | 3 | 7.5 | Tons | 256265.0964 | 340832.5782 | 0 | 0 | 2005 | 15 | 2020 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2136 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | RTU-2/Roof over Fitness Center | 3 | 7.5 | Tons | 256265.0964 | 340832.5782 | 0 | 0 | 2005 | 15 | 2020 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2137 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | RTU-3/Roof over Fitness Center | 3 | 7.5 | Tons | 256265.0964 | 340832.5782 | 0 | 0 | 2005 | 15 | 2020 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2138 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | RTU-4/Roof over Fitness Center | 3 | 1.5 | Tons | 51253.0193 | 68166.5156 | 0 | 0 | 2005 | 15 | 2020 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2139 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | RTU-5/Roof over Fitness Center | 3 | 1.5 | Tons | 51253.0193 | 68166.5156 | 0 | 0 | 2005 | 15 | 2020 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2140 | Ventilation/Terminal Units | AHU/DX Cool/No Heat | AHU Split-1/Ceiling classroom 1 | 3 | 1.5 | Tons | 8542.1699 | 11361.0859 | 0 | 0 | 2002 | 15 | 2017 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2141 | Ventilation/Terminal Units | AHU/DX Cool/No Heat | AHU Split-2/Ceiling classroom 1 | 3 | 1.5 | Tons | 8542.1699 | 11361.0859 | 0 | 0 | 2002 | 15 | 2017 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2142 | Ventilation/Terminal Units | AHU/DX Cool/No Heat | AHU Split-3/Ceiling classroom 1 | 3 | 1.5 | Tons | 8542.1699 | 11361.0859 | 0 | 0 | 2002 | 15 | 2017 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2143 | Ventilation/Terminal Units | Terminal units | HW Cabinet Heaters/Entrance | 3 | 5 | ea | 28473.8996 | 37870.2865 | 0 | 0 | 1966 | 20 | 1986 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2144 | Heating Water System | Piping | Entire system | 3 | 60000 | sf | 630222.311 | 838195.6737 | 0 | 0 | 1966 | 40 | 2006 | Fair condition, reported restrictions from scale, chemical treatment program has been established. |  | SF
HERRIG HALL | HE | MECH | 2145 | Heating Water System | Insulation | Entire system | 3 | 60000 | sf | 91116.4787 | 121184.9167 | 0 | 0 | 1966 |  | 1966 | Good condition, reported to be some ACM |  | SF
HERRIG HALL | HE | MECH | 2146 | Steam System | Piping | Entire system | 3 | 60000 | sf | 216401.6369 | 287814.1771 | 0 | 0 | 1966 | 50 | 2016 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2147 | Building Management | HVAC Control | Pneumatic | 3 | 60000 | sf | 303721.5957 | 403949.7223 | 0 | 0 | 1966 | 25 | 1991 | Replace with DDC with future renovation |  | SF
HERRIG HALL | HE | MECH | 2148 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 60000 | sf | 216401.6369 | 287814.1771 | 0 | 0 | 1966 | 40 | 2006 | Good condition, reported that the base of some stacks have rotted out at grade level |  | SF
HERRIG HALL | HE | MECH | 2149 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rm. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown | 10 | 10 | Replace as a precautionary measure |  | SF
HERRIG HALL | HE | MECH | 2150 | Domestic cold water system | Piping | Entire building | 3 | 60000 | sf | 216401.6369 | 287814.1771 | 0 | 0 | Unknown | 40 | 40 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | MECH | 2151 | Domestic hot water system | Piping | Entire building | 3 | 60000 | sf | 216401.6369 | 287814.1771 | 0 | 0 | Unknown | 40 | 40 | Good condition, no reported problems |  | SF
HERRIG HALL | HE | EH&S | 2152 | Environmental Health & Safety | Asbestos abatement | allwance for mech | 3 | 60000 | sf | 303721.5957 | 403949.7223 | 0 | 0 | 1966 |  | 1966 |  |  | SF
HERRIG HALL | HE | ELEC | 2153 | Distribution | 480 Volt distribution | Basement | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Rusted out |  | SF
HERRIG HALL | HE | ELEC | 2154 | Branch Circuit Condition | Unlabeled ITE | Basement | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Rusted out |  | SF
HERRIG HALL | HE | ELEC | 2155 | Branch Circuit Condition | Panel LP-1E ITE | Terrace | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Needs Upgrade |  | SF
HERRIG HALL | HE | ELEC | 2156 | Branch Circuit Condition | Panel 1-C ITE | Terrace | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Needs Upgrade |  | SF
HERRIG HALL | HE | ELEC | 2157 | Branch Circuit Condition | Panel 1-B ITE | Terrace | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Needs Upgrade |  | SF
HERRIG HALL | HE | ELEC | 2158 | Branch Circuit Condition | Panel 1-A ITE | Terrace | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Needs Upgrade |  | SF
HERRIG HALL | HE | ELEC | 2159 | Branch Circuit Condition | Panel 2 PLA ITE | 2nd Floor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Needs Upgrade |  | SF
HERRIG HALL | HE | ELEC | 2160 | Branch Circuit Condition | Panel 2 PLB ITE | 2nd Floor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Needs Upgrade |  | SF
HERRIG HALL | HE | ELEC | 2161 | Branch Circuit Condition | Panel 2 PLC ITE | 2nd Floor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Needs Upgrade |  | SF
HERRIG HALL | HE | ELEC | 2162 | Branch Circuit Condition | Panel 3LPA ITE | 3rd Floor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Needs Upgrade |  | SF
HERRIG HALL | HE | ELEC | 2163 | Branch Circuit Condition | Panel 3 LPB ITE | 3rd Floor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Needs Upgrade |  | SF
HERRIG HALL | HE | ELEC | 2164 | Branch Circuit Condition | Panel 3 LPC ITE | 3rd Floor | 4 | 1 | 1 | 9491.2999 | 12623.4288 | 0 | 0 | 1966 | 40 | 2006 | Needs Upgrade |  | SF
HERRIG HALL | HE | ELEC | 2165 | Lighting | Surface Incandescent fixture | Entrance | 4 | 6 | ea | 3796.5199 | 5049.3715 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade | Price is for replacing 6 exterior lights with new fixtures | SF
HERRIG HALL | HE | ELEC | 2166 | Lighting | single lamp tamper resistant surface fixtures | Corridors | 3 | 120 | ea | 53151.2792 | 70691.2014 | 0 | 0 | Unknown |  | 0 | Needs upgrade | Price is for replacing corridor lights with new fixtures | SF
HERRIG HALL | HE | ELEC | 2167 | Lighting | Surface mounted 2 lamp fluorescent fixtures | Dorms | 3 | 616 | ea | 272843.2335 | 362881.5005 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade | Price is for replacing existing dorm light with new fixtures | SF
HERRIG HALL | HE | ELEC | 2168 | Lighting | Surface mounted 2 lamp fluorescent fixtures | Kitchenettes | 3 | 88 | ea | 38977.6048 | 51840.2144 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade | price is for replacing Existing kitchenette lights with new fixtures | SF
HERRIG HALL | HE | SUST | 2169 | Lighting/Controls | Occupancy sensors | Building | 3 | 60000 | sf | 75930.3989 | 100987.4306 | 0 | 0 | Unknown |  | 0 | No controlled lighting | price is for updating the light controls in the building. | SF
KEWADIN VILLAGE | KE | ARCH | 2170 | Envelope | Crawl Space | All units | 3 | 3580 | lf | 54366.1656 | 72307.0003 | 0 | 0 | 1972 |  | 1972 | Moisture/water in crawl space has been an ongoing problem at this location | Price is for installing 3580 lnft of perforated drainage pipe around buildings and draining it to the west. Pricing can be adjusted but additional investigation is required to clarify exactly what is needed to address the issue. | SF
KEWADIN VILLAGE | KE | MECH | 2171 | Storm/Sanitary sewer system | Piping | Entire building | 4 | 52000 | sf | 180967.4508 | 240686.7095 | 0 | 0 | 1972 | 40 | 2012 | Replace entire sanitary drainage system all buildings, failures and restrictions reported |  | SF
KEWADIN VILLAGE | KE | MECH | 2172 | Domestic hot water system | Heater/Nat. Gas Boiler | Entire building/Mech. Rm. | 3 | 4 | ea | 25310.133 | 33662.4769 | 0 | 0 | Unknown | 24 | 24 | Good condition, no reported problems except storage tank in Bldg. 5. Replace tank with four 120 gallon units. |  | SF
KEWADIN VILLAGE | KE | ELEC | 2173 | Distribution | Main Switch gear 120/208, 3 phase |  | 4 | 4 | ea | 60744.3191 | 80789.9445 | 0 | 0 | 1972 | 50 | 2022 | (2) at 400A, (1) at 800A |  | SF
KEWADIN VILLAGE | KE | ELEC | 2174 | Distribution | Dist Panels | 200A | 4 | 10 | ea | 94912.9987 | 126234.2882 | 0 | 0 | 1972 | 50 | 2022 | 1 per building |  | SF
KEWADIN VILLAGE | KE | ELEC | 2175 | Feeders | Panelboards | 70A NOW | 4 | 100 | ea | 949129.9865 | 1262342.8821 | 0 | 0 | 1972 | 50 | 2022 | 1 per unit |  | SF
KEWADIN VILLAGE | KE | ELEC | 2176 | Branch Circuit Condition | Not enough circuits |  | 3 | 100 | ea | 316376.6622 | 420780.9607 | 0 | 0 | 1972 | 40 | 2012 | Would require major remodel | Assume adding (2) 20A circuits to the kitchen area and (1) 20 circuit to the bathroom, for a total of (3) per unit | SF
KEWADIN VILLAGE | KE | ELEC | 2177 | Lighting | Mech. Rooms |  | 4 |  |  | 12655.0665 | 16831.2384 | 0 | 0 | 1972 |  | 1972 | 2 lamp industrials (approx.) |  | SF
KEWADIN VILLAGE | KE | ELEC | 2178 |  | Exterior (Fixed to Bldg) |  | 3 |  |  | 31637.6662 | 42078.0961 | 0 | 0 | 1972 |  | 1972 | 1 luminaries / 2 units |  | SF
KEWADIN VILLAGE | KE | LSAF | 2179 | Life Safety | Fire Alarm |  | 3 | 110 | ea | 17400.7164 | 23142.9528 | 0 | 0 | 1972 |  | 1972 | Single Station Smoke Detectors - Does not have proper coverage. Assuming adding 1 per bedroom and relocating 1 per stairwell |  | SF
| KE | LSAF | 2180 | Life Safety | Area of Refuge |  | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | 1972 |  | 1972 | required here? |  | SF
KESSLER HALL | KS | ARCH | 2181 | Envelope | Exterior Walls | Mortar condition | 3 | 36450 | sf | 1012464.3044 | 1346577.5249 | 0 | 0 | 2003 | 100 | 2103 | Mortar is loose, granular and porous | Price is for tuckpointing 80% of brick and sealing 100%. Scope was assumed to be similar to Campbell | SF
KESSLER HALL | KS | ARCH | 2182 | Envelope |  | Cast fabricated units | 3 | 350 | lf | 22146.3664 | 29454.6672 | 0 | 0 | 2003 | 100 | 2103 | Units are absorbing water and cracking, seal and replace damaged units | how many are damaged? Price is for cutting out and replacing 350 lnft of cast units. | SF
KESSLER HALL | KS | ARCH | 2183 | Interior Structure |  | Janitor closets | 3 | 5 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 2003 | 40 | 2043 | Provide lighting and exhaust air. Capital Project? |  | SF
KESSLER HALL | KS | MECH | 2184 | Ventilation/Terminal Units | Terminal units/Fan Coil | HVAC, Resident Rms. | 3 | 9 | ea | 113895.5984 | 151481.1458 | 0 | 0 | 2003 | 20 | 2023 | Replace zone damper system | Price is for adding 2 VAV boxes at each fan coil unit. Further clarification is needed to refine scope and budget | SF
KESSLER HALL | KS | MECH | 2185 | Building Management | Domestic Water Heater | Pneumatic | 4 | 1 | ea | 19615.3531 | 26088.4196 | 0 | 0 | 2005 | 25 | 2030 | Install building control grade air compressor | What should be priced? Price a new control grade air compressor with dryer sized to operate the control on the 2 domestic water heaters (6 water heaters if the control air is piped to the other new tower resident halls). Price is for a heavy duty pressure lubricated 76.7 CFM, 120 gallon tank air compressor | SF
KESSLER HALL | KS | ARCH | 2186 | Interior Structure | Janitor closets | provide lighting and exhaust air | 3 | 5 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 2003 | 40 | 2043 | Provide lighting and exhaust air. Capital Project? |  | SF
KULHAVI HALL | KU | MECH | 2187 | Ventilation/Terminal Units | Terminal units/Fan Coil | HVAC, Resident Rms. | 3 | 9 | ea | 113895.5984 | 151481.1458 | 0 | 0 | 2003 | 20 | 2023 | Replace zone damper system | Price is for adding 2 VAV boxes at each fan coil unit. Further clarification is needed to refine scope and budget | SF
KULHAVI HALL | KU | MECH | 2188 | Building Management | Domestic Water Heater | Pneumatic | 5 | 1 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 2005 | 25 | 2030 | Install building control grade air compressor | Price is for a heavy duty pressure lubricated 76.7 CFM, 120 gallon tank air compressor | SF
KULHAVI HALL | KU | MECH | 2189 | Domestic cold water system | Booster pump | Entire building/Basement Mech. Rm. | 3 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 2003 | 20 | 2023 | Replace corroded nipples & fittings | Price is for replacing a base mounted VFD pump for the demestic cold water system | SF
KULHAVI HALL | KU | LSAF | 2190 | Life Safety | Emergency Lighting |  | 3 | 30 | ea | 18982.5997 | 25246.8576 | 0 | 0 | 2003 |  | 2003 | EBU's, not fully code compliant |  | SF
KULHAVI HALL | KU | LSAF | 2191 | Life Safety | Add Life Safety Generator | None | 3 | 1 | ea | 63275.3324 | 84156.1921 | 0 | 0 | n/a |  | 0 | Assume 30 kW, 200A ATS, 3 Panelboards | Price is for adding new generator and panels | SF
LARZELERE HALL | LA | ARCH | 2192 | Envelope | Roof | Ponding and trees | 4 | 24600 | sf | 716023.6618 | 952311.4702 | 0 | 0 | 1957 | 30 | 1987 | Ponding water and debris from trees should be rectified (remove two trees) | Price is for removal of existing roof and replacement with new roof system. | SF
LARZELERE HALL | LA | ARCH | 2193 | Envelope | Exterior Walls | Cracking/tuckpointing | 3 | 850 | lf | 26892.0163 | 35766.3817 | 0 | 0 | 1957 | 100 | 2057 | Repair 850 linear feet of brick cracks | Price is for cutting out damaged bricks and replacing with new. | SF
LARZELERE HALL | LA | ARCH | 2194 | Envelope | Windows |  | 3 | 8080 | sf | 562391.1547 | 747980.2357 | 0 | 0 | 1957 | 30 | 1987 | Replace all windows | Price includes removing old windows, replacing with new aluminum framed windows, new caulk and minor patching of finishes around windows | SF
LARZELERE HALL | LA | ARCH | 2195 | Interior Structure | Partitions/Walls | Repair cracks | 4 | 1200 | lf | 7593.0399 | 10098.7431 | 0 | 0 | 1957 | 40 | 1997 | Repair 1,200 feet of CMU cracks | Price is for repairing 1,200 lnft of cracks in existing partitions | SF
LARZELERE HALL | LA | ARCH | 2196 | Conveying Systems | Elevators & Llifts | cylinder replacement | 1 | 1 | ea | 0 | 0 | 0 | 0 | 1957 | 30 | 1987 | Otis recommends this work for 2014 per letter dated May 1, 2013. |  | SF | 654347 | 2015-08-21 | 43000
LARZELERE HALL | LA | MECH | 2197 | Ventilation/Terminal Units | AHU/No Cool/Steam Heat | AHU-1/S.E. Basement Mech. Rm. | 3 | 40000 | cfm | 506202.6595 | 673249.5371 | 0 | 0 | 1957 | 30 | 1987 | Replace reaching end of useful life | Could not find any information on AHU. Mechanical information was taken from Mech drawings dated 10-5-56. Unit appears to be original so 1956 information should be correct. Need to know approx size of replacement unit. I can put a budget in for a place holder but any additional information will help. American Standard Size 2V9. | SF
LARZELERE HALL | LA | MECH | 2198 | Ventilation/Terminal Units | Terminal units | Fin Tube HW/Entire Building | 3 | 312 | lf | 110554.6608 | 147037.6989 | 0 | 0 | 1957 | 25 | 1982 | Replace all reaching end of useful life failures reported |  | SF
LARZELERE HALL | LA | MECH | 2199 | Ventilation/Terminal Units | Terminal units | HW Cabinet Heater/Main Entrance | 3 | 2 | ea | 11389.5598 | 15148.1146 | 0 | 0 | 1957 | 20 | 1977 | Replace all reaching end of useful life failures reported |  | SF
LARZELERE HALL | LA | MECH | 2200 | Ventilation/Terminal Units | Terminal units | HW Convectors/Stairs, Corridors, Resident Rms. | 3 | 304 | ea | 1731213.0954 | 2302513.4169 | 0 | 0 | 1957 | 25 | 1982 | Replace all reaching end of useful life failures reported | Also check on quantity as there is more than one convector per resident room. Revised quantity based on schedule from the drawings | SF
LARZELERE HALL | LA | MECH | 2201 | Heating Water System | Pumps | System/Basement Mech. Rm. | 3 | 2 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1957 | 20 | 1977 | Replace reaching end of useful life | price is for replacing 2 old pumps with 2 new vfd pumps | SF
LARZELERE HALL | LA | MECH | 2202 | Heating Water System | Insulation | Entire system | 3 | 76588 | sf | 116307.1479 | 154688.5066 | 0 | 0 | 1957 |  | 1957 | Replace reaching end of useful life. Reported ACM | Price is for replacement of insulation for heat piping | SF
LARZELERE HALL | LA | MECH | 2203 | Steam System | Piping | Entire system | 3 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1957 | 50 | 2007 | Replace reaching end of useful life reported failures | price is for replace steam piping from PRV station to new heat exchanger | SF
LARZELERE HALL | LA | MECH | 2204 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 76588 | sf | 266537.2138 | 354494.4944 | 0 | 0 | 1957 | 40 | 1997 | Replace all, reaching end of useful life failures reported | Price is for replacing existing drainage piping only. Minor architectural demo and patching/replacement of finishes is included | SF
LARZELERE HALL | LA | MECH | 2205 | Domestic hot water system | Heater/Steam | Entire building/Basement Mech. Rm. | 3 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1957 | 24 | 1981 | Replace reaching end of useful life, add mixing valves for scald protection | Price is for replacing one heat exchanger with a new unit. | SF
LARZELERE HALL | LA | EH&S | 2206 | Environmental Health and Safety | Asbsetos abatement | Allowance for mech | 3 | 76588 | sf | 387690.4928 | 515628.3555 | 0 | 0 | 1957 |  | 1957 |  |  | SF
LARZELERE HALL | LA | ELEC | 2207 | Service | Oil Switches |  | 5 | 1 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1957 | 50 | 2007 |  | What should be priced What should be priced - A 15 kV, 600A fused switch in a NEMA 1 enclosure with 4" concrete housekeeping pad. There was room to accommodate a switch in the existing electrical room. | SF
LARZELERE HALL | LA | ELEC | 2208 | Transformers | (2) 75 kVA for 120/240 volt, single phase and (1) 30 kVA for 480 volt, three phase |  | 5 | 3 | Total | 379651.9946 | 504937.1528 | 0 | 0 | 1957 | 50 | 2007 | Undersized for current code | Price is for replacing the existing 3 transformers | SF
LARZELERE HALL | LA | ELEC | 2209 | Distribution Panel | DLP | Split Bus 200A Each | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1957 | 50 | 2007 |  |  | SF
LARZELERE HALL | LA | ELEC | 2210 | Distribution Panel | DPP | 100A | 5 | 20 | ea | 189825.9973 | 252468.5764 | 0 | 0 | 1957 | 50 | 2007 | (20) 3P Circuits |  | SF
LARZELERE HALL | LA | ELEC | 2211 | Panelboards | Assume 125A 30 CKT | Varies | 5 | 19 | ea | 192357.0106 | 255834.8241 | 0 | 0 | Unknown |  | 0 | All panels need replacement. New panels should include AFCI breakers for dwelling areas. This does not allow for growth. |  | SF
LARZELERE HALL | LA | ELEC | 2212 | Exterior Lighting |  |  | 3 | 6 | ea | 3796.5199 | 5049.3715 | 0 | 0 | Unknown |  | 0 | Replace luminaries | price is for replacing 6 exterior lights for new fixtures | SF
LARZELERE HALL | LA | LSAF | 2213 | Life Safety | Fire Alarm |  | 5 | 80068 | sf | 506632.9317 | 673821.7992 | 0 | 0 | 1957 |  | 1957 | Not code compliant, old technology |  | SF
LARZELERE HALL | LA | LSAF | 2214 | Life Safety | Area of Refuge |  |  |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 |  |  | SF
LARZELERE HALL | LA | LSAF | 2215 | Life Safety | Emergency Lighting |  | 3 | 30 | ea | 18982.5997 | 25246.8576 | 0 | 0 | Unknown |  | 0 | EBU's, not fully code compliant |  | SF
LARZELERE HALL | LA | LSAF | 2216 | Life Safety | Add Life Safety Generator | None | 3 | 1 | ea | 63275.3324 | 84156.1921 | 0 | 0 | Unknown |  | 0 | Assume 30 kW, 200A ATS, 3 Panelboards | Price is for adding new generator and panels | SF
MERRILL HALL | ME | ARCH | 2217 | Envelope | Exterior Walls | Base limestone at stairs | 4 | 1000 | sf | 6327.5332 | 8415.6192 | 0 | 0 | 1960 | 50 | 2010 | Apply sealant to approximately 1,000 SF of limestone |  | SF
MERRILL HALL | ME | ARCH | 2218 | Envelope | Windows |  | 3 | 1115 | sf | 77607.1946 | 103217.5736 | 0 | 0 | 1960 | 30 | 1990 | Replace all exterior windows |  | SF | 654066 | 2014-08-01 | 237699.41 | completed 75%; stairwells & Lounge windows remain
MERRILL HALL | ME | ARCH | 2219 | Conveying Systems | Elevators & Llifts | cylinder replacement | 5 | 1 | ea | 39144.909 | 52062.729 | 0 | 0 | 1960 | 30 | 1990 | Recommended by Otis Elevator May 1, 2013 letter. Scheduled for 2014. |  | SF
MERRILL HALL | ME | ARCH | 2220 | Conveying Systems | Elevators & Llifts | modernization | 3 | 1 | ea | 64347.7957 | 85582.5683 | 0 | 0 | 1960 | 30 | 1990 | Recommended by Otis Elevator May 1, 2013 letter. Scheduled for 2021. |  | SF
MERRILL HALL | ME | MECH | 2221 | Ventilation/Terminal Units | AHU/No Cool/Steam Heat | AHU-1/Basement Mech. Rm. | 3 | 6000 | cfm | 75930.3989 | 100987.4306 | 0 | 0 | 1960 | 30 | 1990 | Replace reaching end of useful life |  | SF
MERRILL HALL | ME | MECH | 2222 | Steam System | Piping | Entire system | 3 | 69756 | sf | 242760.8749 | 322871.9636 | 0 | 0 | 1960 | 50 | 2010 | Replace condensate piping, failures observed |  | SF
MERRILL HALL | ME | MECH | 2223 | Building Management | HVAC Control | Pneumatic | 3 | 69756 | sf | 353106.7271 | 469631.9471 | 0 | 0 | 1960 | 25 | 1985 | Replace with DDC | price is for replacing existing pneumatic controls with new DDC controls | SF
MERRILL HALL | ME | MECH | 2224 | Storm/Sanitary sewer system | Sump pumps | Rm. 016 | 4 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | unknown | 10 | 10 | Replace with duplex, failures reported | price is for replacing 1 sump pump with a new one and reconnect to existing pipes | SF
MERRILL HALL | ME | MECH | 2225 | Domestic cold water system | Piping | Entire building | 3 | 69756 | sf | 264830.0454 | 352223.9603 | 0 | 0 | 1960 | 40 | 2000 | Good condition, no reported problems. Reported galvanized/copper mix |  | SF
MERRILL HALL | ME | MECH | 2226 | Domestic hot water system | Piping | Entire building | 3 | 69756 | sf | 264830.0454 | 352223.9603 | 0 | 0 | 1960 | 40 | 2000 | Good condition, no reported problems. Reported galvanized/copper mix |  | SF
MERRILL HALL | ME | EH&S | 2227 | Environmental Health & Safety | Asbestos Abatement | Allowance | 3 | 48200 | sf | 243989.6819 | 324506.2769 | 0 | 0 | 1960 |  | 1960 |  |  | SF
MERRILL HALL | ME | ELEC | 2228 | Distribution | Panelboards | Bsmnt Vault | 1 | 12 | Total | 0 | 0 | 0 | 0 | 1960 | 50 | 2010 | Replace with 125A Panelboard |  | SF | 654076 | 2014-08-01 | 3021847.86 | Part of South Quad Improvements included FCA project #'s 2373,2374,2390,2391,2392,2228,2229,1934,1935,1936,2257
MERRILL HALL | ME | LSAF | 2229 | Life Safety | Fire Alarm |  | 1 | 69756 | sf | 0 | 0 | 0 | 0 | Unknown | 40 | 40 | Complete building upgrade |  | SF | 654076 | 2014-08-01 | 3021847.86 | Part of South Quad Improvements included FCA project #'s 2373,2374,2390,2391,2392,2228,2229,1934,1935,1936,2257
MERRILL HALL | ME | LSAF | 2230 | Life Safety | Area of Refuge | Allowance |  |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | SF |  |  |  | Building fully sprinkled not required
MERRILL DINING | MF | ARCH | 2231 | Exterior Structure | Windows | Exterior windows | 4 | 5725 | sf | 398476.406 | 529973.62 | 0 | 0 | 1960 | 30 | 1990 | Replace all exterior windows |  | SF
MERRILL DINING | MF | ARCH | 2232 | Interior Structure | Ceiling Finishes |  | 3 |  |  | 0 | 0 | 0 | 0 | 1960 |  | 1960 |  |  | SF
MERRILL DINING | MF | ARCH | 2233 | Interior Structure | Ceililng Finishes | Tectum over cooking area | 4 | 2000 | sf | 50620.2659 | 67324.9537 | 0 | 0 | 1960 | 20 | 1980 | Tectum tile should be replaced with cleanable tile (approx 2,000 SF) |  | SF
MERRILL DINING | MF | EH&S | 2234 | Environmental Health and Safety | Asbestos abatement | Allowance for ceiling | 4 | 2000 | sf | 7593.0399 | 10098.7431 | 0 | 0 | 1960 |  | 1960 |  |  | SF
MERRILL DINING | MF | ARCH | 2235 | Conveying Systems | Elevators & Llifts | modernization | 1 | 1 | ea | 0 | 0 | 0 | 0 | 1960 |  | 1960 | Otis recommends work in 2013 per May 1, 2013 letter. |  | SF | 684210 | 2013-08-01 | 40495
MERRILL DINING | MF | ARCH | 2236 | Conveying Systems | Elevators & Llifts | cylinder replacement | 4 | 1 | ea | 39144.909 | 52062.729 | 0 | 0 | 1960 |  | 1960 | Otis recommends work in 2014 per May 1, 2013 letter. |  | SF
MERRILL DINING | MF | MECH | 2237 | Ventilation/Terminal Units | AHU/No Cool/Steam Heat | AHU-1/Basement under kitchen | 3 | 6000 | cfm | 75930.3989 | 100987.4306 | 0 | 0 | 1960 | 30 | 1990 | Replace with roof mounted equipment, reaching end of useful life | Mechanical information taken from mechanical sheets dated 8/21/59 | SF
MERRILL DINING | MF | MECH | 2238 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | RTU-1/South Roof | 3 | 7.5 | Tons | 32903.1729 | 43761.2199 | 0 | 0 | 2001 | 15 | 2016 | Good condition, evaluate cooling load requirements |  | SF
MERRILL DINING | MF | MECH | 2239 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | RTU-2/South Roof | 3 | 7.5 | Tons | 32903.1729 | 43761.2199 | 0 | 0 | 2001 | 15 | 2016 | Good condition, evaluate cooling load requirements |  | SF
MERRILL DINING | MF | MECH | 2240 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | RTU-3/South Roof | 3 | 7.5 | Tons | 32903.1729 | 43761.2199 | 0 | 0 | 2001 | 15 | 2016 | Good condition, evaluate cooling load requirements |  | SF
MERRILL DINING | MF | MECH | 2241 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | RTU-4/North Roof | 3 | 7.5 | Tons | 32903.1729 | 43761.2199 | 0 | 0 | 2001 | 15 | 2016 | Good condition, evaluate cooling load requirements |  | SF
MERRILL DINING | MF | MECH | 2242 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | RTU-5/North Roof | 3 | 7.5 | Tons | 32903.1729 | 43761.2199 | 0 | 0 | 2001 | 15 | 2016 | Good condition, evaluate cooling load requirements |  | SF
MERRILL DINING | MF | MECH | 2243 | Ventilation/Terminal Units | RTU/DX Cool/Nat. Gas Heat | RTU-6/North Roof | 3 | 7.5 | Tons | 32903.1729 | 43761.2199 | 0 | 0 | 2001 | 15 | 2016 | Good condition, evaluate cooling load requirements |  | SF
MERRILL DINING | MF | MECH | 2244 | Ventilation/Terminal Units | Terminal units | Steam Cabinet Heater/South entrance | 3 | 2 | ea | 11389.5598 | 15148.1146 | 0 | 0 | 1960 | 20 | 1980 | Replace with larger unit as this unit is reaching end of useful life and lacks capacity. |  | SF
MERRILL DINING | MF | MECH | 2245 | Storm/Sanitary sewer system | Piping | Entire Dining & Kitchen area | 3 |  |  | 0 | 0 | 0 | 0 | Various | 40 | 40 | Replace trench drain by steam kettles |  | SF
MERRILL DINING | MF | MECH | 2246 | Domestic cold water system | Piping | Entire Dining & Kitchen area | 3 | 61000 | sf | 270185.6695 | 359346.9404 | 0 | 0 | unknown | 40 | 40 | Verify that storage tank is installed |  | SF
MERRILL DINING | MF | MECH | 2247 | Domestic cold water system | Booster pump | Entire system/Basement Mech. Rm. | 2 |  |  | 0 | 0 | 0 | 0 | 2009 | 20 | 2029 | Good condition, no reported problems |  | SF
MERRILL DINING | MF | MECH | 2248 | Domestic hot water system | Piping | Entire Dining & Kitchen area | 3 | 61000 | sf | 270185.6695 | 359346.9404 | 0 | 0 | unknown | 40 | 40 | Install mixing valves for the resident halls for scald protection. |  | SF
MERRILL DINING | MF | MECH | 2249 | Domestic hot water system | Heater/Steam | Resident Halls/Basement Mech. Rm. | 3 | 4 | ea | 151860.7978 | 201974.8611 | 0 | 0 | 1979 | 24 | 2003 | Replace reaching end of useful life. Aerco SW1B08 |  | SF
MERRILL DINING | MF | EH&S | 2250 | Environmental Health & Safety | Asbestos abatement | allowance for mech items | 3 | 61000 | sf | 308783.6223 | 410682.2176 | 0 | 0 | Unknown |  | 0 |  |  | SF
MERRILL DINING | MF | ELEC | 2251 | Panelboards | 125A, 120/240, 1ph | Kitchen | 4 | 3 |  | 28473.8996 | 37870.2865 | 0 | 0 | 1960 | 40 | 2000 | 30 pole panel with breakers |  | SF
MERRILL DINING | MF | ELEC | 2252 | Distribution | 150A, 120/240, 1ph | Kitchen | 4 | 2 |  | 18982.5997 | 25246.8576 | 0 | 0 | 1960 | 40 | 2000 | 30 pole panel with breakers |  | SF
MERRILL DINING | MF | ELEC | 2253 | Distribution | 225A, 120/240, 1ph | Kitchen | 4 | 3 |  | 28473.8996 | 37870.2865 | 0 | 0 | 1960 | 40 | 2000 | 42 pole panel with breakers |  | SF
MERRILL DINING | MF | ELEC | 2254 | Lighting/Controls | Interior |  | 3 | 61000 | sf | 65420.259 | 87008.9444 | 0 | 0 | Unknown | 20 | 20 | Needs automatic controls with renovation |  | SF
MERRILL DINING | MF | ELEC | 2255 | Interior Lighting | Kitchen Area | 2x4,K-12 lens 3L,T8 | 4 | 10 | ea | 4429.2733 | 5890.9334 | 0 | 0 | Unknown | 20 | 20 | Approx. 2000 square feet |  | SF
MERRILL DINING | MF | ELEC | 2256 | Lighting | Downlights with open apertures | Food Service | 5 | 40 |  | 25310.133 | 33662.4769 | 0 | 0 | Unknown | 20 | 20 | Provide lenses for the downlights. Lamps cannot be exposed. |  | SF
MERRILL DINING | MF | LSAF | 2257 | Life Safety | Fire Alarm |  | 1 | 61000 | sf | 0 | 0 | 0 | 0 | Unknown | 40 | 40 | Kitchen area portion may need to be updated to the addressable system |  | SF | 654076 | 2014-08-01 | 3021847.86 | Part of South Quad Improvements included FCA project #'s 2373,2374,2390,2391,2392,2228,2229,1934,1935,1936,2257
MERRILL DINING | MF | LSAF | 2258 | Life Safety | Area of Refuge | Allowance |  |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | SF |  |  |  | Building fully sprinkled not required
NORTHWEST APARTMENTS | NW | ARCH | 2259 | Envelope | SOG | Exterior walks & stoups | 4 | 1680 | sf | 21260.5117 | 28276.4806 | 0 | 0 | 1967 | 100 | 2067 | Replace 30 4' x 4' stops and 300 feet of 4 foot wide sidewalk | Price is for replacing 30 4' x 4' stoops and about 1,200 sf of 4" sidewalk. | SF
NORTHWEST APARTMENTS | NW | ARCH | 2260 | Envelope | Site water |  | 4 | 0.5 | acre | 69602.8657 | 92571.8114 | 0 | 0 | 1967 |  | 1967 | Regrade 1/4 acre adjacent to buildings 3 and 5 to redirect site water | Price is for regrading 2 1/4 acre areas next to buildings 3 and 5. Price also includes hydro seeding. | SF
NORTHWEST APARTMENTS | NW | ELEC | 2261 | Distribution | Main Switch gear 120/240 1 phase |  | 4 | 7 | ea | 70868.3723 | 94254.9352 | 0 | 0 | 1967 | 40 | 2007 | (4) at 100A, (2) at 400A, (1) at 200A | Price is for replacing 4-100A panels, 2 400A Panels and 1 200A panel and reconnect to existing feeds | SF
NORTHWEST APARTMENTS | NW | ELEC | 2262 | Distribution | Panelboards - | 100A NOW | 3 | 196 | ea | 1860294.7736 | 2474192.0488 | 0 | 0 | 1967 | 40 | 2007 | Multiple panels per feeder | Price is for replacing one distribution panel per apartment unit (total 196 units) and reconnect to existing feeds | SF
NORTHWEST APARTMENTS | NW | ELEC | 2263 | Feeders |  |  | 3 |  |  | 0 | 0 | 0 | 0 | 1967 | 40 | 2007 |  | Replace feeds | SF
NORTHWEST APARTMENTS | NW | ELEC | 2264 | Branch Circuit Condition | Not enough circuits |  | 3 | 196 | ea | 620098.2579 | 824730.6829 | 0 | 0 | 1967 |  | 1967 | Would require major remodel | Price is based on scope from Kewadin Apartments of adding (2) 20A circuits to the kitchen area and (1) 20 circuit to the bathroom, for a total of (3) per unit | SF
NORTHWEST APARTMENTS | NW | ELEC | 2265 | GFCI in Kitchen |  |  | 4 | 196 | ea | 124019.6516 | 164946.1366 | 0 | 0 | Unknown |  | 0 | Provide (1) per kitchen | Price is for adding 1 GFCI outlet to an existing curcuit in each kitchen | SF
NORTHWEST APARTMENTS | NW | ELEC | 2266 | Vanity Lighting |  |  | 3 | 392 | ea | 173627.5122 | 230924.5912 | 0 | 0 | unknown |  | 0 | (2) per bathroom | Price is for replacing 2 vanity lights per bathroom and reaplcing tem with new fixtures. Price is based on 1 bathroom per apartment (196 total) | SF
NORTHWEST APARTMENTS | NW | ELEC | 2267 | Lighting | Exterior (Old) |  | 4 | 32 | ea | 20248.1064 | 26929.9815 | 0 | 0 | Unknown |  | 0 | Replacement Luminaires - 175W MH |  | SF
NORTHWEST APARTMENTS | NW | LSAF | 2268 | Life Safety | Fire Alarm | Smoke Detectors | 3 | 334 | ea | 211339.6103 | 281081.6817 | 0 | 0 | Unknown | 40 | 40 | Single Station Smoke Detectors - Does not have proper coverage, assume adding 1 per bedroom | Price is for adding 1 smoke detector to every bedroom (334 total). | SF
NORTHWEST APARTMENTS | NW | LSAF | 2269 | Life Safety | Area of Refuge |  | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | SF
ROBINSON HALL | RB | ARCH | 2270 | Envelope | Roof |  | 3 | 24600 | sf | 716023.6618 | 952311.4702 | 0 | 0 | Unknown | 30 | 30 | Roof should be replaced in 3 to 5 years | Price is for the replacement of existing roof with a new roofing system. Similar to Therico roofing system | SF
ROBINSON HALL | RB | ARCH | 2271 | Envelope | Exterior Walls | Brick and CMU | 3 | 750 | lf | 23728.2497 | 31558.5721 | 0 | 0 | 1954 | 100 | 2054 | Repair approximately 750 linear feet of cracked brick or block | Price is for the repair of 750 lnft of damaged/broken brick. Some replacement is included in the budget | SF
ROBINSON HALL | RB | ARCH | 2272 | Envelope | Windows |  | 3 | 7500 | sf | 522021.4926 | 694288.5851 | 0 | 0 | 1954 | 30 | 1984 | Replace all windows | Price is for removing existing window and replacing them with new aluminum framed windows. Budget also includes new caulk around window and some finish patching around new windows | SF
ROBINSON HALL | RB | ARCH | 2273 | Interior Structure | Partitions/Walls |  | 3 | 1000 | lf | 25310.133 | 33662.4769 | 0 | 0 | 1954 | 40 | 1994 | Repair approximately 1,000 feet of cracked block | Price is for repairing about 1,000 lnft of damaged interior CMU walls and painting when finished | SF
ROBINSON HALL | RB | ARCH | 2274 | Conveying Systems | Elevators & Llifts |  | 5 | 2 | ea | 92381.9854 | 122868.0405 | 0 | 0 | Unknown | 30 | 30 | Elevator should be replaced or repaired in 3 to 5 years | Price is for the replacement of the existing elevator | SF
ROBINSON HALL | RB | ARCH | 2275 | Conveying Systems | Elevators & Llifts |  | 3 | 2 | ea | 151860.7978 | 201974.8611 | 0 | 0 | Unknown | 30 | 30 |  |  | SF
ROBINSON HALL | RB | ADAC | 2276 | Barrier Free Compliance | Building Access |  | 5 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1954 |  | 1954 | Building is not accessible, build ramp at main entry to match architecture | Price is for building a new accessible ramp at the main entry. Price does not include adding automatic openers or any door replacements | SF
ROBINSON HALL | RB | ADAC | 2277 | Barrier Free Compliance | Internal Circulation |  | 4 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1954 |  | 1954 | Add ramps at main floor entry | Price is for adding an accessible ramp to the first floor main entry lobby area. | SF
ROBINSON HALL | RB | ADAC | 2278 | Barrier Free Compliance | Doors & Hardware |  | 3 | 198 | ea | 125285.1582 | 166629.2604 | 0 | 0 | 1954 |  | 1954 | Replace hardware in 3 to 5 years | Price is for replacing existing door hardware with new hardware to meet ADA codes | SF
ROBINSON HALL | RB | ADAC | 2279 | Barrier Free Compliance | Toilet Rooms |  | 5 | 4120 | sf | 521388.7393 | 693447.0232 | 0 | 0 | 1954 |  | 1954 | Provide accessible toilet facilities | Price is for the renovation of bathroom areas to comply with ADA codes | SF
ROBINSON HALL | RB | MECH | 2280 | Ventilation/Terminal Units | AHU/No Cool/Steam Heat | AHU-1/S.E. Basement Mech. Rm. | 3 | 40000 | cfm | 506202.6595 | 673249.5371 | 0 | 0 | 1954 | 30 | 1984 | Replace reaching end of useful life | Price is for replacing existing AHU with a new 40,000 cfm model and reconnecting to existing mains | SF
ROBINSON HALL | RB | MECH | 2281 | Ventilation/Terminal Units | Terminal units | Fin Tube HW/Entire Building | 3 | 312 | lf | 110554.6608 | 147037.6989 | 0 | 0 | 1954 | 25 | 1979 | Replace all reaching end of useful life failures reported |  | SF
ROBINSON HALL | RB | MECH | 2282 | Ventilation/Terminal Units | Terminal units | HW Cabinet Heater/Main Entrance | 3 | 2 | ea | 11389.5598 | 15148.1146 | 0 | 0 | 1954 | 20 | 1974 | Replace all reaching end of useful life failures reported |  | SF
ROBINSON HALL | RB | MECH | 2283 | Ventilation/Terminal Units | Terminal units | HW Convectors/Stairs, Corridors, Resident Rms. | 3 | 66 | ea | 375855.4747 | 499887.7813 | 0 | 0 | 1954 | 25 | 1979 | Replace all reaching end of useful life failures reported |  | SF
ROBINSON HALL | RB | MECH | 2284 | Heating Water System | Pumps | System/Basement Mech. Rm. | 3 | 2 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1954 | 20 | 1974 | Replace reaching end of useful life | price is for replacing 2 heating water pumps with new units and reconnect to existing piping | SF
ROBINSON HALL | RB | MECH | 2285 | Heating Water System | Insulation | Entire system | 3 | 68351 |  | 103798.3739 | 138051.8373 | 0 | 0 | 1954 |  | 1954 | Replace reaching end of useful life. Reported ACM |  | SF
ROBINSON HALL | RB | MECH | 2286 | Steam System | Piping | Entire system | 3 | 1 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1954 | 50 | 2004 | Replace reaching end of useful life reported failures | Price is for replace piping to the PRV station only. | SF
ROBINSON HALL | RB | MECH | 2287 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 68351 | sf | 194621.9511 | 258847.195 | 0 | 0 | 1954 | 40 | 1994 | Replace all, reaching end of useful life failures reported | price is for replacing the existing drainage piping. Some architectural demo and repair/replacement of finishes is included | SF
ROBINSON HALL | RB | MECH | 2288 | Domestic hot water system | Heater/Steam | Entire building/Basement Mech. Rm. | 3 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1985 | 24 | 2009 | Replace reaching end of useful life, add mixing valves for scald protection | Price is for replacing one heat exchanger with a new unit. | SF
ROBINSON HALL | RB | EH&S | 2289 | Env Health & Safety | asbestos abatement | mech item alllowance | 3 | 68351 | sf | 345994.5798 | 460172.7911 | 0 | 0 | 1954 |  | 1954 |  |  | SF
ROBINSON HALL | RB | ELEC | 2290 | Distribution | DPA | 200A | 5 | 2 | ea | 25310.133 | 33662.4769 | 0 | 0 | 1966 | 50 | 2016 | All panels need replacement. New panels should include AFCI breakers for dwelling areas. This does not allow for growth or | Price is for replacing 2 - 200A panel boards with new units and reconnect to existing feeds | SF
ROBINSON HALL | RB | ELEC | 2291 | Panel boards | Assume 125A 30 CKT | Varies | 5 | 10 | ea | 94912.9987 | 126234.2882 | 0 | 0 | Unknown |  | 0 |  | price is for replacing 10 panelboards and reconnecting to existing feeds | SF
ROBINSON HALL | RB | ELEC | 2292 | Branch Circuit Condition | Original | Old, should be replaced | 3 |  | ea | 0 | 0 | 0 | 0 | Unknown |  | 0 | Rooms have inadequate receptacles and circuits |  | SF
ROBINSON HALL | RB | ELEC | 2293 | Exterior Lighting |  |  | 3 | 4 | ea | 2531.0133 | 3366.2477 | 0 | 0 | Unknown |  | 0 | Replace luminaries or lenses | Price is for replacing 4 existing exterior lights with new fixtures | SF
ROBINSON HALL | RB | LSAF | 2294 | Life Safety | Fire Alarm |  | 5 | 68351 | sf | 432493.2247 | 575215.9889 | 0 | 0 | 1966 |  | 1966 | Grandfathered, old technology | price is for upgrading building fire alarm system | SF
ROBINSON HALL | RB | LSAF | 2295 | Life Safety | Area of Refuge | Allowance | 5 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | Per S. Esch |  | SF
ROBINSON HALL | RB | LSAF | 2296 | Life Safety | Emergency Lighting |  | 3 | 30 | ea | 18982.5997 | 25246.8576 | 0 | 0 | Unknown |  | 0 | EBU's, grandfathered | Price is for adding around 30 emergency lights to building | SF
ROBINSON DINING | RF | ARCH | 2297 | Envelope | Windows |  | 4 | 1815 | sf | 126329.2012 | 168017.8376 | 0 | 0 | 1954 | 30 | 1984 |  |  | SF
ROBINSON DINING | RF | ARCH | 2298 | Envelope | Exterior Doors |  | 3 | 5 | ea | 31637.6662 | 42078.0961 | 0 | 0 | 1954 | 30 | 1984 |  |  | SF
ROBINSON DINING | RF | ARCH | 2299 | Interior Structure | #2 | Kitchen flooring | 3 | 500 | sf | 9491.2999 | 12623.4288 | 0 | 0 | Unknown | 15 | 15 | Operations has a concern with non-skid surface | Price is for adding non-skid flooring to about 500 sf of floor | SF
ROBINSON DINING | RF | EH&S | 2300 | Environmental Health & Safety | Asbestos Abatement | Kitchen flooring | 3 | 500 | sf | 1898.26 | 2524.6858 | 0 | 0 | 1954 |  | 1954 |  |  | SF
ROBINSON DINING | RF | ARCH | 2301 | Interior Structure | #2 | Area below loading dock | 4 | 100 | sf | 2531.0133 | 3366.2477 | 0 | 0 | 1954 |  | 1954 | Water damage below loading dock, approximately 100 SF of repair required | Price is based on repairing about 100 sf of ceiling area | SF
ROBINSON DINING | RF | ARCH | 2302 | Interior Structure | Fixed Equip/Furnishing | Older kitchen equipment | 3 |  |  | 0 | 0 | 0 | 0 | 1954 | 40 | 1994 | Operations indicated equipment is old, breaks down and difficult to repair | Part of DM scope? | SF
ROBINSON DINING | RF | ADAC | 2303 | Barrier Free Compliance | Toilet Rooms |  | 3 | 515 | sf | 65173.5924 | 86680.8779 | 0 | 0 | Unknown |  | 0 | Toilet rooms are not ADA-accessible |  | SF
ROBINSON DINING | RF | MECH | 2304 | Ventilation/Terminal Units | AHU/No Cool/Steam Heat | MUA-1/S.W. Kitchen above Walk In Coolers | 1 | 1 | ea | 0 | 0 | 0 | 0 | 1999 | 30 | 2029 | Replace, problematic installation, failing steam coil. Replace with natural gas fired roof mounted equipment. | Price is for a new 5 ton RTU. Price includes $5,000 for pipe rework and tying back into existing system | SF | 654074 | 2014-08-01 | 65355.05 | Work also include the installation of new gas service due to load requirements
ROBINSON DINING | RF | MECH | 2305 | Ventilation/Terminal Units | AHU/DX Cool/No Heat | AC Split/ Testing Center Booths | 3 | 3 | Tons | 32903.1729 | 43761.2199 | 0 | 0 | Unknown | 15 | 15 | Replace reaching end of useful life |  | SF
ROBINSON DINING | RF | MECH | 2306 | Ventilation/Terminal Units | Terminal units | Steam Unit Ventilators/Dining rooms | 4 | 7 | ea | 26575.6396 | 35345.6007 | 0 | 0 | 1954 | 20 | 1974 | Replace reaching end of useful life reported failures. Consider replacement with central air handler with heating and cooling capability. |  | SF
ROBINSON DINING | RF | MECH | 2307 | Steam System | Piping | Entire system | 4 | 67791 | sf | 235922.6132 | 313777.0112 | 0 | 0 | 1954 | 50 | 2004 | Replace reaching end of useful life reported failures of condensate piping |  | SF
ROBINSON DINING | RF | MECH | 2308 | Storm/Sanitary sewer system | Piping | Entire Dining & Kitchen area | 3 | 67791 | sf | 235922.6132 | 313777.0112 | 0 | 0 | 1954 | 40 | 1994 | Replace remaining 70%, reaching end of useful life failures reported |  | SF
ROBINSON DINING | RF | MECH | 2309 | Domestic cold water system | Piping | Entire Dining & Kitchen area | 3 | 67791 | sf | 343160.3597 | 456402.8279 | 0 | 0 | 1954 | 40 | 1994 | No reported problems, replace galvanized portions as they are reaching the end of there useful life. Quantity of galvanized remaining is unknown |  | SF
ROBINSON DINING | RF | MECH | 2310 | Domestic hot water system | Piping | Entire Dining & Kitchen area | 3 | 67791 | sf | 343160.3597 | 456402.8279 | 0 | 0 | 1954 | 40 | 1994 | No reported problems, replace galvanized portions as they are reaching the end of there useful life. Quantity of galvanized remaining is unknown |  | SF
ROBINSON DINING | RF | MECH | 2311 | Domestic hot water system | Heater/Steam | Entire building/Basement Mech. Rm. Robinson Hall | 3 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1985 | 24 | 2009 | Replace reaching end of useful life. AERCO similar to a model SW1B+07 |  | SF
ROBINSON DINING | RF | EH&S | 2312 | Environmental Health & Safety | Asbestos abatement | allowance for mech | 3 | 67791 | sf | 343159.8449 | 456402.5937 | 0 | 0 | 1954 |  | 1954 |  |  | SF
ROBINSON DINING | RF | ELEC | 2313 | Service | 480 Transformer | Vault | 4 | 1 | ea | 50620.2659 | 67324.9537 | 0 | 0 | 1954 |  | 1954 | Replace with new OFPM |  | SF
ROBINSON DINING | RF | ELEC | 2314 | Distribution | 480 Main | Basement | 5 | 1 | ea | 12655.0665 | 16831.2384 | 0 | 0 | 1954 | 40 | 1994 | Replace main 480 panel |  | SF
ROBINSON DINING | RF | ELEC | 2315 | Distribution | Distribution Panelboards | Throughout | 4 | 13 | ea | 123386.8982 | 164104.5747 | 0 | 0 | 1954 | 40 | 1994 | Replace all distribution panels | Quantity was taken from Electrical upgrade drawings 1 and 2 dated 10-5-90 | SF
ROBINSON DINING | RF | ELEC | 2316 | Branch Circuit Condition | Assumed original |  | 4 | 67791 | sf | 223054.1265 | 264755.3805 | 0 | 0 | 1954 | 40 | 1994 | Re-wire existing circuits |  | SF
ROBINSON DINING | RF | LSAF | 2317 | Life Safety | Fire Alarm | Building | 5 | 67791 | sf | 428949.8061 | 570503.2421 | 0 | 0 | 1954 | 30 | 1984 | New system required | Capital Improvement? | SF
ROBINSON DINING | RF | LSAF | 2318 | Life Safety | Area of Refuge |  | 5 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | 1954 |  | 1954 | per S. Esch |  | SF
ROBINSON DINING | RF | LSAF | 2319 | Life Safety | Emergency Lighting | Throughout | 4 | 67791 | sf | 257369.7335 | 343160.3597 | 0 | 0 | 1990 | 10 | 2000 | New system required | Capital Improvement? | SF
SAXE HALL | SA | ARCH | 2320 | Envelope | Windows | Alum. single pane | 3 | 7830 | sf | 445901.2677 | 593048.686 | 0 | 0 | 1966 | 30 | 1996 | Windows are in good condition for age but should be replaced for energy savings and to update the building since they are almost 50 years old. |  | SF
SAXE HALL | SA | ARCH | 2321 | Envelope | Exterior Doors | Building Entrance | 3 | 20 | ea | 126550.6649 | 168312.3843 | 0 | 0 | 1966 | 30 | 1996 | Replace doors to match new campus standard exterior doors. |  | SF
SAXE HALL | SA | ARCH | 2322 | Interior Structure | Partitions | CMU walls painted | 3 | 26500 | sf | 83839.8155 | 111506.9546 | 0 | 0 | 1966 | 40 | 2006 | Interior corridor walls to be repainted. |  | SF
SAXE HALL | SA | ARCH | 2323 | Interior Structure | Interior Doors | Wood | 3 | 120 | ea | 75930.3989 | 100987.4306 | 0 | 0 | 1966 | 30 | 1996 | Hardware has been replaced on room entry doors. |  | SF
SAXE HALL | SA | ARCH | 2324 | Floor Finishes | Corridor | Carpet | 3 | 8110 | sf | 56447.9241 | 75075.739 | 0 | 0 | 1990 | 15 | 2005 | Carpet in all corridors will need replacement within 3 years. |  | SF
SAXE HALL | SA | ARCH | 2325 | Floor Finishes | Rooms | VCT | 3 | 27000 | sf | 170843.3976 | 227221.7188 | 0 | 0 | 1990 | 15 | 2005 | Student rooms need new flooring. |  | SF
SAXE HALL | SA | ARCH | 2326 | Floor Finishes | Toilet Rooms - Rooms | Ceramic Tile | 3 | 3000 | sf | 56947.7992 | 75740.5729 | 0 | 0 | 1990 | 20 | 2010 | Floor to be replaced in next 10 years. |  | SF
SAXE HALL | SA | ARCH | 2327 | Floor Finishes | Toilet Rooms | Public | 3 | 3000 | sf | 379651.9946 | 504937.1528 | 0 | 0 | 1966 | 30 | 1996 | Not ADA Accessible. Renovate toilet rooms to make them accessible. |  | SF
SAXE HALL | SA | ARCH | 2328 | Wall Finishes | Painted | Corridor | 3 | 26500 | sf | 83839.8155 | 111506.9546 | 0 | 0 | 1966 | 30 | 1996 | Corridor walls have been painted but need repainting. |  | SF
SAXE HALL | SA | ARCH | 2329 | Ceiling Finishes | 12" x 12" Spline Ceiling | Corridor | 3 | 8110 | sf | 75191.4181 | 100004.5861 | 0 | 0 | 1966 | 30 | 1996 | Replace ceilings in all corridors with 2' x 2' lay-in ceiling and lighting. | Unit price increased because of the added demo of the splined ceiling | SF
SAXE HALL | SA | ARCH | 2330 | Conveying Systems | Elevators |  | 5 | 1 | ea | 39144.909 | 52062.729 | 0 | 0 | Unknown | 30 | 30 | Otis recommends cylinder replacement in 2014. |  | SF
SAXE HALL | SA | EH&S | 2331 | Environmental Health & Safety | asbestos abatement | allowance for ceilings | 3 | 8110 | SF | 115679.1048 | 153853.2094 | 0 | 0 | 1966 |  | 1966 |  |  | SF
SAXE HALL | SA | MECH | 2332 | Ventilation/Terminal Units | Terminal units | HW Cabinet Heaters/Entrance | 3 | 5 | ea | 28473.8996 | 37870.2865 | 0 | 0 | 1966 | 25 | 1991 | Good condition, no reported problems |  | SF
SAXE HALL | SA | MECH | 2333 | Heating Water System | Piping | Entire system | 3 | 70500 | sf | 740511.2155 | 984879.9166 | 0 | 0 | 1966 | 40 | 2006 | Fair condition, reported restrictions from scale, chemical treatment program has been established. |  | SF
SAXE HALL | SA | MECH | 2334 | Heating Water System | Insulation | Entire system | 3 | 70500 | sf | 107061.8625 | 142392.2771 | 0 | 0 | 1966 |  | 1966 | Good condition, reported to be some ACM |  | SF
SAXE HALL | SA | MECH | 2335 | Steam System | Piping | Entire system | 3 | 70500 | sf | 254271.9234 | 338181.6581 | 0 | 0 | 1966 | 50 | 2016 | Good condition, no reported problems |  | SF
SAXE HALL | SA | MECH | 2336 | Building Management | HVAC Control | Pneumatic | 3 | 70500 | sf | 356872.8749 | 474640.9237 | 0 | 0 | 1966 | 25 | 1991 | Replace with DDC with future renovation |  | SF
SAXE HALL | SA | MECH | 2337 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 70500 | sf | 156131.8828 | 207655.4041 | 0 | 0 | 1966 | 40 | 2006 | Good condition, reported that the base of some stacks have rotted out at grade level |  | SF
SAXE HALL | SA | MECH | 2338 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rm. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown | 10 | 10 | Replace as a precautionary measure |  | SF
SAXE HALL | SA | MECH | 2339 | Domestic cold water system | Piping | Entire building | 3 | 70500 | sf | 254271.9234 | 338181.6581 | 0 | 0 | Unknown | 40 | 40 | Good condition, no reported problems |  | SF
SAXE HALL | SA | MECH | 2340 | Domestic hot water system | Piping | Entire building | 3 | 70500 | sf | 254271.9234 | 338181.6581 | 0 | 0 | Unknown | 40 | 40 | Good condition, no reported problems |  | SF
SAXE HALL | SA | EH&S | 2341 | Environmental Health and Safety | asbestos abatement | allowance for mech items | 3 | 65884 | sf | 333506.5602 | 443563.725 | 0 | 0 | 1966 |  | 1966 |  |  | SF
SAXE HALL | SA | ELEC | 2342 | Branch Circuit Condition Unlabeled ITE with contactor |  | Room 037 | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1965 | 40 | 2005 | Needs Upgrade |  | SF
SAXE HALL | SA | ELEC | 2343 | Branch Circuit Condition | Panel LP-1E ITE | Terrice | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1965 | 40 | 2005 | Needs Upgrade |  | SF
SAXE HALL | SA | ELEC | 2344 | Branch Circuit Condition | Panel 1-C ITE | Terrice | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1965 | 40 | 2005 | Needs Upgrade |  | SF
SAXE HALL | SA | ELEC | 2345 | Branch Circuit Condition | Panel 1-B ITE | Terrice | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1965 | 40 | 2005 | Needs Upgrade |  | SF
SAXE HALL | SA | ELEC | 2346 | Branch Circuit Condition | Panel 1-A ITE | Terrice | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1965 | 40 | 2005 | Needs Upgrade |  | SF
SAXE HALL | SA | ELEC | 2347 | Branch Circuit Condition | Panel 2 PLA ITE | 2nd Floor | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1965 | 40 | 2005 | Needs Upgrade |  | SF
SAXE HALL | SA | ELEC | 2348 | Branch Circuit Condition | Panel 2 PLB ITE | 2nd Floor | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1965 | 40 | 2005 | Needs Upgrade |  | SF
SAXE HALL | SA | ELEC | 2349 | Branch Circuit Condition | Panel 2 PLC ITE | 2nd Floor | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1965 | 40 | 2005 | Needs Upgrade |  | SF
SAXE HALL | SA | ELEC | 2350 | Branch Circuit Condition | Panel 3LPA ITE | 3rd Floor | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1965 | 40 | 2005 | Needs Upgrade |  | SF
SAXE HALL | SA | ELEC | 2351 | Branch Circuit Condition | Panel 3 LPB ITE | 3rd Floor | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1965 | 40 | 2005 | Needs Upgrade |  | SF
SAXE HALL | SA | ELEC | 2352 | Branch Circuit Condition | Panel 3 LPC ITE | 3rd Floor | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1965 | 40 | 2005 | Needs Upgrade |  | SF
SAXE HALL | SA | ELEC | 2353 | Lighting | Surface Incandescent fixture | Entrance | 4 | 6 | ea | 3796.5199 | 5049.3715 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade |  | SF
SAXE HALL | SA | ELEC | 2354 | Lighting | single lamp tamper resistant surface fixtures | Corridors | 3 | 120 | ea | 53151.2792 | 70691.2014 | 0 | 0 | Unknown |  | 0 | Needs upgrade |  | SF
SAXE HALL | SA | ELEC | 2355 | Lighting | Surface mounted 2 lamp fluorescent fixtures | Dorms | 3 | 616 | ea | 272843.2335 | 362881.5005 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade |  | SF
SAXE HALL | SA | ELEC | 2356 | Lighting | Surface mounted 2 lamp fluorescent fixtures | Kitchenettes | 3 | 88 | ea | 38977.6048 | 51840.2144 | 0 | 0 | Unknown | 20 | 20 | Needs upgrade |  | SF
SAXE HALL | SA | ELEC | 2357 | Lighting/Controls | Occupancy sensors | Building | 3 | 70500 | sf | 89218.2187 | 118660.2309 | 0 | 0 | Unknown |  | 0 | No controlled lighting |  | SF
SAXE HALL | SA | LSAF | 2358 | Life Safety | Simplex Fire Alarm System model 4100U | Woldt Dining/Sleep Rooms | 3 | 70500 | sf | 446091.0937 | 593301.1546 | 0 | 0 | 1965 |  | 1965 | No devices in rooms | Capital Improvement? | SF
SAXE HALL | SA | LSAF | 2359 | Life Safety | Area of Refuge | Allowance | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | 1965 |  | 1965 | per S. Esch |  | SF
SAXE HALL | SA | LSAF | 2360 | Life Safety | Emergency Lighting | Building | 3 | 30 | ea | 18982.5997 | 25246.8576 | 0 | 0 | Unknown |  | 0 | Wall mounted battery packs in corridors not in rooms |  | SF
SWEENEY HALL | SW | ARCH | 2361 | Envelope | Windows | Original windows | 4 | 4460 | sf | 310428.7809 | 412870.2786 | 0 | 0 | 1960 | 30 | 1990 | Replace all exterior windows | Price is for removing existing windows and replacing them with new aluminum framed windows. Price includes new caulk around windows and minor patch/repair of adjacent finishes | SF
SWEENEY HALL | SW | ARCH | 2362 | Conveying Systems | Elevators & Llifts | Control System | 1 | 1 | ea | 0 | 0 | 0 | 0 | 1960 |  | 1960 | Otis modernization recommended for hydraulic control system 2013 | Refer to Otis Proposal # CWV-12051105 | SF | 684209 | 2013-08-15 | 42560
SWEENEY HALL | SW | ARCH | 2363 | Conveying Systems | Elevators & Llifts | Cylinder Replacement | 4 | 1 | ea | 40217.3723 | 53489.1052 | 0 | 0 | 1960 |  | 1960 | Otis recommends cylinder replacement in 2016. | Refer to Otis Elevator Letter May 1, 2013. | SF
SWEENEY HALL | SW | MECH | 2364 | Ventilation/Terminal Units | AHU/No Cool/Steam Heat | AHU-1/Basement Mech. Rm. | 3 | 6000 | cfm | 75930.3989 | 100987.4306 | 0 | 0 | 1960 | 30 | 1990 | Replace reaching end of useful life | Price is for removing AHU and replacing it with a new 6,000 CFM unit and reconnecting to existing mains. | SF
SWEENEY HALL | SW | MECH | 2365 | Heating Water System | Insulation | Entire system | 3 | 74557 | sf | 113223.1639 | 150586.7115 | 0 | 0 | 1960 | 40 | 2000 | Good condition, reported to be some ACM | Price is for replacing heat water piping insulation with new. | SF
SWEENEY HALL | SW | MECH | 2366 | Steam System | Piping | Entire system | 3 | 74557 | sf | 268904.0759 | 357642.9036 | 0 | 0 | 1960 | 50 | 2010 | Replace condensate piping, failures observed |  | SF
SWEENEY HALL | SW | MECH | 2367 | Building Management | HVAC Control | Pneumatic | 3 | 74557 | sf | 377409.4739 | 501954.6325 | 0 | 0 | 1960 | 25 | 1985 | Replace with DDC | Price is for replacing existing pneumatic controls with new DDC controls | SF
SWEENEY HALL | SW | MECH | 2368 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rm. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | unknown | 10 | 10 | Replace entire duplex unit as precautionary measure | Price is for replacing 1 existing sump pump with a new one and reconnect to existing piping | SF
SWEENEY HALL | SW | MECH | 2369 | Domestic cold water system | Piping | Entire building | 3 | 74557 | sf | 268904.0759 | 357642.9036 | 0 | 0 | 1960 | 40 | 2000 | Good condition, no reported problems. Reported galvanized/copper mix |  | SF
SWEENEY HALL | SW | MECH | 2370 | Domestic hot water system | Piping | Entire building | 3 | 74557 | sf | 268904.0759 | 357642.9036 | 0 | 0 | 1960 | 40 | 2000 | Good condition, no reported problems. Reported galvanized/copper mix |  | SF
SWEENEY HALL | SW | EH&S | 2371 | Environmental Health & Safety | Asbestos Abatement Allowance | Mechanical Systems | 3 | 74557 | sf | 377409.5168 | 501954.6574 | 0 | 0 | Unknown |  | 0 |  |  | SF
SWEENEY HALL | SW | ELEC | 2372 | Distribution | Panelboards | Bsmnt Vault | 1 | 12 | Total | 0 | 0 | 0 | 0 | 1960 | 50 | 2010 | Replace with 125A Panelboard | Price is for replacing 12 existing panels with new and reconnect to existing feeds | SF | 654076 | 2014-08-01 | 30211847.86 | Part of South Quad Improvements included FCA project #'s 2373,2374,2390,2391,2392,2228,2229,1934,1935,1936,2257
SWEENEY HALL | SW | LSAF | 2373 | Life Safety | Fire Alarm | Entire building | 1 | 74557 | sf | 0 | 0 | 0 | 0 | Unknown | 40 | 40 | Complete building upgrade | Price is for upgrading existing building fire alarm system | SF | 654076 | 2014-08-01 | 3021847.86 | Part of South Quad Improvements included FCA project #'s 2373,2374,2390,2391,2392,2228,2229,1934,1935,1936,2257
SWEENEY HALL | SW | LSAF | 2374 | Life Safety | Area of Refuge |  |  |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | SF |  |  |  | Building fully sprinkled not required
THORPE HALL | TH | ARCH | 2375 | Envelope | Windows | Existing aluminum | 4 | 5330 | sf | 370983.2741 | 493407.7545 | 0 | 0 | 1962 | 30 | 1992 | Replace all windows | Price is for removing existing windows and replacing them with new aluminum framed windows. Price includes new caulk around windows and minor patch/repair of adjacent finishes | SF
THORPE HALL | TH | ARCH | 2376 | Interior Structure | Partitions/Walls | Resident room 124 & 104 | 4 | 36 | lf | 683.3736 | 908.8869 | 0 | 0 | 1962 | 40 | 2002 | Room 124- repair 20 feet of horizontal crack in CMU at east wall 48 inches AFF. Room 104 patch gap between wall and floor on north wall, 16 linear feet | Price is for patching wall and repainting over patched area | SF
THORPE HALL | TH | ARCH | 2377 | Conveying Systems | Elevators & Lifts | cylinder replacement | 2 | 1 | ea | 0 | 0 | 0 | 0 | Unknown | 30 | 30 | Otis recommendation for 2016. Refer to May 1, 2013 scope letter. |  | SF | 654129 | 2014-04-24 | 153825 | replaced cylinder&casing
THORPE HALL | TH | ARCH | 2378 | Conveying Systems | Elevators & Lifts | modernization | 3 | 1 | ea | 64347.7957 | 85582.5683 | 0 | 0 | Unknown | 30 | 30 | Otis recommendation for 2022. Refer to May 1, 2013 scope letter. |  | SF
THORPE HALL | TH | ADAC | 2379 | Barrier Free Compliance | Toilet Rooms | Refer to comments | 3 | 3720 | sf | 470768.4733 | 626122.0695 | 0 | 0 | 1962 | 50 | 2012 |  | Price is for renovating suite bathrooms and first floor public bathrooms to meet ADA codes. | SF
THORPE HALL | TH | EH&S | 2380 | Evnironmental Health & Safety | Asbestos abatement | allowance | 3 |  |  | 53623.1631 | 71318.8069 | 0 | 0 | Unknown |  | 0 | allowance for elevator work and toilet room renovation |  | SF
THORPE HALL | TH | MECH | 2381 | Ventilation/Terminal Units | AHU/No Cool/Steam Heat | AHU-1/Basement Mech. Rm. | 3 | 6000 | cfm | 75930.3989 | 100987.4306 | 0 | 0 | 1962 | 30 | 1992 | Replace reaching end of useful life | Price is for removing existing AHU and replacing it with a new 6,000 CFM unit and reconnecting to existing mains | SF
THORPE HALL | TH | MECH | 2382 | Heating Water System | Insulation | Entire system | 3 | 74842 | sf | 71034.6041 | 94476.5061 | 0 | 0 | 1962 |  | 1962 | Good condition, reported to be some ACM |  | SF
THORPE HALL | TH | MECH | 2383 | Steam System | Piping | Entire system | 3 | 74842 | sf | 269932.5682 | 359010.2942 | 0 | 0 | 1962 | 50 | 2012 | Replace condensate piping, failures observed |  | SF
THORPE HALL | TH | MECH | 2384 | Building Management | HVAC Control | Pneumatic | 3 | 74842 | sf | 378851.937 | 503873.2693 | 0 | 0 | 1962 | 25 | 1987 | Replace with DDC | Price is for replacing existing pneumatic controls with new DDC controls | SF
THORPE HALL | TH | MECH | 2385 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rm. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | unknown | 10 | 10 | Replace entire duplex unit as precautionary measure | Price is for replacing 1 existing sump pump with a new one and reconnect to existing piping | SF
THORPE HALL | TH | MECH | 2386 | Domestic cold water system | Piping | Entire building | 3 | 74842 | sf | 269932.5682 | 359010.2942 | 0 | 0 | 1962 | 40 | 2002 | Good condition, no reported problems. Reported galvanized/copper mix |  | SF
THORPE HALL | TH | MECH | 2387 | Domestic hot water system | Piping | Entire building | 3 | 74842 | sf | 269932.5682 | 359010.2942 | 0 | 0 | 1962 | 40 | 2002 | Good condition, no reported problems. Reported galvanized/copper mix |  | SF
THORPE HALL | TH | MECH | 2388 | Fire protection system | Piping | Control Valve | 3 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 1962 | 40 | 2002 | Replace control valve located in tunnel | Price if replacing 1 valve located in the buildings tunnel | SF
THORPE HALL | TH | EH&S | 2389 | Environmental Health & Safety | Asbestos abatement | allowance for mech items | 3 | 74842 | sf | 378852.1944 | 503873.4186 | 0 | 0 | 1962 |  | 1962 |  |  | SF
THORPE HALL | TH | ELEC | 2390 | Distribution | Main Dist. Panel | Bsmnt Vault | 1 | 1 | ea | 0 | 0 | 0 | 0 | 1962 | 50 | 2012 | 1200A, 120/240, (12) 125A/2P CB's | Price is for replacing 1 existing 1200A main Distribution Panel with a new one and reconnecting to existing feeds | SF | 654076 | 2014-08-01 | 3021847.86 | Part of South Quad Improvements included FCA project #'s 2373,2374,2390,2391,2392,2228,2229,1934,1935,1936,2257
THORPE HALL | TH | ELEC | 2391 | Distribution | Panelboards | Varies | 1 | 16 | Total | 0 | 0 | 0 | 0 | 1962 | 50 | 2012 | Replace with 125A Panelboard | Price is for replacing 16 existing distribution panels and reconnect to existing feeds | SF | 654076 | 2014-08-01 | 3021847.86 | Part of South Quad Improvements included FCA project #'s 2373,2374,2390,2391,2392,2228,2229,1934,1935,1936,2257
THORPE HALL | TH | LSAF | 2392 | Life Safety | Fire Alarm |  | 1 | 74842 | sf | 0 | 0 | 0 | 0 | Unknown | 40 | 40 | Complete building upgrade | Price is for upgrading the building fire alarm system. | SF | 654076 | 2014-08-01 | 3021847.86 | Part of South Quad Improvements included FCA project #'s 2373,2374,2390,2391,2392,2228,2229,1934,1935,1936,2257
THORPE HALL | TH | LSAF | 2393 | Life Safety | Area of Refuge |  | 0 |  |  | 0 | 0 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | SF |  |  |  | Building fully sprinkled not required
TROUTMAN HALL | TM | ARCH | 2394 | Envelope | Exterior Walls | Brick cracking | 3 | 7065 | sf | 223520.1118 | 297281.7487 | 0 | 0 | 1969 | 100 | 2069 | Areas of brick cracked by movement and mortar joints need to be repaired, approximately 25% of building | Price is for removing damaged brick and replacing it | SF
TROUTMAN HALL | TM | ARCH | 2395 | Envelope | Exterior Walls | Mortar joints in brick | 3 | 32570 | sf | 647124.332 | 860675.3616 | 0 | 0 | 1969 |  | 1969 | Mortar joints should be tuckpointed (55% of joints) and the systems sealed (100% sealed) | price is for removing existing mortar and replacing it with new. Also includes sealing the existing brick | SF
TROUTMAN HALL | TM | ARCH | 2396 | Envelope | Exterior Walls | Re-caulk all joints | 3 | 32570 | sf | 103043.8789 | 137048.3589 | 0 | 0 | 1969 |  | 1969 | Remove of backer rod and sealant and replace, 100% of caulk joints | Price is for removing old caulk and replacing it with new caulk | SF
TROUTMAN HALL | TM | ARCH | 2397 | Envelope | Exterior Walls | Exposed concrete columns | 3 | 15 | ea | 6264.2579 | 8331.463 | 0 | 0 | 1969 |  | 1969 | Repair concrete columns, area 36" high x 18" wide 2" deep concrete patch in 15 locations |  | SF
TROUTMAN HALL | TM | ARCH | 2398 | Envelope | Windows |  | 4 | 4280 | sf | 297900.2651 | 396207.3526 | 0 | 0 | 1969 | 30 | 1999 | Replacement of all original windows is recommended | Price is for removing old windows and replacing them with new aluminum framed windows. Also includes new caulk around the joints and minor finish patch around new unit. | SF
TROUTMAN HALL | TM | ARCH | 2399 | Interior Structure | Floor Finishes | General finishes | 3 | 61000 | sf | 424577.4806 | 564688.0492 | 0 | 0 | 1969 | 15 | 1984 | Flooring should be replaced | Price is for removing old flooring and replacing it with VCT or Carpet | SF
TROUTMAN HALL | TM | EH&S | 2400 | Environmental Health & Safety | Asbestos abatement | Allowance for flooring | 3 | 61000 | sf | 231587.7167 | 308011.6632 | 0 | 0 | 1969 |  | 1969 |  |  | SF
TROUTMAN HALL | TM | ARCH | 2401 | Conveying Systems | Elevators & Lifts | modernization | 3 | 2 | ea | 390376.6272 | 519200.9142 | 0 | 0 | 1969 | 30 | 1999 | Otis recommends this work for 2019 per letter dated May 1, 2013. | Price is for replacing 2 elevators | SF
TROUTMAN HALL | TM | ADAC | 2402 | Barrier Free Compliance | Doors & Hardware |  | 3 | 232 | ea | 146798.7712 | 195242.3658 | 0 | 0 | Unknown |  | 0 | Replacement is required to comply with current codes | Price is for replacing existing hardware for ADA compliant hardware | SF
TROUTMAN HALL | TM | ADAC | 2403 | Barrier Free Compliance | Toilet Rooms |  | 3 | 5040 | sf | 637815.3509 | 848294.4167 | 0 | 0 | Unknown |  | 0 | Design and construction is necessary to comply with current codes | Price is for renovation of bathroom to meet ADA requirements | SF
TROUTMAN HALL | TM | MECH | 2404 | Ventilation/Terminal Units | Terminal units/Unit Ventilator | UV, Elevator Lobby Area | 3 | 4 | ea | 136674.7181 | 181777.375 | 0 | 0 | 1969 | 20 | 1989 | Replace nearing end of useful life, alternately replace the 4 units with a single air handler. |  | SF
TROUTMAN HALL | TM | MECH | 2405 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 61000 | sf | 231587.7167 | 308011.6632 | 0 | 0 | 1969 | 40 | 2009 | Replace all drainage piping |  | SF
TROUTMAN HALL | TM | EH&S | 2406 | Environmental Health & Safety | Asbestos Abatement | Allowance | 3 | 104192 | sf | 527422.675 | 701472.1577 | 0 | 0 | Unknown |  | 0 |  |  | SF
TROUTMAN HALL | TM | ELEC | 2407 | Service | Abandoned Primary Switch | Basement | 5 | 1 | ea | 6327.5332 | 8415.6192 | 0 | 0 | 1969 |  | 1969 |  | Price is for removing abandoned unit | SF
TROUTMAN HALL | TM | ELEC | 2408 | Service | Abandoned Transformer | Basement | 5 | 1 | ea | 10124.0532 | 13464.9907 | 0 | 0 | 1969 |  | 1969 |  | Price is for removing abandoned unit | SF
TROUTMAN HALL | TM | ELEC | 2409 | Distribution | Main Panelboard 120/240V | Carey Dining Basement | 5 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1969 | 40 | 2009 |  |  | SF
TROUTMAN HALL | TM | ELEC | 2410 | Distribution | Floor Panels, Dorm | Ground through 8th | 4 | 9 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1969 | 40 | 2009 |  |  | SF
TROUTMAN HALL | TM | ELEC | 2411 | Distribution | Floor Panels, Kitchenette | Ground through 8th | 4 | 9 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1969 | 40 | 2009 |  |  | SF
TROUTMAN HALL | TM | ELEC | 2412 | Branch Circuit Condition | Functional | Throughout | 3 | 61000 | sf | 200709.3545 | 266943.4415 | 0 | 0 | 1969 | 50 | 2019 |  | Price is for circuit rewiring | SF
TROUTMAN HALL | TM | COMM | 2413 | Communications/Security |  |  | 3 |  | sf | 0 | 0 | 0 | 0 | Unknown |  | 0 | Partial raceway system for cameras |  | SF
TROUTMAN HALL | TM | LSAF | 2414 | Life Safety | Fire Alarm | Sleeping Rooms | 5 | 61000 | sf | 385979.5278 | 513352.772 | 0 | 0 | Unknown | 40 | 40 | Consider adding horn/strobes in sleeping rooms | price is for adding a fire alarm system in sleeping areas | SF
TROUTMAN HALL | TM | LSAF | 2415 | Life Safety | Area of Refuge | Alowance | 5 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 |  |  | SF
TROUTMAN HALL | TM | LSAF | 2416 | Life Safety | Emergency Lighting | Distributed Battery | 3 | 20 | ea | 12655.0665 | 16831.2384 | 0 | 0 | Unknown |  | 0 | Consider re-use of 1/2 Corridor lighting as egress using generator | price is for adding an emergency egress lighting to building | SF
TROUTMAN HALL | TM | SUST | 2417 | Energy/Sustainability | Occupancy sensors | Throughout | 3 | 61000 | sf | 77195.9056 | 102670.5544 | 0 | 0 | Unknown |  | 0 | Consider lighting controls retrofit for energy savings | Price is for adding sensors for dorm rooms | SF
TROUT HALL | TR | ARCH | 2418 | Envelope | Roof |  | 1 | 16600 | sf | 0 | 0 | 0 | 0 | 1959 | 30 | 1989 | Roofing should be scheduled for repair or replacement in 3 to 5 years |  | SF | 654044 | 2013-08-16 | 285533.2
TROUT HALL | TR | ARCH | 2419 | Envelope | Exterior Walls | Brick cracks | 3 | 550 | lf | 17400.7164 | 23142.9528 | 0 | 0 | 1959 | 100 | 2059 | Repair approximately 550 lineal feet of brick cracks | Price is for removing damaged bricks and tuckpointing in new bricks | SF
TROUT HALL | TR | ARCH | 2420 | Envelope | Windows |  | 3 | 5720 | sf | 398128.3917 | 529510.7609 | 0 | 0 | 1959 | 30 | 1989 | Replace all exterior windows as some do not lock |  | SF
TROUT HALL | TR | ARCH | 2421 | Envelope | Canopy limestone |  | 4 | 100 | sf | 10756.8065 | 14306.5527 | 0 | 0 | 1959 | 80 | 2039 | Replace 100 feet of limestone at main entry canopy | Price is for replacing Limestone at canopy | SF
TROUT HALL | TR | ARCH | 2422 | Envelope | Leak at success center |  | 4 | 1000 | sf | 44292.7327 | 58909.3345 | 0 | 0 | 1959 | 50 | 2009 | Remove curtainwall and install 22 feet of water stop |  | SF
TROUT HALL | TR | ARCH | 2423 | Interior Structure | Partitions/Walls |  | 3 | 500 | lf | 15818.8331 | 21039.048 | 0 | 0 | 1959 | 40 | 1999 | Repair approximately 500 lineal feet if interior cracks | Price is for repairing 500 lnft of cracks | SF
TROUT HALL | TR | ARCH | 2424 | Environmental Health & Safety | Allowance |  | 3 |  |  | 32173.8978 | 42791.2841 | 0 | 0 | Unknown |  | 0 | allowance for toilet room finish replacements, and misc finish replacements throughout |  | SF
TROUT HALL | TR | ADAC | 2425 | Barrier Free Compliance | Building Access |  | 3 | 3 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown |  | 0 | Should be updated when building improvements are made | Price is for adding an automatic openers at 3 entrances | SF
TROUT HALL | TR | ADAC | 2426 | Barrier Free Compliance | Toilet Rooms |  | 3 | 4400 | sf | 556822.9254 | 740574.4908 | 0 | 0 | Unknown |  | 0 | Should be updated when building improvements are made |  | SF
TROUT HALL | TR | MECH | 2427 | Ventilation/Terminal Units | Terminal units | Fin Tube HW/Entire Building | 3 | 200 | lf | 70868.3723 | 94254.9352 | 0 | 0 | 1959 | 25 | 1984 | Replace all reaching end of useful life failures reported |  | SF
TROUT HALL | TR | MECH | 2428 | Ventilation/Terminal Units | Terminal units | HW Cabinet Heater/Main Entrance | 3 | 4 | ea | 22779.1197 | 30296.2292 | 0 | 0 | 1959 | 20 | 1979 | Replace all reaching end of useful life failures reported |  | SF
TROUT HALL | TR | MECH | 2429 | Ventilation/Terminal Units | Terminal units | HW Convectors/Stairs, Corridors, Resident Rms. | 3 | 190 | ea | 1082008.1846 | 1439070.8856 | 0 | 0 | 1959 | 25 | 1984 | Replace all reaching end of useful life failures reported |  | SF
TROUT HALL | TR | MECH | 2430 | Heating Water System | Pumps | System/Basement Mech. Rm. | 3 | 3 | ea | 75930.3989 | 100987.4306 | 0 | 0 | 1959 | 20 | 1979 | Replace reaching end of useful life |  | SF
TROUT HALL | TR | MECH | 2431 | Heating Water System | Insulation | Entire system | 3 | 65861 | sf | 100016.8513 | 133022.9807 | 0 | 0 | 1959 |  | 1959 | Replace reaching end of useful life. Reported ACM |  | SF
TROUT HALL | TR | MECH | 2432 | Steam System | Piping | Entire system | 3 | 65861 | sf | 237540.9603 | 315928.3725 | 0 | 0 | 1959 | 50 | 2009 | Replace reaching end of useful life reported failures |  | SF
TROUT HALL | TR | MECH | 2433 | Storm/Sanitary sewer system | Piping | Entire building | 3 | 65861 | sf | 237540.9603 | 315928.3725 | 0 | 0 | 1959 | 40 | 1999 | Replace all, reaching end of useful life failures reported |  | SF
TROUT HALL | TR | MECH | 2434 | Domestic hot water system | Heater/Steam | Entire building/Basement Mech. Rm. | 3 | 1 | ea | 37965.1995 | 50493.7153 | 0 | 0 | 1986 | 24 | 2010 | Replace reaching end of useful life |  | SF
TROUT HALL | TR | EH&S | 2435 | Environmental Health & Safety | Asbestos abatement | allowance for mech items | 3 | 65861 | sf | 333390.2194 | 443408.863 | 0 | 0 | 1959 |  | 1959 |  |  | SF
TROUT HALL | TR | ELEC | 2436 | Distribution | Main Dist. Panel |  | 5 | 1 | ea | 60744.3191 | 80789.9445 | 0 | 0 | 1961 | 50 | 2011 | 1200A, 120/240, (16) 125A/2P CB's |  | SF
TROUT HALL | TR | ELEC | 2437 | Distribution | Panelboards | Bsmnt Vault | 5 | 16 | Total | 151860.7978 | 201974.8611 | 0 | 0 | 1961 | 50 | 2011 | Replace with 125A Panelboard |  | SF
TROUT HALL | TR | LSAF | 2438 | Life Safety | Fire Alarm |  | 5 | 65861 | sf | 416737.6669 | 554261.097 | 0 | 0 | Unknown | 40 | 40 | Complete building upgrade | Capital Improvement? | SF
TROUT HALL | TR | LSAF | 2439 | Life Safety | Area of Refuge |  | 5 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | SF
WHEELER HALL | WH | ARCH | 2440 | Envelope | Windows |  | 4 | 5350 | sf | 372375.3314 | 495259.1907 | 0 | 0 | 1970 | 30 | 2000 | Replace all exterior windows |  | SF
WHEELER HALL | WH | ARCH | 2441 | Conveying Systems | Elevators & Llifts |  | 3 | 1 | ea | 390376.6272 | 519200.9142 | 0 | 0 | 1970 | 30 | 2000 | Otis recommends modernization for 2020. |  | SF
WHEELER HALL | WH | EH&S | 2442 | Environmental Health & Safety | Asbestos abatement | allowance | 3 |  |  | 53623.1631 | 71318.8069 | 0 | 0 | Unknown |  | 0 | related to elevator work |  | SF
WHEELER HALL | WH | MECH | 2443 | Ventilation/Terminal Units | Terminal units/Unit Ventilator | UV, Elevator Lobby Area | 3 | 4 | ea | 136674.7181 | 181777.375 | 0 | 0 | 1970 | 20 | 1990 | Replace nearing end of useful life, alternately replace the 4 units with a single air handler. |  | SF
WHEELER HALL | WH | ELEC | 2444 | Distribution | DLP-1 | Bsmnt Vault - 600A | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 50 | 2020 | (18) 2P BRANCHES |  | SF
WHEELER HALL | WH | ELEC | 2445 | Distribution | LPBA | Bsmnt Vault | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 50 | 2020 | Replace with 125A Panelboard |  | SF
WHEELER HALL | WH | ELEC | 2446 | Distribution | LPBB | Bsmnt Vault | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 50 | 2020 | Replace with 125A Panelboard |  | SF
WHEELER HALL | WH | ELEC | 2447 | Distribution | LPBC | Bsmnt Vault | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 50 | 2020 | Replace with 125A Panelboard |  | SF
WHEELER HALL | WH | ELEC | 2448 | Distribution | LPX-1 | Bsmnt Vault | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 50 | 2020 | Replace with 125A Panelboard |  | SF
WHEELER HALL | WH | ELEC | 2449 | Distribution | 30A - 2P CONTACTOR | Bsmnt Vault | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 50 | 2020 | Replace |  | SF
WHEELER HALL | WH | ELEC | 2450 | Corridor Panelboards | (6) at 125A | Corridors | 4 | 6 | ea | 56947.7992 | 75740.5729 | 0 | 0 | 1970 | 50 | 2020 | Replace with 125A Panelboard |  | SF
WHEELER HALL | WH | ELEC | 2451 | Corridor Panelboards | (1) at 150A | Corridors | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | 1970 | 50 | 2020 | Replace with a 150A Panelboard |  | SF
WHEELER HALL | WH | ELEC | 2452 | Kitchen Power Panel | (1) 125A |  | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | Unknown |  | 0 | (26) 3P Branches |  | SF
WHEELER HALL | WH | ELEC | 2453 | Motor Control Center | (1) 125A |  | 4 | 1 | ea | 9491.2999 | 12623.4288 | 0 | 0 | Unknown |  | 0 | (26) 3P Branches |  | SF
WHEELER HALL | WH | LSAF | 2454 | Life Safety | Emergency Lighting |  | 3 | 30 | sf | 18982.5997 | 25246.8576 | 0 | 0 | Unknown |  | 0 | EBU's, not fully code compliant |  | SF
WHEELER HALL | WH | LSAF | 2455 | Life Safety | Add Life Safety Generator |  | 3 | 71117 | sf | 63275.3324 | 84156.1921 | 0 | 0 | Unknown |  | 0 | Assume 30 kW, 200A ATS, 3 Panelboards |  | SF
WOLDT HALL | WO | ARCH | 2456 | Exterior Structure | Windows |  | 3 | 7110 | sf | 494876.375 | 658185.5787 | 0 | 0 | 1964 | 30 | 1994 |  |  | SF
WOLDT HALL | WO | ARCH | 2457 | Conveying Systems | Elevators & Llifts | cylinder replacement | 1 | 2 | ea | 0 | 0 | 0 | 0 | 1964 |  | 1964 | Otis recommends this work for 2014. Refer to May 1, 2013 Otis Elevator letter. |  | SF | 654348 | 2015-07-01 | 71000
WOLDT HALL | WO | ARCH | 2458 | Conveying Systems | Elevators & Llifts | modernization | 3 | 2 | ea | 128695.5914 | 171165.1366 | 0 | 0 | 1964 |  | 1964 | Otis recommends this work for 2017. Refer to May 1, 2013 Otis Elevator letter. |  | SF
WOLDT HALL | WO | ADAC | 2459 | Barrier Free Compliance | Building Access |  | 3 | 3 | ea | 22779.1197 | 30296.2292 | 0 | 0 | 1964 |  | 1964 | Access for wheel chairs is through another building | Budget is for adding 2 automatic openers to entry doors | SF
WOLDT HALL | WO | ADAC | 2460 | Barrier Free Compliance | Toilet Rooms |  | 3 | 125 | sf | 15818.8331 | 21039.048 | 0 | 0 | 1964 |  | 1964 | Public rest rooms do not meet current codes | Area was taken from resident hall floor plan from the rooms marked T in the corridor. | SF
WOLDT HALL | WO | MECH | 2461 | Building Management | HVAC Control | Pneumatic | 3 | 64820 | sf | 328120.5639 | 436400.3499 | 0 | 0 | 1964 | 25 | 1989 | Replace with DDC with future renovation |  | SF
WOLDT HALL | WO | MECH | 2462 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rm. & transformer vault | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | Unknown | 10 | 10 | Replace as a precautionary measure |  | SF
WOLDT HALL | WO | MECH | 2463 | Domestic hot water system | Anti-scald mixing valve |  | 3 | 2 | ea | 12655.0665 | 16831.2384 | 0 | 0 | Unknown |  | 0 | It is recommended that anti-scald mixing valve(s) be installed on the domestic hot water system. |  | SF
WOLDT HALL | WO | ELEC | 2464 | Distribution | 120/240 volt panel,800 amp main breaker | Basement | 3 | 1 | ea | 40496.2128 | 53859.963 | 0 | 0 | 1972 | 40 | 2012 | Panel is corroded |  | SF
WOLDT HALL | WO | ELEC | 2465 | Branch Circuit Condition | ITE circuit breaker panels | Corridors | 4 | 11 | ea | 104404.2985 | 138857.717 | 0 | 0 | 1964 | 40 | 2004 | needs upgrade |  | SF
WOLDT HALL | WO | ELEC | 2466 | Branch Circuit Condition | circuits to rooms | dorm rooms + laundry rooms | 4 | 64820 | sf | 213278.3665 | 283660.2275 | 0 | 0 | 1964 | 40 | 2004 | needs upgrade |  | SF
WOLDT HALL | WO | SUST | 2467 | Lighting | 2x4 flourescent troffers | office | 3 | 6 | ea | 2657.564 | 3534.5601 | 0 | 0 | Unknown | 20 | 20 | upgrade for energy savings |  | SF
WOLDT HALL | WO | SUST | 2468 | Lighting | 4 foot flourescent wraparound flourescent fixtures | room 131 | 3 | 6 | ea | 2657.564 | 3534.5601 | 0 | 0 | Unknown | 20 | 20 | upgrade for energy savings |  | SF
WOLDT HALL | WO | SUST | 2469 | Lighting | 4 foot vandal resistant flourescent fixtures | Corridors | 3 | 160 | ea | 70868.3723 | 94254.9352 | 0 | 0 | Unknown | 20 | 20 | upgrade for energy savings |  | SF
WOLDT HALL | WO | SUST | 2470 | Lighting controls | Lutron model XPS8120FT | Lobby | 3 | 64820 | sf | 82030.141 | 109100.0875 | 0 | 0 | Unknown |  | 0 |  |  | SF
WOLDT HALL | WO | LSAF | 2471 | Life Safety | Fire Alarm - Simplex 4100U | Wolt Dining | 3 | 96 | ea | 60744.3191 | 80789.9445 | 0 | 0 | Unknown | 40 | 40 | No horn/strobes in residence rooms |  | SF
WOLDT HALL | WO | LSAF | 2472 | Life Safety | Wall mounted battery Egress lighting | Corridors | 3 | 88 | ea | 55682.2925 | 74057.4491 | 0 | 0 | Unknown |  | 0 | Should be upgraded with renovation |  | SF
WOLDT HALL | WO | LSAF | 2473 | Life Safety | Area of Refuge | Allowance | 3 |  |  | 42898.5305 | 57055.0455 | 0 | 0 | Unknown |  | 0 | per S. Esch |  | SF
WOLDT DINING | WF | MECH | 2474 | Storm/Sanitary sewer system | Sump pumps | Basement Mech. Rm. | 3 | 1 | ea | 22779.1197 | 30296.2292 | 0 | 0 | unknown | 10 | 10 | Replace as a precautionary measure |  | SF
ROSE RYAN SAC | RO | ARCH |  | Floor Finishes | Wood |  | 3 | 97210 | sf | 309119.6 | 309119.6 | 0 | 0 |  |  | 0 | Need to plan $60,000 everyother year for screen and recoat for the next 10 years | $300,000 (See A/E comment) CMU added to list Feb. 2014 |  | 684481 | 7.29.14 | 5027.73 | McGuirk Arena only - 16,700 sf
Column1
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## PIVOT
Values
Row Labels | Sum of Construction Cost (18% GC/CA) | Sum of Project Cost (33% Owner soft costs)
AC | 270051.5258 | 359168.5293
AN | 643643.0091 | 856045.202
BE | 2216549.9097 | 2948007.5726
BF | 1230757.7237 | 1636905.1235
BH | 967424.7083 | 1286674.8621
BN | 2876132.0822 | 3825253.578
BR | 2408950.4623 | 3203904.1148
BT | 1845960.3798 | 2455127.3051
CA | 4878190.0903 | 6487992.8201
CE | 195900.4292 | 260547.5709
CF | 2846061.1776 | 3785261.3662
CL | 5501759.8045 | 7317340.8938
CO | 2607605.0844 | 3468114.7622
CP | 1269362.1541 | 1688251.665
CS | 736173.0604 | 979110.1667
EA | 131612.6915 | 175044.8796
ED | 0 | 0
EM | 3830656.9879 | 5094773.7939
FB | 197165.9359 | 262230.6947
FI | 8434019.3569 | 11207912.2346
FO | 1753571.3805 | 2332249.9361
GR | 3335811.8806 | 4436629.8012
HE | 5749016.3703 | 7646191.7725
HP | 1518.608 | 2019.7486
IT | 160823.7487 | 213895.5857
KE | 1786399.6954 | 2375911.5949
KS | 1180776.6887 | 1570432.996
KU | 240446.2633 | 319793.5301
L1 | 61883.2751 | 82304.7559
LA | 6014222.7838 | 7998916.3024
ME | 1655654.3259 | 2202020.2581
MF | 1952679.4401 | 2597063.6553
MO | 1874354.5524 | 2492891.5547
MP | 158701.5048 | 169001.2328
MU | 37256.5157 | 49551.1659
NA | 841137.9767 | 1118713.5089
NW | 3214258.1921 | 4274963.3955
PA | 1470379.0911 | 1955603.7621
PB | 869677.6182 | 1156671.2323
PE | 7699062.3372 | 10239752.9084
PH | 1320237.2802 | 1755061.3657
PM | 31004.9129 | 41236.5341
PO | 3377983.1148 | 4492717.5426
RB | 4608061.8415 | 6128722.2492
RF | 2974765.2629 | 3925388.7763
RN | 2128225.6963 | 2830540.1761
RO | 3636677.5835 | 4658189.5832
RW | 3802007.2526 | 5056669.646
S1 | 0 | 0
SA | 5288485.0736 | 7033685.1479
SC | 9506389.7664 | 12643498.3894
SF | 12655.0665 | 16831.2384
SL | 1685710.0665 | 2241994.3884
SM | 1676508.3531 | 2229755.9381
SO | 121615.1889 | 161748.2013
ST | 3548189.5764 | 4719092.1366
SW | 2124110.0542 | 2825067.7556
TH | 2703979.5716 | 3596293.4416
TM | 4826005.5723 | 6418587.4112
TR | 3968455.004 | 5278043.3857
TS | 314197.4597 | 417882.6214
UA | 393811.1157 | 523768.7839
UC | 7898735.6782 | 10505318.452
VS | 52834.9026 | 70270.4204
WA | 5256898.7998 | 6991675.4038
WE | 909046.3075 | 1208960.8278
WF | 22779.1197 | 30296.2292
WH | 1177677.2699 | 1566310.7689
WI | 3494114.8634 | 4647172.7683
WO | 1701442.3303 | 2262918.2993
Grand Total | 161708212.9067 | 214809943.7151

## Instructions
Instructions for Annual Archiving and New Fiscal Year Set Up
Archive Current Year
PIVOT Tab:
Select "data" and "refresh all" before saving.
Save file to CMU's archive folder location --save file with current year name.
New Fiscal Year Set Up
Escalation Factor Tab:
Update/confirm factor for current year in cell A2. This cell is tied to "FCA Summary Tab" and "FCA Bldg Detail Tab".
Log prior year escalation factor shown below in same tab.
FCA Bldg Detail Tab:
Update Construction Cost (18%) and Project Cost (33%):
Clear all Filters.
Copy Construction Cost Esc (Column M) and Project Cost Escalation (Column N), rows 2 through the end of table. "Paste special values only" into Construction Cost (Column K ) and Project Cost (Column L) .
Construction Cost Esc(Column M) and Project Cost Escalation (Column N) will populate based upon the new values.
Note: Construction Cost (Column K ) and Project Cost (Column L) both need to remain as values. Construction Cost Esc(Column M) and Project Cost Escalation (Column N) will calculate based upon those values.
Construction Cost Esc(Column M) and Project Cost Escalation (Column N) indicate 2.38% inflation factor. You may wish to revise the heading, if it changes.
The formula for escalation is tied to Escalation Factor Tab - cell A2 in the escalation tab and will update the factor in Construction Cost Esc(Column M) and Project Cost Escalation (Column N) if changed.
FCA Summary Tab:
Update CostGSF (Column E):
Copy values on rows 2 through end of table from CostGSFEsc (Column I) and "paste special values only " into CostGSF (Column E).
This step will give you current year escalated cost per GSF, and automatically calculate ReplacementValueExclContents (Column F) and CostGSFEsc (Column I).
DMCostEST (Column G) will automatically calculate from the PIVOT table data when refreshed. FCI (Column H) will automatically calculate.
The formula for escalation is tied to Escalation Factor Tab - cell A2 in the escalation tab and will update the factor in CostGSFESc (Column I) if changed.

## Condition Rating Code
CMU FCA Spreadsheet CodeKey
Facilities Condition Assessments - Opinion of Probable Cost for Deferred Maintenance
CMU 2013 Campus Master Plan
Deferred Maintenance is the repair or replacement of an existing building item or system. This model assumes that item costs represent a one-for-one replacement
for that stand alone item/system. For project planning purposes, most systems will likely require additional capital costs to meet newer code requirements
(example: increased ventilation). When combining projects and/or making functional changes to a building, if the project scope affects 50% or more of the building,
additional replacement systems will be required to meet current code standards. This may have a significant affect on the overall scope of the project/budget.
Functional changes to the building will require accessibility improvements budgeted at 20% of the cost to renovate that area. Refer to tabs for SF planning costs.
Key of Column Information
A | Building Name
B | Building Code
C | Category
ARCH: architecture/interior MECH: mechanical ELEC: electrical LSAF: life safety ADAC: barrier-free/ADA code EH&S: environmental health & safety SUST: sustainability/energy savings opportunities COMM: communications and IT
D | Item Identification Number
E | System 1 - Category/Classification/Function of Building System
F | System 2 - Component or Equipment Name. First choice is to use the drawing equipment Tag name. Should match tag used on-site survey forms for reference.
G | Describe the item, location, and or what it serves as needed for readers understanding . Refer to detail in narrative outline.
H | Equipment / System Condition Rating Score. Scale is 1 - 5. See Condition Rating Code below:
1 Excellent - Best of Class in efficiency, reliability and operating per design intent. No work anticipated due to recent construction or renovation.
2 Good - Operating per design intent, good working order. May require attention after 10 years. Due to age of system/facility, is not an excellent.
3 Average - Needing repair and/or opportunities exist for efficiency upgrade. Will require attention within 7-10 years. And/or accepted under prior code and substantial renovation may require conformance to current code.
4 Poor - Equipment soon to be nonfunctional; high risk of failure within 3-6 years.
5 Failure - Equipment nonfunctional and requires immediate attention within 1-2 years.
I | Equipment / system component unit quantity
J | Equipment / system component units for column F
K | Estimated repair/replacementconstruction cost in 2013 dollars. (Includes 18% Contractor GC and CA)
L | Estimated project cost. Construction cost plus a factor to include Owner's costs. (Ave 1.33 multiplier)
M | Construction Cost Escalated for one year - average based upon historical data for the region over the last 30 years - refer to Escalation Factor Tab.
N | Project Cost Escalated for one year - average based upon historical data for the region over the last 30 years - refer to Escalation Factor Tab.
O | Approximate installation date.
P | Common/industry expected useful life
Q | Projected date for end-of-life replacement
R | A/E notes, comments or reference to narrative
S | Estimating team comments/qualifications and questions.
T | General Fund (GF) or Self-Liquidating Fund (SF)
U | ION number

## Project Cost Multiplier
CMU Project Cost Multiplier - | 1.33 * Construction Cost
1.033
Breakdown:
A/E Design Fee (Average) | 10%
Third Party Review Fee & Cx'g | 1.5%
Permits | 1.5%
PEP | 5%
Project Contingency | 15%
33%
Assume Included:
CMU Physical Plant or Shops Fee | 20000
Soil Borings as needed
Hazardous Material Abatement (CMU costs)

## Estimating Assumptions
2013 Facilities Condition Assessment - Deferred Maintenance Estimating Assumptions
Architectural
· Price of replacing windows includes the removal of the existing window, abatement of caulk, replacing it with a new standard fixed double pane window with a clear anodized aluminum frame, new sill, caulking around new window and repair and paint of adjacent surfaces.
· Replacing the flooring includes the removal of the existing flooring and adhesive and replacing it with new standard VCT or carpet as indicated on the sheet. No abatement, floor prep, floor leveling or crack repair costs were included at this time unless noted otherwise on the spreadsheet. Pricing for additional floor items are listed on a separate to be used on a case by case basis. (Refer to the end of this page for abatement costs.)
· Replacement of door hardware for classrooms, residence hall, and offices is for replacing existing door knobs with ADA compliant lever devices. Also includes a new intruder lockset for the door (similar to Anspach).
· Tuckpointing includes removing mortar to a depth of 1” and re-point new mortar for brick. Price is based on a composite unit price for various wall heights.
· Replacement of brick includes the cutting out of damaged brick and replacing it with a new brick re-pointed back into area.
· Painting costs includes minor wall/ceiling patch and repair from normal wear and tear as well as repainting of identified area.
· Acoustical Ceiling pricing includes the removal of the existing ceiling system, inclusive of hanger wire, tiles and grid, and replacing it with a standard 2 x 4 and 5/8” thick acoustical ceiling system.
· Elevator costs are for the complete replacement of the existing elevator unless noted as just the interior cab update. Elevator replacement includes new gearless hoisting machines along with controls, fixtures and wiring for elevator cab, steel work required as well as updated finishes in the cab. Price does not include drilling of the cylinder of the elevators. Price assumes reusing hoist way rails, counterweights, cab, sling, and platform of existing elevators.
· Replacement of aluminum entrance doors includes the removal of existing door and replacing it with a new aluminum framed door. (Similar to Anspach). Price does not include automatic openers listed on separate line items on the spreadsheet.
· Roof repair includes removal of the existing roof system down to roof decking and replacing it with a 3-ply reinforced built-up roof system based on a Tremco System. Price includes flashing at base/curb locations and roof penetrations, wood blocking, metal fascia, insulation and sealants.
· Bathroom ADA remodel costs are SF costs for demo and rework of existing bathroom space to comply with ADA requirements. Demo includes removal of all existing fixtures and toilet partitions and accessories, as well as wall, ceiling and floor finishes. Rework costs include new ADA compliant bathroom fixtures and partitions. New ceramic floor and wall tile and gypsum board ceiling for bathroom area. Price would also include new toilet accessories (mirrors, toilet paper dispenser, paper towel dispenser, grab bars). Price assumes that ADA compliant toilet will be able to fit into existing bathroom space. No demo and or remodeling were figured for any adjoining spaces outside of existing bathrooms.
· No moving costs are included in any of the prices unless specifically noted otherwise on the spreadsheet.
Electrical
· Panel pricing is for removing the old panel and replacing it with a new panel of equal size and capacity and reconnect to the existing feeds. Includes minor patch and repair to adjacent surfaces. A square foot multiplier will be added to the line item on a case-by-case basis to cover feeders, branch panels and circuiting. A square foot multiplier of $5.50/SF should be added for new feeders and circuit wiring.
· Price for light fixture replacement includes the removal of the old fixture and replacing it with a new fixture type indicated on the spreadsheet. Price assumes new fixture will fit in existing ceiling system. It is assumed new fixture will not require alteration to existing circuiting or service capacity.
· Emergency lighting is for adding battery wall pack lights in the amount indicated on the spreadsheet for each building.
· Lighting controls costs are calculated on a square foot basis for adding basic occupancy sensors to existing switching circuiting.
· All panel, fixture and outlet replacement is priced to re-use existing feeds and circuits unless noted otherwise on the spreadsheet. A square foot multiplier of $5.50/SF should be added for new feeders and circuit wiring.
· Fire Alarm pricing includes adding surface mounted smoke detectors, horn and strobe alarming devices and a new annunciater panel. Price does not include duct detectors or tying into existing mechanical equipment controls.
Mechanical
· Price for AHU is for removing the old unit and replacing it with a new unit with comparable capacity and to reconnecting to existing main ducts. Price includes electrical hook-up and new transition duct from the new unit to the existing mains. A square foot multiplier will be added to the line item on a case-by-case basis to cover system capacity increase and upgrades.
· Price for unit ventilators includes the removal of the old unit, replacing it with a new vertical unit and hooking up to existing piping. Price includes new duct from the unit to the space being served, electrical hook-up and tying the controls back into the BMS system. No architectural rework has been included. Refer to separate pricing sheet for architectural cost for project specific scope. A square foot multiplier will be added to the line item on a case-by-case basis to cover system upgrades.
· Pricing for terminal units is for removing the existing unit and replacing it with the same type of unit and reconnecting to existing piping and ductwork in place. A square foot multiplier will be added to the line item on a case-by-case basis to cover system upgrades.
· Piping replacement includes replacing the existing type of piping listed on the spreadsheet. Architectural demo and repair/replacement is listed as a separate multiplier on construction budget numbers based on specific known scope.
· Domestic water and sanitary piping replacement costs include adding a booster pump, removing and replacing of the water heater, replacement of all domestic water piping, replacement of faucets, urinals and toilets. Some ADA modifications were included typically to the first floor bathrooms including adding an ADA compliant bathroom stall, door openers and correct clearances.
· Controls pricing is for replacing existing pneumatic controls with new DDC control system based on the same number of control points and tying it into the main campus control system. Price also includes cable tray and J-Hooks for control wiring. A square foot multiplier will be added to the line item on a case-by-case basis when linked to new AHU scope.
· Sump pump pricing is for removing existing pumps and replacing them with a new duplex pump unit with an alarm.
Hazardous Material Abatement
$10/SF for interior ceiling and wall material.
$3/SF for interior flooring material.
$4/SF of total building area for mechanical item allowance.
$20/LF of pipe insulation.
Note: window replacement includes abatement of caulk.

## DM Unit Costs
CMU Deferred Maintenance Unit Costs
Description | Unit | Costs/SF
Remove and Replace Standard Acoustical Tile Ceiling | sf | 5.31
Remove and Replace Standard Carpet | sf | 6.49
Remove and Replace Standard VCT and base | sf | 5.605
Floor Leveling (Price is for area that requires leveling only) | sf | 3.54
Prep and Paint Wall | sf | 1.18
Removal and Disposal of ACM Floor Tile and Mastic | sf | 4.13
Remove and Dispose of Insulation Corner | ea | 59
Remove and Dispose of Pipe Insulation | lnft | 18.88
Clarifications
Costs are based on 2013 pricing. No escalation factor has been applied to costs
Pricing is for construction costs and contractor fee, bonds and GC's. No owner costs or AE fee is included in pricing.
Cabinet Heater (each)
|  |  |  | Material |  | 1350
|  |  |  | Labor |  | 1375
|  |  |  | Demo |  | 225
|  |  |  | Insulation |  | 350
|  |  |  | Temp Controls |  | 1200
4500
|  |  |  | 18% Contractor/AE Fee |  | 810
5310
Window Replacement (per SF) |  |  |  | Fin Tube Unit (per lnft)
Material |  | 30 |  | Material |  | 65
Installation |  | 6.5 |  | Labor |  | 120
Demo |  | 5.5 |  | Demo |  | 15
Sill |  | 6.5 |  | Insulation |  | 30
Wall Patch |  | 3.5 |  | Temp Controls |  | 50
Insulation |  | 1.25 |  |  |  | 280
Paint and Touch up |  | 1.75 |  | 18% Contractor/AE Fee |  | 50.4
|  | 55 |  |  |  | 330.4
18% Contractor/CA Fee |  | 9.9
|  | 64.9 |  | AHU Replacement (per CFM)
|  |  |  | Material |  | 4.05
|  |  |  | Labor |  | 2.25
Roof Replacement (per SF) |  |  |  | Demo |  | 0.36
New Roof |  | 20 |  | Duct |  | 1.2
Demo |  | 3 |  | Insulation |  | 0.64
|  | 23 |  | Temp Controls |  | 1.5
18% Contractor/AE Fee |  | 4.14 |  |  |  | 10
|  | 27.14 |  | 18% Contractor/AE Fee |  | 1.8
11.8
Bathroom Renovation
|  | Quantity | Unit | Unit Costs | Total
Demo |  | 1100 | sf | 8 | 8800
Gyp Board Ceiling |  | 700 | sf | 8.5 | 5950
Ceramic Wall Tile |  | 1250 | sf | 12 | 15000
Ceramic Floor Tile |  | 1100 | sf | 12 | 13200
Toilet Partitions |  | 11 | ea | 1000 | 11000
Toilet Accessories |  | 31 | ea | 100 | 3100
New Plumbing Fixtures |  | 20 | ea | 2600 | 52000
Constsruction Costs |  |  |  |  | 109050
18% Contractor/AE Fee |  |  |  |  | 19629
128679
Based on a 1100 SF Bathroom |  |  |  |  | 1100
Cost per SF |  |  |  |  | 116.9809
Costs are based on 2012-2013 dollars
18% mark up has been added to the total cost for contractor mark-up, GCs, bond costs, ect.
No owners costs or A/E fees have been included in these cost breakdowns

## MEP SF budget costs
Average College Building MEP Costs
College Classroom
| Low | Median | High
Mechanical | 41.55 | 54.44 | 71.76
Electrical | 12.98 | 20.1 | 27.6
College Science and Engineering Labs
| Low | Median | High
Mechanical | 65.97 | 72.45 | 113.85
Electrical | 24.43 | 35.19 | 53.13
College Residential Halls
| Low | Median | High
Mechanical | 42 | 44.1 | 68.66
Electrical | 10.42 | 15.87 | 21.74
Clarifications
*Prices are averages for New MEP systems for typical college building types. These prices reflect costs for new code compliant MEP systems NOT 1 for 1 replacement
*Prices are based on 2012-2013 costs. No escalation factor has been figured into the pricing
*Prices include 18% mark-up for CM fee and contingency.
*Prices include 20% mark-up for a renovation factor to cover associated work not identified.
*Prices are based on comparable project averages
Mechanical Pricing Includes
~ Pluming Fixtures
~Domestic Water Distribution
~Heating Supply System
~Cooling Generating System
Electrical Pricing Includes
~Electrical Service and Distribution including electrical service, panel boards and feeders
~Lighting and Branch Wiring including fluorescent fixtures, receptacles and switches

## Anspach MEP SF budget costs
Anspach Electrical Costs
Description | cost | cost/sf
Electrical Demo | 41455 | 0.40764
Light Fixtures | 508805 | 5.0032
Branch Lighting and Power | 264915 | 2.605
Fire Alarm | 180986 | 1.7797
Switch Gear & Panels | 191854 | 1.8866
Feeders | 295585 | 2.9066
Transformer | 170140 | 1.673
Generator | 94646 | 0.93069
Misc. Electrical (General Conditions, Temp Power, Bond) | 56275 | 0.55337
| 1804661 | 17.7458
Anspach Hall Mechanical Costs
Description | Cost | Cost/SF
HHW | 842550 | 8.2851
CHW | 500285 | 4.9195
Steam System | 239550 | 2.3556
Hydro Equipment | 77100 | 0.75815
AHU | 504000 | 4.956
Mech Insulation | 243950 | 2.3988
Sheet Metal | 911800 | 8.966
Temp Controls | 381750 | 3.7539
Fire Protection | 43750 | 0.43021
TAB | 132425 | 1.3022
Misc. (General Conditions, Demo, Cut/patch, Permits) | 243540 | 2.3948
BIM Modeling/Clash Detection | 128400 | 1.2626
| 4249100 | 41.7828
Clarifications
Based on 120,000 SF of building
Prices are for construction costs and include 18%GC/CA costs. No owner or AE fees have been included in the prices
Costs are from 2012-2013 pricing. No escalation has been figured into costs.

## Replacement Cost Assumptions
The estimated new construction cost values listed on the Facilities Assessment Summary were developed using a number of data sources.
We utilized our internal data base of historical costs for similar projects built or estimated by Clark Construction
We also have database software (D4 Cost) that has historical construction cost information on a national level
This data was reviewed for similar project costs as well. We also reviewed any existing building plans or documents that were available to us provided by CMU for each building.
Site visits by Clark personnel were also made to some of the buildings for photographs etc. Individual building assessment reports provided by FTCH were also utilized where applicable.
Using the data sources listed above, a parametric cost was developed for each building. This cost was individualized as much as possible based on building type, intended use and size.
In some cases ( i.e. Warriner Hall) the cost model assumed some historical replication as well.
This cost per square foot was then applied to the building gross square footage (provided on CMU document) for an estimated cost value of a similar new building.
The cost model also assumes the following:
• | Construction cost only plus CM soft costs.
• | No demolition or abatement costs of the existing buildings.
• | Replacement site to be prepared for new construction costs not included.
• | No FFE or contents replacement/moving costs included.
• | No A/E design fees or CMU Project Costs included.
The FCI ratio compares construction costs only: deferred maintenance construction cost/construction cost to replace building.

## Notes
Some ADAC projects (I.E.) toilet rooms, door hardware can be found under the ARCH category