## SR Emissions Summary
University of Massachusetts - Amherst Campus
2018 Massachusetts Source Registration Emissions Summary
Actual and Potential Emissions
|  | Emission Unit | Actual Emissions (ton/yr) | [7 empty] | Potential Emissions (ton/yr)
|  |  | SOX | PM | PM10 | NOX | CO | VOC | PM2.5 | NH3 | SOX | PM | PM10 | NOX | CO | VOC | PM2.5 | NH3
Central Heating Plant |  | CTG and duct burner - oil | 0.020886 | 0.050982 | 0.050982 | 0.24563 | 0.03401 | 0.00638 | 0.050982 | 0.010593 | 0.24394 | 0.65558 | 0.65558 | 3.1915 | 0.44189 | 0.64034 | 0.65558 | 0.13763
|  | CTG and duct burner - natural gas | 1.4315 | 24.3752 | 24.3752 | 5.0575 | 1.8122 | 0.31587 | 24.3752 | 0.42789 | 1.9 | 31.4 | 31.4 | 13.7 | 12.1 | 2.2 | 31.4 | 3
| 32 | Total CTG and duct burner | 1.4524 | 24.4262 | 24.4262 | 5.3031 | 1.8463 | 0.32225 | 24.4262 | 0.43849 | 1.9 | 31.4 | 31.4 | 13.7 | 12.1 | 2.2 | 31.4 | 3
| 34 | #200 Boiler-Oil | 0.011366 | 0.035692 | 0.035692 | 0.075455 | 3.5e-05 | 0.00071384 | 0.035692 | 0.00341 | 0.68995 | 2.2056 | 2.2056 | 2.3821 | 0.0021246 | 0.044113 | 2.2056 | 0.044113
| 34 | #200 Boiler-NG | 0.08516 | 1.4193 | 1.4193 | 0.72056 | 0.00197 | 0.22709 | 1.4193 | 0.025725 | 1.1055 | 20.6482 | 20.6482 | 10.3063 | 19.0434 | 2.8886 | 20.6482 | 0.71324
| 35 | #300 Boiler-Oil | 0.013791 | 0.034647 | 0.034647 | 0.14205 | 0.00016 | 0 | 0.034647 | 0.00269 | 0.62111 | 2.0512 | 2.0512 | 2.0512 | 0.02795 | 0 | 2.0512 | 0.51279
| 35 | #300 Boiler-NG | 0.051244 | 0.51244 | 0.51244 | 0.41332 | 0.001569 | 0.17081 | 0.51244 | 0.0093885 | 0.99724 | 18.6259 | 18.6259 | 9.2969 | 17.1783 | 2.6057 | 18.6259 | 0.64338
| 36 | #400 Boiler-Oil | 0.0075132 | 0.018875 | 0.018875 | 0.076385 | 0.0002185 | 0 | 0.018875 | 0.0016225 | 0.62111 | 2.0512 | 2.0512 | 2.0512 | 0.010256 | 0 | 2.0512 | 0.51279
| 36 | #400 Boiler-NG | 0.04915 | 0.4915 | 0.4915 | 0.39551 | 0.0036225 | 0.16383 | 0.4915 | 0.012539 | 0.99724 | 18.6259 | 18.6259 | 9.2969 | 17.1783 | 2.6057 | 18.6259 | 0.64338
| 37 | Black Start Emergency Generator | 0.0001855 | 0.0053 | 0.0053 | 0.17106 | 0.092088 | 0.010865 | 0.0053 | 0.00027825 | 0.002142 | 0.06 | 0.06 | 1.9365 | 1.0425 | 0.123 | 0.06 | 0.02876
|  | Total CHP Emissions | 1.6708 | 26.944 | 26.944 | 7.2975 | 1.9459 | 0.89557 | 26.944 | 0.49414 | 6.9343 | 95.668 | 95.668 | 51.0209 | 66.5828 | 10.4671 | 95.668 | 6.0984
| 20 | Tillson Sawmill
Small Boilers | 21 | Small Boilers-#2 Fuel Oil | 0.00093697 | 0.0087978 | 0.0047508 | 0.087978 | 0.021994 | 0.0014956 | 0.0036511 | 0.0035191 | 0.016367 | 0.15368 | 0.082988 | 1.5368 | 0.3842 | 0.026126 | 0.063778 | 0.061473
| 27 | Furcolo Hall Boiler #1 - Natural gas | 0.0010133 | 0.0032088 | 0.0032088 | 0.16888 | 0.14186 | 0.0092886 | 0.0032088 | 0.0054043 | 0.010789 | 0.034167 | 0.034167 | 1.7982 | 1.5105 | 0.098903 | 0.034167 | 0.057544
| 28 | Small Boilers - Natural gas | 0.0026617 | 0.0084287 | 0.0084287 | 0.44182 | 0.35942 | 0.024399 | 0.0084287 | 0.014196 | 0.016228 | 0.051388 | 0.051388 | 2.6959 | 2.2078 | 0.14876 | 0.051388 | 0.086548
Emergency Generators | 7 | Conte Emergency Generator - Group 1 | 0.0040833 | 0.004365 | 0.004365 | 0.061954 | 0.013376 | 0.0060546 | 0.004365 | 0.00029569 | 0.40833 | 0.4365 | 0.4365 | 6.1954 | 1.3376 | 0.60546 | 0.4365 | 0.029569
| 8 | Caterpillar Portable Emergency Generators - Group 2 | 0.00027222 | 0.000291 | 0.000291 | 0.0041303 | 0.00089176 | 0.00040364 | 0.000291 | 1.9713e-05 | 0.032667 | 0.03492 | 0.03492 | 0.49563 | 0.10701 | 0.048437 | 0.03492 | 0.0023655
| 9 | Caterpillar Emergency Generators - Group 3 | 0.028151 | 0.030092 | 0.030092 | 0.42711 | 0.092217 | 0.041741 | 0.030092 | 0.0020385 | 1.3365 | 1.4287 | 1.4287 | 20.2782 | 4.3783 | 1.9817 | 1.4287 | 0.096782
| 10 | Small Cummins Emergency Generators - Group 4 | 0.0089636 | 0.0095818 | 0.0095818 | 0.136 | 0.029364 | 0.013291 | 0.0095818 | 0.00064909 | 0.62679 | 0.67002 | 0.67002 | 9.51 | 2.0533 | 0.92938 | 0.67002 | 0.045388
| 16 | Kohler Emergency Generators - Group 5 | 0.024318 | 0.025995 | 0.025995 | 0.36896 | 0.079661 | 0.036057 | 0.025995 | 0.0017609 | 1.047 | 1.1192 | 1.1192 | 15.8859 | 3.4299 | 1.5525 | 1.1192 | 0.075819
| 17 | Small Onan Emergency Generators - Group 6 | 0.01174 | 0.012549 | 0.012549 | 0.17812 | 0.038457 | 0.017407 | 0.012549 | 0.00085011 | 0.81504 | 0.87125 | 0.87125 | 12.3661 | 2.6699 | 1.2085 | 0.87125 | 0.05902
| 19 | Lincoln Campus Center Parking Diesel Generator - Group 8 | 0.0057677 | 0.0061655 | 0.0061655 | 0.08751 | 0.018894 | 0.0085521 | 0.0061655 | 0.00041766 | 0.23071 | 0.24662 | 0.24662 | 3.5004 | 0.75577 | 0.34209 | 0.24662 | 0.016707
| 43 | Life Science Diesel Emergency Generator - Group 9 | 0.020703 | 0.02213 | 0.02213 | 0.31411 | 0.067819 | 0.030697 | 0.02213 | 0.0014992 | 1.0617 | 1.1349 | 1.1349 | 16.1081 | 3.4779 | 1.5742 | 1.1349 | 0.07688
| 18 | Natural Gas Emergency Generators - Group 7 | 3.8973e-05 | 0.0031178 | 0.00061707 | 0.12226 | 0.48884 | 0.011521 | 0.00061707 | 0.0011692 | 0.00075274 | 0.060219 | 0.011918 | 3.6794 | 8.2227 | 0.59442 | 0.011918 | 0.9
Storage Tanks | 11 | 20,000 gal Gasoline Storage Tank-Underground | [5 empty] | 0.37326 | [7 empty] | 0.456
| 38 & 40 | (2) 234,810 Gallon ULSD Storage Tank | [5 empty] | 0.050066 | [7 empty] | 0.25125
| 12 | (3) 10,000 gal Diesel Storage Tanks-underground | [5 empty] | 0.00032128 | [7 empty] | 0.002
| 14 | 2,500 gal Diesel Storage Tank-Underground | [5 empty] | 1.22e-06 | [7 empty] | 0
| 23 | (2) 550 gal Diesel Storage Tanks-AG | [5 empty] | 0.00020238 | [7 empty] | 0.001
| 22 | (2) 1,000 gal Lube Oil Storage Tanks-AG | [5 empty] | 2.0278e-05 | [7 empty] | 0
| 24 | 1,000 gal Transmission Fluid Tank-AG | [5 empty] | 1.0026e-05 | [7 empty] | 0
| 42 | 5,000 gal Diesel Storage Tank (UMPD) - UG | [5 empty] | 7.4418e-07 | [7 empty] | 0
| 25 | 5,000 gal Diesel Storage Tank (Life Sciences) - AG | [5 empty] | 7.4418e-07 | [7 empty] | 0
| 46 | LNG Tank (TK-01) | [5 empty] | 0
| 47 | LNG Tank (TK-02) | [5 empty] | 0
| 48 | LNG Tank (TK-03) | [5 empty] | 0
Other Sources | 41 | (2) Ammonium Hydroxide Tanks | [7 empty] | 0.084361 | [7 empty] | 0.41
| 44 | Space Heating - NG | 0.0036657 | 0.011608 | 0.011608 | 0.61094 | 0.51319 | 0.033602 | 0.011608 | 0.0029936 | 0.061235 | 0.19391 | 0.19391 | 10.2058 | 8.5729 | 0.56132 | 0.19391 | 0.050009
| 44 | Space Heating - propane | 2.3017e-05 | 0.0017705 | 0.0017705 | 0.11508 | 0.066394 | 0.0088525 | 0.0017705 | -- | 0.0028679 | 0.22061 | 0.22061 | 14.3394 | 8.2727 | 1.103 | 0.22061 | --
| 26 | Safety Kleen Cold Cleaning Degreasers | [5 empty] | 0.069292 | [7 empty] | 0.14591
| 25 | Maintenance Paint Booth |  | 0.00044979 | 0.00044979 |  |  | 0.018197 | 0.00044979 |  |  | 0.010825 | 0.010825 |  |  | 0.43794 | 0.010825
| 45 | LNG burners | 0.0097658 | 0.030925 | 0.030925 | 1.6276 | 1.3672 | 0.089519 | 0.030925 | 0.0079754 | 0.019136 | 0.060597 | 0.060597 | 3.1893 | 2.679 | 0.17541 | 0.060597 | 0.015628
|  | Total Emissions (tons/yr) | 1.7929 | 27.1235 | 27.1169 | 12.05 | 5.2455 | 1.7398 | 27.1158 | 0.62129 | 12.6204 | 102.3955 | 102.2765 | 172.8056 | 116.6425 | 22.7115 | 102.2573 | 8.0822

## Federal eGGRT Calcs
University of Massachusetts - Amherst Campus
2018 Federal Greenhouse Gas Reporting - eGGRT
Facility Emission Summary
[6 empty] | CO2 Emissions - Federal eGGRT |  |  |  | CH4 Emissions - Federal eGGRT |  |  |  | N2O Emissions - Federal eGGRT
Equipment Name | Emitting Activity | 2018 Fuel Use |  | 2018 Fuel Use |  | CO2 Emission Factor 40 CFR 98 Table C-1 |  | CO2 Emissions (kg) | CO2 Emissions (metric tons) | CH4 Emission Factor - 40 CFR 98 Table C-2 |  | CH4 Emissions (kg) | CH4 Emissions (metric tons) | N2O Emission Factor 40 CFR 98 Table C-2 |  | N2O Emissions (kg) | N2O Emissions (metric tons)
Boiler #200 | Boiler on NG | 275599.4 | kCF | 283867.382 | MMBTU | 53.06 | kg/MMbtu | 15062003.2889 | 15062.0033 | 0.001 | kg/MMbtu | 283.8674 | 0.28387 | 0.0001 | kg/MMbtu | 28.3867 | 0.028387
Boiler #200 | Boiler on Oil | 106272 | gal. | 14533.865 | MMBTU | 73.96 | kg/MMbtu | 1074924.6548 | 1074.9247 | 0.003 | kg/MMbtu | 43.6016 | 0.043602 | 0.0006 | kg/MMbtu | 8.7203 | 0.0087203
Boiler #300 | Boiler on NG | 165837.2 | kCF | 170812.316 | MMBTU | 53.06 | kg/MMbtu | 9063301.487 | 9063.3015 | 0.001 | kg/MMbtu | 170.8123 | 0.17081 | 0.0001 | kg/MMbtu | 17.0812 | 0.017081
Boiler #300 | Boiler on Oil | 128949 | gal. | 17635.1942 | MMBTU | 73.96 | kg/MMbtu | 1304298.9622 | 1304.299 | 0.003 | kg/MMbtu | 52.9056 | 0.052906 | 0.0006 | kg/MMbtu | 10.5811 | 0.010581
Boiler #400 | Boiler on NG | 159060.2 | kCF | 163832.006 | MMBTU | 53.06 | kg/MMbtu | 8692926.2384 | 8692.9262 | 0.001 | kg/MMbtu | 163.832 | 0.16383 | 0.0001 | kg/MMbtu | 16.3832 | 0.016383
Boiler #400 | Boiler on Oil | 70250 | gal. | 9607.4603 | MMBTU | 73.96 | kg/MMbtu | 710567.7601 | 710.5678 | 0.003 | kg/MMbtu | 28.8224 | 0.028822 | 0.0006 | kg/MMbtu | 5.7645 | 0.0057645
CTG-NG | CTG on NG | 955953 | kCF | 984631.59 | MMBTU | 53.06 | kg/MMbtu | 52244552.1654 | 52244.5522 | 0.001 | kg/MMbtu | 984.6316 | 0.98463 | 0.0001 | kg/MMbtu | 98.4632 | 0.098463
CTG-DSL | CTG on Oil | 121085 | gal. | 16559.7057 | MMBTU | 73.96 | kg/MMbtu | 1224755.8325 | 1224.7558 | 0.003 | kg/MMbtu | 49.6791 | 0.049679 | 0.0006 | kg/MMbtu | 9.9358 | 0.0099358
HRSG with Duct Burner | Duct Burner on NG | 303564.7 | kCF | 312671.641 | MMBTU | 53.06 | kg/MMbtu | 16590357.2715 | 16590.3573 | 0.001 | kg/MMbtu | 312.6716 | 0.31267 | 0.0001 | kg/MMbtu | 31.2672 | 0.031267
Small Boilers - NG (EU27&EU28) | Boiler on NG | 125807.7 | Therms | 12580.77 | MMBTU | 53.06 | kg/MMbtu | 667535.6562 | 667.5357 | 0.001 | kg/MMbtu | 12.5808 | 0.012581 | 0.0001 | kg/MMbtu | 1.2581 | 0.0012581
Small Boilers - Oil | Boiler on Oil | 8797.8 | gal. | 1203.1959 | MMBTU | 73.96 | kg/MMBtu | 88988.3707 | 88.9884 | 0.003 | kg/MMbtu | 3.6096 | 0.0036096 | 0.0006 | kg/MMbtu | 0.72192 | 0.00072192
Space Heating-propane | Propane | 17705.1 | gal. | 1611.1641 | MMBTU | 61.71 | kg/MMBtu | 99424.9366 | 99.4249 | 0.003 | kg/MMbtu | 4.8335 | 0.0048335 | 0.0006 | kg/MMbtu | 0.9667 | 0.0009667
Space Heating-NG | Natural Gas | 125854.58 | Therms | 12585.458 | MMBTU | 53.06 | kg/MMbtu | 667784.4015 | 667.7844 | 0.001 | kg/MMbtu | 12.5855 | 0.012585 | 0.0001 | kg/MMbtu | 1.2585 | 0.0012585
Dining Commons | Natural Gas | 116053.1 | Therms | 11605.31 | MMBTU | 53.06 | kg/MMbtu | 615777.7486 | 615.7777 | 0.001 | kg/MMbtu | 11.6053 | 0.011605 | 0.0001 | kg/MMbtu | 1.1605 | 0.0011605
[8 empty] | Total (MT) | 108107.1988 |  |  |  | 2.136 |  |  |  | 0.23195
*Note: Small Boilers - NG are grouped for entry into eGGRT
2 eGGRT Emission Factors are based on the EPA GHG reporting requirements under 40 CFR 98 Subpart C and are contained in Tables C-1 and C-2. These default values vary in some cases from the CRIS emission factors. Greenhouse gas emissions reported in the eGGRT system are calculated using the Subpart C, Tables C-1 and C-2 default emission factors.
[8 empty] | CO2 equivalent factor | 1 |  |  |  | 25 |  |  |  | 298
[8 empty] | CO2e emissions (MT) | 108107.1988 |  |  |  | 53.401 |  |  |  | 69.1208
[8 empty] | Total CO2e Emissions |  | 108229.7205 | metric tons

## MA GHG Calcs
University of Massachusetts - Amherst Campus
2018 Massachusetts Greenhouse Gas Reporting
Facility Emission Summary
[7 empty] | CO2 Emissions |  |  |  | CH4 Emissions |  |  |  | N2O Emissions |  |  |  | e-CO2
Equipment Name | Emitting Activity | Fuel Type | 2018 Fuel Use |  | 2018 Fuel Use |  | CO2 Emission Factor |  | CO2 Emissions (lbs) | CO2 emissions (tons) | CH4 Emission Factor |  | Lb CH4 Emissions | CH4 emissions (tons) | N2O Emission Factor |  | lb N2O Emissions | N2O emissions (tons)
Boiler #200 | Boiler on NG | Nat. Gas | 275.5994 | MMCF | 283867.382 | MMBTU | 120000 | lb/MMCF | 33071928 | 16535.964 | 2.2708 | lb/MMCF | 625.8204 | 0.31291 | 0.22046 | lb/MMCF | 60.7592 | 0.03038 | 16536.3073
Boiler #200 | Boiler on Oil | #2 Oil | 106272 | gal. | 14533.865 | MMBTU | 22509.197 | lb/1000 gal | 2392097.3804 | 1196.0487 | 0.9039 | lb/1000 gal | 96.0587 | 0.048029 | 0.11 | lb/1000 gal | 11.6899 | 0.005845 | 1196.1026
Boiler #300 | Boiler on NG | Nat. Gas | 165.8372 | MMCF | 170812.316 | MMBTU | 120000 | lb/MMCF | 19900464 | 9950.232 | 2.2708 | lb/MMCF | 376.5766 | 0.18829 | 0.22046 | lb/MMCF | 36.5608 | 0.01828 | 9950.4386
Boiler #300 | Boiler on Oil | #2 Oil | 128949 | gal. | 17635.1942 | MMBTU | 22509.197 | lb/1000 gal | 2902538.4401 | 1451.2692 | 0.9039 | lb/1000 gal | 116.5564 | 0.058278 | 0.11 | lb/1000 gal | 14.1844 | 0.0070922 | 1451.3346
Boiler #400 | Boiler on NG | Nat. Gas | 159.0602 | MMCF | 163832.006 | MMBTU | 120000 | lb/MMCF | 19087224 | 9543.612 | 2.2708 | lb/MMCF | 361.1877 | 0.18059 | 0.22046 | lb/MMCF | 35.0667 | 0.017533 | 9543.8101
Boiler #400 | Boiler on Oil | #2 Oil | 70250 | gal. | 9607.4603 | MMBTU | 22509.197 | lb/1000 gal | 1581271.0871 | 790.6355 | 0.9039 | lb/1000 gal | 63.4986 | 0.031749 | 0.11 | lb/1000 gal | 7.7275 | 0.0038637 | 790.6712 | 39468.6643
CTG | CTG on NG | Nat. Gas | 955953 | kCF | 984631.59 | MMBTU | 110 | lb/MMBtu | 108309474.9 | 54154.7374 | 0.002213 | lb/MMBtu | 2178.9897 | 1.0895 | 0.000215 | lb/MMBtu | 211.6958 | 0.10585 | 54155.9328
CTG | CTG on Oil | #2 Oil | 121085 | gal. | 16559.7057 | MMBTU | 157 | lb/Mmbtu | 2599873.7925 | 1299.9369 | 0.00655 | lb/MMBTU | 108.4661 | 0.054233 | 0.001278 | lb/mmbtu | 21.1633 | 0.010582 | 1300.0017 | 55455.9345
HRSG with Duct Burner | Duct Burner on NG | Nat. Gas | 303564.7 | kCF | 312671.641 | MMBTU | 120000 | lb/MMCF | 36427764 | 18213.882 | 2.2708 | lb/MMCF | 689.3229 | 0.34466 | 0.22046 | lb/MMCF | 68.9322 | 0.034466 | 18214.2611 | 18214.2611
Furcolo Boiler #1 | Boiler on NG | Nat. Gas | 3.3777 | MMCF | 3445.2097 | MMBTU | 120020 | lb/MMCF | 405386.3457 | 202.6932 | 2.2708 | lb/MMCF | 7.6699 | 0.0038349 | 0.22046 | lb/MMCF | 0.74464 | 0.00037232 | 202.6974
Small Boilers - NG | Boiler on NG | Nat. Gas | 8.8724 | MMCF | 9049.8101 | MMBTU | 120000 | lb/MMCF | 1064683.5443 | 532.3418 | 2.2708 | lb/MMCF | 20.147 | 0.010074 | 0.22046 | lb/MMCF | 1.956 | 0.00097801 | 532.3528
Small Boilers - Oil | Boiler on Oil | #2 Oil | 8797.8 | gal. | 1203.1959 | MMBTU | 22509.197 | lb/1000 gal | 198031.4131 | 99.0157 | 0.9039 | lb/1000 gal | 7.9523 | 0.0039761 | 0.11 | lb/1000 gal | 0.96776 | 0.00048388 | 99.0202
Em. Gen. Group 1 | Oil Generator | #2 Oil | 202.5971 | gal. | 28.161 | MMBTU | 22600 | lb/1000 gal | 4578.695 | 2.2893 | 0.91045 | lb/1000 gal | 0.18445 | 9.2227e-05 | 0.17765 | lb/1000 gal | 0.035991 | 1.7996e-05 | 2.2895
Em. Gen. Group 2 | Oil Generator | #2 Oil | 13.5065 | gal. | 1.8774 | MMBTU | 22600 | lb/1000 gal | 305.2463 | 0.15262 | 0.91045 | lb/1000 gal | 0.012297 | 6.1485e-06 | 0.17765 | lb/1000 gal | 0.0023994 | 1.1997e-06 | 0.15263
Em. Gen. Group 3 | Oil Generator | #2 Oil | 1396.7046 | gal. | 194.1419 | MMBTU | 22600 | lb/1000 gal | 31565.5231 | 15.7828 | 0.91045 | lb/1000 gal | 1.2716 | 0.00063581 | 0.17765 | lb/1000 gal | 0.24812 | 0.00012406 | 15.7835
Em. Gen. Group 4 | Oil Generator | #2 Oil | 444.7344 | gal. | 61.8181 | MMBTU | 22600 | lb/1000 gal | 10050.9986 | 5.0255 | 0.91045 | lb/1000 gal | 0.40491 | 0.00020245 | 0.17765 | lb/1000 gal | 0.079007 | 3.9504e-05 | 5.0257
Em. Gen. Group 5 | Oil Generator | #2 Oil | 1206.5352 | gal. | 167.7084 | MMBTU | 22600 | lb/1000 gal | 27267.6946 | 13.6338 | 0.91045 | lb/1000 gal | 1.0985 | 0.00054924 | 0.17765 | lb/1000 gal | 0.21434 | 0.00010717 | 13.6345
Em. Gen. Group 6 | Oil Generator | #2 Oil | 582.4667 | gal. | 80.9629 | MMBTU | 22600 | lb/1000 gal | 13163.748 | 6.5819 | 0.91045 | lb/1000 gal | 0.53031 | 0.00026515 | 0.17765 | lb/1000 gal | 0.10348 | 5.1738e-05 | 6.5822
Em. Gen. Group 7 | NG generator | Nat. Gas | 0.12736 | MMCF | 129.9095 | MMBTU | 120019.6555 | lb/MMCF | 15285.975 | 7.643 | 2.2708 | lb/MMCF | 0.28921 | 0.0001446 | 0.22046 | lb/1000 gal | 0.028079 | 1.4039e-05 | 7.6431
Em. Gen. Group 8 | Oil generator | #2 Oil | 286.1684 | gal. | 39.7774 | MMBTU | 22600 | lb/1000 gal | 6467.4066 | 3.2337 | 0.91015 | lb/1000 gal | 0.26046 | 0.00013023 | 0.17765 | lb/1000 gal | 0.050838 | 2.5419e-05 | 3.2339
Em. Gen. Group 9 | Oil Generator | #2 Oil | 1027.1674 | gal. | 142.7763 | MMBTU | 22600 | lb/1000 gal | 23213.9835 | 11.607 | 0.91015 | lb/1000 gal | 0.93488 | 0.00046744 | 0.17765 | lb/1000 gal | 0.18248 | 9.1238e-05 | 11.6076
Em. Gen. Group EU17 - Black Start Generator | Oil Generator | #2 Oil | 205 | gal. | 28.29 | MMBTU | 22600 | lb/1000 gal | 4633 | 2.3165 | 0.91015 | lb/1000 gal | 0.18658 | 9.329e-05 | 0.17765 | lb/1000 gal | 0.036418 | 1.8209e-05 | 2.3166
Space Heating/Cooking-Propane | Propane Cooking and Heating | Propane | 17705.1 | gal. | 1611.1641 | MMBTU | 12500 | lb/1000 gal | 221313.75 | 110.6569 | 0.59525 | lb/1000 gal | 10.5389 | 0.0052695 | 0.11023 | lb/1000 gal | 1.9517 | 0.00097583 | 110.6631
Space Heating | NG Space Heating | Natural Gas | 12.2189 | MMCF | 12585.458 | MMBTU | 120019.6555 | lb/MMCF | 1466507.1199 | 733.2536 | 2.2708 | lb/MMCF | 27.7462 | 0.013873 | 0.22046 | lb/MMCF | 2.6938 | 0.0013469 | 733.2688
Dining Commons | NG Cooking | Natural Gas | 11.2892 | MMCF | 11605.31 | MMBTU | 120019.7 | lb/MMCF | 1354927.8449 | 677.4639 | 2.2708 | lb/MMCF | 25.6351 | 0.012818 | 0.22046 | lb/MMCF | 2.4888 | 0.0012444 | 677.478
LNG Facility | Boiler on NG | Natural Gas | 32.5525 | MMCF | 33529.0968 | MMBTU | 120019.7 | lb/MMCF | 3906943.8269 | 1953.4719 | 2.2708 | lb/MMCF | 73.919 | 0.036959 | 0.22046 | lb/MMCF | 7.1766 | 0.0035883 | 1953.5125 | 4377.2619
[6 empty] | Subtotal Stationary Combustion (lb/yr) |  |  | 235026961.7157 |  |  |  | 4795.2587 |  |  | 486.7403
[6 empty] | Subtotal Stationary Combustion (T/yr) |  |  | 117513.4809 |  |  |  | 2.3976 |  |  | 0.24337
Emission Factor basis is default MassDEP value
Dining Commons is not SR reportable and has a GHG-Only form

## CHP Fuel Use, CEMS Data
UMass Boiler Fuel Use and CEMS Data | [6 empty] | UMass Boiler Fuel Use and CEMS Data | [5 empty] | UMass Boiler Fuel Use and CEMS Data | [6 empty] | UMass Boiler Fuel Use and CEMS Data
Boiler 200 Operating Year 2018 | [6 empty] | Boiler 300 Operating Year 2018 | [5 empty] | Boiler 400 Operating Year 2018 | [6 empty] | CTG Operating Year 2018
Boiler 200 | [6 empty] | Boiler 300 | [5 empty] | Boiler 400 | [6 empty] | CTG
Fuel Use and Operating Hours | [6 empty] | Fuel Use and Operating Hours | [5 empty] | Fuel Use and Operating Hours | [6 empty] | Fuel Use and Operating Hours
Month | CEMS Gas (kscf) | CEMS Gas (hr) | CEMS Oil (gal) | CEMS Oil (hr) | Total Hours |  | Month | CEMS Gas (kscf) | CEMS Gas (hr) | CEMS Oil (gal) | CEMS Oil (hr) | Total Hours | Month | CEMS Gas (kscf) | CEMS Gas (hr) | CEMS Oil (gal) | CEMS Oil (hr) | Total Hours |  | Month | CEMS Gas (kscf) | CEMS Gas (hr) | CEMS Gas w/DB (hr) | CEMS Oil (gal) | CEMS Oil (hr) | CEMS Oil w/DB (hr) | NG-DB Gas (kscf) | Oil- DB Gas (kscf) | Total Operating Hours
January |  |  |  |  | 743.5 |  | January |  |  |  |  | 407.25 | January |  |  |  |  | 596.75 |  | January | [8 empty] | 728
February |  |  |  |  | 648.5 |  | February |  |  |  |  | 345.25 | February |  |  |  |  | 424.25 |  | February | [8 empty] | 672
March |  |  |  |  | 744 |  | March |  |  |  |  | 628.75 | March |  |  |  |  | 1 |  | March | [8 empty] | 744
April |  |  |  |  | 579.75 |  | April |  |  |  |  | 351.75 | April |  |  |  |  | 280.5 |  | April | [8 empty] | 578
May |  |  |  |  | 152.25 |  | May |  |  |  |  | 0 | May |  |  |  |  | 0.5 |  | May | [8 empty] | 744
June |  |  |  |  | 70.75 |  | June |  |  |  |  | 0.5 | June |  |  |  |  | 1.5 |  | June | [8 empty] | 684.75
July |  |  |  |  | 181.5 |  | July |  |  |  |  | 1 | July |  |  |  |  | 8.25 |  | July | [8 empty] | 711.75
August |  |  |  |  | 4.25 |  | August |  |  |  |  | 89.5 | August |  |  |  |  | 22.25 |  | August | [8 empty] | 720.25
September |  |  |  |  | 0.25 |  | September |  |  |  |  | 100.25 | September |  |  |  |  | 6.5 |  | September | [8 empty] | 720
October |  |  |  |  | 158.5 |  | October |  |  |  |  | 86.5 | October |  |  |  |  | 355.75 |  | October | [8 empty] | 600.75
November |  |  |  |  | 297.25 |  | November |  |  |  |  | 394.5 | November |  |  |  |  | 503.25 |  | November | [8 empty] | 720
December |  |  |  |  | 709.75 |  | December |  |  |  |  | 371 | December |  |  |  |  | 316.5 |  | December | [8 empty] | 744
Total | 275599.4 | 4093 | 106272 | 197.25 | 4290.25 |  | Total | 165837.2 | 2363 | 128949 | 413.25 | 2776.25 | Total | 159060.2 | 2301.5 | 70250 | 215.5 | 2517 |  | Total | 955953 | 8198 | 7976 | 121085 | 169.5 | 167 | 303564.7 |  | 8367.5
[28 empty] | 303564.7 | total DB NG
Boiler 200 - Natural Gas Burning | [6 empty] | B300 - Natural Gas Burning | [5 empty] | B400 - Natural Gas Burning | [6 empty] | CT1 - Natural Gas Burning
CEMS Emission Data (pounds) | [6 empty] | CEMS Emission Data (pounds) | [5 empty] | CEMS Emission Data (pounds) | [6 empty] | CEMS Emission Data (pounds)
| CO | NH3 | NOx | Operating Hours | Total Gas (kscf) |  |  | CO | NH3 | NOx | Operating Hours | Total Gas (kscf) |  | CO | NH3 | NOx | Operating Hours | Total Gas (kscf) |  |  | Gas Flow (kscf) | CO | NH3 | NOx | DB Gas Flow (kscf) | Operating hours | DB Hours
1st Qrt | [6 empty] | 1st Qrt | [5 empty] | 1st Qrt | [6 empty] | 1st Qrt
2nd Qrt | [6 empty] | 2nd Qrt | [5 empty] | 2nd Qrt | [6 empty] | 2nd Qrt
3rd Qrt | [6 empty] | 3rd Qrt | [5 empty] | 3rd Qrt | [6 empty] | 3rd Qrt
4th Qrt | [6 empty] | 4th Qrt | [5 empty] | 4th Qrt | [6 empty] | 4th Qrt
total | 3.94 | 51.45 | 1441.12 | 4093 | 275599.4 |  | Total | 3.138 | 18.777 | 826.639 | 2363 | 165837.2 | Total | 7.245 | 25.078 | 791.025 | 2301.5 | 159060.2 |  | Totals | 955953.1 | 3624.489 | 855.785 | 10115.01 | 296620.3 | 8198 | 7976
Boiler 200 - Oil Burning | [6 empty] | B300 - Oil Burning | [5 empty] | B400 - Oil Burning | [6 empty] | CT1 - Oil Burning
CEMS Emission Data (pounds) | [6 empty] | CEMS Emission Data (pounds) | [5 empty] | CEMS Emission Data (pounds) | [6 empty] | CEMS Emission Data (pounds)
| CO | NH3 | NOx | Operating Hours | Total Oil (gal) |  |  | CO | NH3 | NOx | Operating Hours | Total Oil (gal) |  | CO | NH3 | NOx | Operating Hours | Total Oil (gal) |  |  | Total Oil (gal) | CO | NH3 | NOx | DB Gas Flow (kscf) | Operating hours | DB Hours
1st Qrt | [6 empty] | 1st Qrt | [5 empty] | 1st Qrt | [6 empty] | 1st Qrt
2nd Qrt | [6 empty] | 2nd Qrt | [5 empty] | 2nd Qrt | [6 empty] | 2nd Qrt
3rd Qrt | [6 empty] | 3rd Qrt | [5 empty] | 3rd Qrt | [6 empty] | 3rd Qrt
4th Qrt | [6 empty] | 4th Qrt | [5 empty] | 4th Qrt | [6 empty] | 4th Qrt
Total | 0.07 | 6.82 | 150.91 | 197.25 | 106272 |  | Total | 0.32 | 5.38 | 284.108 | 413.25 | 128949 | Total | 0.437 | 3.245 | 152.771 | 215.5 | 70250 |  |  | 121085 | 68.019 | 21.185 | 491.264 | 6944.4 | 169.5 | 167
[21 empty] | 2018 CTG | Gas |  |  |  | Oil
Stack Test Data - Oil Fired | [21 empty] | CO | NH3 | NOx | Hours | CO | NH3 | NOx | Hours
| Boiler 200 |  | Boiler 300 |  | Boiler 400 | [12 empty] | Percent Operation by Quarter (from CEMS report) |  |  |  | [lbs] | [lbs] | [lbs] | [hours] | [lbs] | [lbs] | [lbs] | [hours]
| Emission Rate |  | Emission Rate |  | Emission Rate |  |  | Stack Testing Date: | [5 empty] | Operating Hours: | [6 empty] | TOTAL | 3624.489 | 855.785 | 10115.01 | 8198 | 68.019 | 21.185 | 491.264 | 169.5
Pollutant | lb/MMBtu | lb/1000 gal | lb/MMBtu | lb/1000 gal | lb/MMBtu | lb/1000 gal | [11 empty] | Boiler 200
NOx | 0.0054 | 0.72545 | 0.004 | 0.53737 | 0.004 | 0.53737 | [7 empty] | Boiler 200 | 24 | hr/day |  | 1st Quarter | 49.79% |  |  | 2018 CTG | Gas |  | Oil
CO** | 4.8163e-06 | 0.00064704 | 2e-05 | 0.0026869 | 2e-05 | 0.0026869 |  |  | heating value Distillate, Btu/gal | 136761 | Btu/gal | ATC fuel oil analysis (Jan 2019) |  |  | 6 | day/wk |  | 2nd Quarter | 18.71% |  |  |  | DB Fuel | DB Hours | DB Fuel | DB Hours
VOC | 0.0001 | 0.013434 | 0 | 0 | 0 | 0 |  |  | heating value Natural Gas, Btu/cf | 1030 | Btu/scf ** |  |  |  | 30 | wk/yr | 4290.25 | 3rd Quarter | 4.335% |  |  |  | [Kscf] | [hours] | [Kscf] | [hours]
NH3 | 0.0001 | 0.013434 | 0.001 | 0.13434 | 0.001 | 0.13434 | [8 empty] | 7 | wk ozone | 4320 | 4th Quarter | 27.17% | 100% |  | TOTAL | 296620.3 | 7976 | 6944.4 | 167
PM10 | 0.005 | 0.67172 | 0.004 | 0.53737 | 0.004 | 0.53737 |  | * 2/26/13, AmSpec Analysis. | [5 empty] | Boiler 300 | 24 | hr/day
PM | 0.002 | 0.26869 | 0.001 | 0.13434 | 0.001 | 0.13434 |  | ** e-mail from G. Ritter 1/24/17, value is 2016 average from Berkshire Gas | [6 empty] | 6 | day/wk |  | Boiler 300
SO2 | 0.0016 | 0.21495 | 0.0016 | 0.21495 | 0.0016 | 0.21495 | [8 empty] | 20 | wk/yr | 2776.25 | 1st Quarter | 49.75%
[15 empty] | 6 | wk ozone | 2880 | 2nd Quarter | 12.69%
Emissions rate based on stack test data at 75% load. | [13 empty] | Boiler 400 | 24 | hr/day |  | 3rd Quarter | 6.871%
**CO stack test emissions were zero. Used CEMS data to calculate emission factor | [14 empty] | 4 | day/wk |  | 4th Quarter | 30.69% | 100%
**SO2 emissions are based on a maximum sulfur content fuel of 0.0015%. Density of fuel equals 7.13 lb/gal. | [14 empty] | 27 | wk/yr | 2517
(SO2 = fuel use, gal*7.13 lb/gal*0.000015*2/2000 ) | [14 empty] | 1 | wk ozone | 2592 | Boiler 400
[14 empty] | CT | 24 | hr/day |  | 1st Quarter | 40.6%
Stack Test Data - NG Fired | [14 empty] | 7 | day/wk |  | 2nd Quarter | 11.22%
| Boiler 200 |  | Boiler 300 |  | Boiler 400 | [9 empty] | 50 | wk/yr | 8367.5 | 3rd Quarter | 1.47%
| Emission Rate |  | Emission Rate |  | Emission Rate | [9 empty] | 20 | wk ozone | 8400 | 4th Quarter | 46.7% | 100%
Pollutant | lb/MMBtu | lb/MMcf | lb/MMBtu | lb/MMcf | lb/MMBtu | lb/MMcf
NOx | 0.003 | 3.09 | 0.004 | 4.12 | 0.004 | 4.12 | [11 empty] | CT1
CO** | 1.388e-05 | 0.014296 | 1e-05 | 0.0103 | 1e-05 | 0.0103 | [11 empty] | 1st Quarter | 25.62%
VOC | 0.0016 | 1.648 | 0.002 | 2.06 | 0.002 | 2.06 | [11 empty] | 2nd Quarter | 23.98%
NH3 | 0.001 | 1.03 | 0 | 0 | 0 | 0 | [11 empty] | 3rd Quarter | 25.72%
PM10 | 0.01 | 10.3 | 0.006 | 6.18 | 0.006 | 6.18 | [11 empty] | 4th Quarter | 24.68% | 100%
PM | 0.003 | 3.09 | -- | -- | -- | --
SO2 | 0.0006 | 0.618 | 0.0006 | 0.618 | 0.0006 | 0.618
Emissions rate based on stack test data at 75% load.
**CO stack test emissions were zero. Used CEMS data to calculate emission factor

## CTG - oil
University of Massachusetts - Amherst Campus
2018 Central Heating Plant CTG and Duct Burner - Oil Fired
Actual and Potential Emissions
CTG & Duct burner - Oil
CTG fuel use and firing rate: |  |  |  | duct burner fuel use and firing rate:
oil: | 121085 | gallons | 16787.5877 | CTG on oil: | 6.9444 | MMcf | 7152.732 | MMBtu
nat. gas: | 955.953 | MMcf |  | CTG on gas: | 296.6203 | MMcf
firing rate: | 131.96 | MMBtu/hr |  | firing rate: | 87.84 | MMBtu/hr
CTG run time on oil: |  |  | 169.5 | hours |  | Oil HV = | 136761 | BTU/Gal.
duct burner hours while CTG on oil: |  |  | 167 | hours
CTG hours without duct burner: |  |  | 2.5 | hours |  | CTG on oil = | 16559.7057 | mmbtu
Proportion oil use based on hours with and without duct burner:
oil, gallons / CTG runtime oil , hours = x /CTG runtime w/o DB, hours |  |  |  | 1785.9145 | gallons oil CTG without DB
|  |  |  | 119299.0855 | gallons oil CTG with DB = |  | 16315.4622 | MMBtu
CTG ran at base load and DB at 50% | [6 empty] | 23468.1942 | MMBtu
CTG on oil with Duct Burner
|  |  | Fuel | Actual |  | Permit Max. Oil | Permit Max. | Potential
Pollutant | Emission |  | Input | Emissions |  | Oil Use | Oil Use | Emissions
| Factor | Units | (MMBtu) | (ton/year) |  | k Gal. | MMBTU | (ton/year)
NOx | 0.020933 | lb/MMBtu | 23468.1942 | 0.24563 |  | 2229.6 | 304922.3256 | 3.1915
CO | 0.0028983 | lb/MMBtu | 23468.1942 | 0.03401 |  | 2229.6 | 304922.3256 | 0.44189
VOC | 0.0005 | lb/MMBtu | 23468.1942 | 0.005867 |  | 2229.6 | 304922.3256 | 0.076231
NH3 | 0.00090271 | lb/MMBtu | 23468.1942 | 0.010593 |  | 2229.6 | 304922.3256 | 0.13763
PM10* | 0.0043 | lb/MMBtu | 23468.1942 | 0.050457 |  | 2229.6 | 304922.3256 | 0.65558
PM* | 0.0043 | lb/MMBtu | 23468.1942 | 0.050457 |  | 2229.6 | 304922.3256 | 0.65558
SOx** | 0.0016 | lb/MMBtu | 23468.1942 | 0.020695 |  | 2229.6 | 304922.3256 | 0.24394
NOx, CO, and NH3 actual emissions are obtained from CEMS, VOC based on stack data.
*PM and PM10 EF based on AP-42, Table 3.1-2, filterable portion only.
**SOx emissions are based on a maximum sulfur content fuel of 0.0015% for oil and 0.8 gr/100cf for gas.
(SOx = CTG on oil w/DB, gal*7.13 lb/gal*0.000015*2/2000 + 0.8 gr/100cf * lb/7,000 gr * DB - CTG on oil * 2/2000 = 0.102 tpy)
CTG on oil without Duct Burner |  |  | CTG at 100% load
|  |  |  | Actual |  | Permit Max. Oil | Permit Max. | Potential
Pollutant | Emission |  | Fuel | Emissions |  | Oil Use | Oil Use | Emissions
| Factor | Units | (gallons) | (ton/year) |  | k Gal. | MMBTU | (ton/year)
VOC | 0.0042 | lb/MMBtu | 1785.9145 | 0.00051291 |  | 2229.6 | 304922.3256 | 0.64034
PM10 | 0.0043 | lb/MMBtu | 1785.9145 | 0.00052512 |  | 2229.6 | 304922.3256 | 0.65558
PM | 0.0043 | lb/MMBtu | 1785.9145 | 0.00052512 |  | 2229.6 | 304922.3256 | 0.65558
SOx* | 0.0016 | lb/MMBtu | 1785.9145 | 0.000191 |  | 2229.6 | 304922.3256 | 0.24394
Emissions of Nox, CO, and NH3 are based on CEMS data and reported under CTG w/duct burner
*SOx emissions are based on a maximum sulfur content fuel of 0.0015%. Density of fuel equals 7.13 lb/gal.
(SOx = oil use, gal*7.13 lb/gal*0.000015*2/2000)
CTG-oil w/o DB
|  | Total Oil MMBtu: | 23712.4377 |  | 9.19S+3.22
[5 empty] | 3.2338 | lb/1000 gal
0.023265

## CTG - ng
University of Massachusetts - Amherst Campus
2018 Central Heating Plant CTG and Duct Burner - Natural Gas Fired
Actual and Potential Emissions
CTG & Duct burner - Natural Gas
CTG fuel use and firing rate: |  |  |  | duct burner fuel use and firing rate:
oil: | 121085 | gallons |  | CTG on oil: | 6.9444 | MMcf
nat. gas: | 955.953 | MMcf |  | CTG on gas: | 296.6203 | MMcf | 305518.909 | MMBtu
firing rate: | 131.96 | MMBtu/hr |  | firing rate: | 87.84 | MMBtu/hr
CTG run time on nat gas: |  |  | 8198 | hours | Natural Gas HV = | 1030 | BTU/scf
duct burner hours while CTG on nat gas: |  |  | 7976 | hours
CTG hours without duct burner: |  |  | 222 | hours
Proportion gas use based on hours with and without duct burner:
NG, MMcf / DB on NG, hours = x / total CTG run time on NG |  |  |  | 930.066 | MMcf CTG with DB |  | 957967.9875 | MMBtu
|  |  |  | 25.887 | MMcf CTG without DB
calculate firing rate of duct burner:
| 296.6203 | MMCF burned in | 7976 | Hours = | 0.037189 | MMcf/hr
| 87.84 | MMBTU/Hr / | 1030 | BTU/CF | 0.089126 | MMcf/hr
[5 empty] | 41.7263 | % load
Stack test data for 100% CTG/50% DB applied
CTG on gas with Duct Burner | [5 empty] | Total CTG Permit
|  |  | Fuel | Actual |  | Potential
Pollutant | Emission |  | Input | Emissions |  | Emissions
| Factor | Units | (MMBtu) | (ton/year) | EF | (ton/year)
NOx | 0.0080056 |  | 1263486.8965 | 5.0575 | 0.0080056 | 13.7
CO | 0.0028686 |  | 1263486.8965 | 1.8122 | 0.0028686 | 12.1
VOC | 0.0005 | lb/MMBtu | 1263486.8965 | 0.31587 | 0.0005 | 2.2
NH3 | 0.00067732 |  | 1263486.8965 | 0.42789 | 0.00067732 | 3
PM10* | 6.01 | lb/hr | 1263486.8965 | 23.9679 | 0.037939 | 31.4
SOx** | 0.8 | gr S/100 cf | 1263486.8965 | 1.4019 | 0.0022191 | 1.9
NOx, CO, and NH3 actual emissions are obtained from CEMS
VOC EF based on stack data
*no stack test data available, therefore manufacturer's performance data is presented
**no stack test data available, therefore sulfur content of fuel is provided
CTG on gas without Duct Burner |  |  | Stack test data for CTG at 100% load
Actual
Pollutant | Emission |  | Fuel | Emissions
| Factor | Units | (MMcf) | (ton/year) |  | MMBtu |  | Total Fuel
VOC | 0 | lb/MMBtu | 25.887 | 0 |  | 26539.6038 |  | 1290026.5003 | MMBtu
PM10* | 3.67 | lb/hr | 25.887 | 0.40737
SOx** | 0.8 | gr S/100 cf | 25.887 | 0.029585
Emissions of NOx, CO, and NH3 are obtained from CEMS and are reported under CTG w/duct burner
*no stack test data at 100% load, therefore manufacturer's performance data is presented
**no stack test data available, therefore sulfur content of fuel is provided

## Boiler Emissions
UMASS Central Heating Plant - Boiler Emissions
2018 Boiler Emissions
Process Information |  | B200 | B300 | B400 | [8 empty] | Boiler Permit Limits - Potential Emissions
| Max. input rating, MMBtu/hr (NG input rating) | 179.7 | 162.1 | 162.1 |  |  | Fuel oil heating value | 136761 | Btu/gal |  |  | Pollutant |  | Tons/Yr | Lb/Yr
| Max. input rating, MMBtu/hr (Oil input rating) | 173.4 | 156.1 | 156.1 |  |  | Natural gas heating value | 1030 | Btu/cf |  |  | PM/PM10/PM2.5 |  | 57.9 | 115800 |  |  |  |  | eDEP Data entry
| Max. oil flowrate, gal/hour | 1267.9053 | 1141.4073 | 1141.4073 |  |  | Oil density | 7.13 | lb/gal |  |  | SO2 |  | 3.1 | 6200
| Fuel Oil Use, gal | 106272 | 128949 | 70250 | [7 empty] | NOx |  | 28.9 | 57800
| Fuel Oil Use, MMBtu | 14533.865 | 17635.1942 | 9607.4603 | [7 empty] | CO |  | 53.4 | 106800 |  |  |  |  | 200 | Natural Gas |  |  | Diesel |  |  | TES
| Ozone Season Fuel Oil Use, gal | 0 | 0 | 0 | [7 empty] | VOC |  | 8.1 | 16200 | [5 empty] | Act | Pot | EF | Act | Pot | EF
| Annual Natural Gas use, kscf | 275599.4 | 165837.2 | 159060.2 |  | Oil Limits: | [5 empty] | NH3 |  | 2 | 4000 |  |  |  |  | PM10 | 1.4193 | 20.6482 | 10.3 | 0.035692 | 2.2056 | 0.67172 | 1.455
| Annual Natural Gas use, mMCF | 275.5994 | 165.8372 | 159.0602 |  | Boiler #200: 5088 Hours (No Ozone Season Use) | [13 empty] | PM2.5 | 1.4193 | 20.6482 | 10.3 | 0.035692 | 2.2056 | 0.67172 | 1.455
| Annual Natural Gas use, MMBtu | 283867.382 | 170812.316 | 163832.006 |  | Boiler #300 & #400: 13140 Total Hours (5508 Total Ozone Season Hours) | [13 empty] | SO2 | 0.08516 | 1.1055 | 0.618 | 0.011366 | 0.68995 | 0.2139 | 0.096526
| % of Total Boiler Max. Input Rating | 35.6618 | 32.1691 | 32.1691 | [15 empty] | NO2 | 0.72056 | 10.3063 | 5.229 | 0.075455 | 2.3821 | 1.42 | 0.79601
| Ozone Season Natural Gas Use, kscf | 0 | 0 | 0 | [15 empty] | CO | 0.00197 | 19.0434 | 0.014296 | 3.5e-05 | 0.0021246 | 0.00065869 | 0.002005
| Ozone Season Natural Gas Use, MMBtu | 0 | 0 | 0 | [15 empty] | VOC | 0.22709 | 2.8886 | 1.648 | 0.00071384 | 0.044113 | 0.0001 | 0.22781
[20 empty] | NH3 | 0.025725 | 0.71324 | 0.18668 | 0.00341 | 0.044113 | 0.064175 | 0.029135
|  | NOX |  |  | CO |  |  | NH3 |  |  | VOC |  |  | PM10 |  |  | PM2.5
|  | B200 | B300 | B400 | B200 | B300 | B400 | B200 | B300 | B400 | B200 | B300 | B400 | B200 | B300 | B400 | B200 | B300 | B400 | 300 | Natural Gas |  |  | Diesel
Fuel Oil Burning | Fuel Oil Emission Factor*, lb/gal oil | [9 empty] | 1.3434e-05 | 0 | 0 | 0.00067172 | 0.00053737 | 0.00053737 | 0.00067172 | 0.00053737 | 0.00053737 |  | Act | Pot | EF | Act | Pot | EF
| Fuel Oil Emission Factor*, lb/1000 gal oil (calculated for CEMS emissions) | 1.42 | 2.2033 | 2.1747 | 0.00065869 | 0.0024816 | 0.0062206 | 0.064175 | 0.041722 | 0.046192 | 0.013434 | 0 | 0 | 0.67172 | 0.53737 | 0.53737 | 0.67172 | 0.53737 | 0.53737 | PM10 | 0.51244 | 18.6259 | 6.18 | 0.034647 | 2.0512 | 0.53737 | 0.54708
| Fuel Oil Emission Factor*, lb/MMBtu oil | [9 empty] | 0.0001 | 0 | 0 | 0.005 | 0.004 | 0.004 | 0.005 | 0.004 | 0.004 | PM2.5 | 0.51244 | 18.6259 | 6.18 | 0.034647 | 2.0512 | 0.53737 | 0.54708
| Total Annual Emissions, lbs (from CEMS) | 150.91 | 284.108 | 152.771 | 0.07 | 0.32 | 0.437 | 6.82 | 5.38 | 3.245 | [9 empty] | SO2 | 0.051244 | 0.99724 | 0.618 | 0.013791 | 0.62111 | 0.2139 | 0.065035
| Total Ozone Season Emissions, lb | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | [6 empty] | NO2 | 0.41332 | 9.2969 | 4.9846 | 0.14205 | 2.0512 | 2.2033 | 0.55537
| Annual Fuel Oil Emissions (lb/yr) | 150.91 | 284.108 | 152.771 | 0.07 | 0.32 | 0.437 | 6.82 | 5.38 | 3.245 | 1.4277 | 0 | 0 | 71.3845 | 69.2936 | 37.7504 | 71.3845 | 69.2936 | 37.7504 | CO | 0.003 | 17.1783 | 0.018922 | 0.00016 | 0.02795 | 0.0024816 | 0.00316
| Annual Fuel Oil Emissions (ton/yr) | 0.075455 | 0.14205 | 0.076385 | 3.5e-05 | 0.00016 | 0.0002185 | 0.00341 | 0.00269 | 0.0016225 | 0.00071384 | 0 | 0 | 0.035692 | 0.034647 | 0.018875 | 0.035692 | 0.034647 | 0.018875 | VOC | 0.17081 | 2.6057 | 2.06 | 0 | 0 | 0 | 0.17081
| Potential Fuel Oil Emissions (lb/yr)* | 4764.1997 | 4102.308 | 4102.308 | 4.2493 | 55.9 | 20.5115 | 88.2259 | 1025.577 | 1025.577 | 88.2259 | 0 | 0 | 4411.296 | 4102.308 | 4102.308 | 4411.296 | 4102.308 | 4102.308 | NH3 | 0.0093885 | 0.64338 | 0.11323 | 0.00269 | 0.51279 | 0.041722 | 0.012078
| Potential Fuel Oil Emissions (ton/yr)* | 2.3821 | 2.0512 | 2.0512 | 0.0021246 | 0.02795 | 0.010256 | 0.044113 | 0.51279 | 0.51279 | 0.044113 | 0 | 0 | 2.2056 | 2.0512 | 2.0512 | 2.2056 | 2.0512 | 2.0512
| Ozone Season Fuel Oil Emissions - lb | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | [6 empty] | 400 | Natural Gas |  |  | Diesel
| Ozone Season Fuel Oil Emissions - lb/day | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | [7 empty] | Act | Pot | EF | Act | Pot | EF
Natural Gas Burning | Emission Factor*, lb/MMBtu Nat'l gas | [9 empty] | 0.0016 | 0.002 | 0.002 | 0.01 | 0.006 | 0.006 | 0.01 | 0.006 | 0.006 | PM10 | 0.4915 | 18.6259 | 6.18 | 0.018875 | 2.0512 | 0.53737 | 0.51037
| Emission Factor, lb/MCF (calculated for CEMS emissions) | 5.229 | 4.9846 | 4.9731 | 0.014296 | 0.018922 | 0.045549 | 0.18668 | 0.11323 | 0.15766 | 1.648 | 2.06 | 2.06 | 10.3 | 6.18 | 6.18 | 10.3 | 6.18 | 6.18 | PM2.5 | 0.4915 | 18.6259 | 6.18 | 0.018875 | 2.0512 | 0.53737 | 0.51037
| Total Annual Emissions, lbs (from CEMS) | 1441.12 | 826.639 | 791.025 | 3.94 | 3.138 | 7.245 | 51.45 | 18.777 | 25.078 | [9 empty] | SO2 | 0.04915 | 0.99724 | 0.618 | 0.0075132 | 0.62111 | 0.2139 | 0.056663
| Annual Natural Gas Emissions (lb/yr) | 1441.12 | 826.639 | 791.025 | 3.94 | 3.138 | 7.245 | 51.45 | 18.777 | 25.078 | 454.1878 | 341.6246 | 327.664 | 2838.6738 | 1024.8739 | 982.992 | 2838.6738 | 1024.8739 | 982.992 | NO2 | 0.39551 | 9.2969 | 4.9731 | 0.076385 | 2.0512 | 2.1747 | 0.4719
| Annual Natural Gas Emissions (ton/yr) | 0.72056 | 0.41332 | 0.39551 | 0.00197 | 0.001569 | 0.0036225 | 0.025725 | 0.0093885 | 0.012539 | 0.22709 | 0.17081 | 0.16383 | 1.4193 | 0.51244 | 0.4915 | 1.4193 | 0.51244 | 0.4915 | CO | 0.0036225 | 17.1783 | 0.045549 | 0.0002185 | 0.010256 | 0.0062206 | 0.003841
| Potential Natural Gas Emissions (lb/yr)** | 20612.5422 | 18593.7289 | 18593.7289 | 38086.8426 | 34356.5787 | 34356.5787 | 1426.4735 | 1286.7632 | 1286.7632 | 5777.2177 | 5211.3911 | 5211.3911 | 41296.408 | 37251.796 | 37251.796 | 41296.408 | 37251.796 | 37251.796 | VOC | 0.16383 | 2.6057 | 2.06 | 0 | 0 | 0 | 0.16383
| Potential Natural Gas Emissions (ton/yr)** | 10.3063 | 9.2969 | 9.2969 | 19.0434 | 17.1783 | 17.1783 | 0.71324 | 0.64338 | 0.64338 | 2.8886 | 2.6057 | 2.6057 | 20.6482 | 18.6259 | 18.6259 | 20.6482 | 18.6259 | 18.6259 | NH3 | 0.012539 | 0.64338 | 0.15766 | 0.0016225 | 0.51279 | 0.046192 | 0.014161
| Ozone Season Nat'l Gas Emissions, lb | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0
| Ozone Season Nat'l Gas Emissions, lb/day | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0
SO2 (lb/yr)
|  | B200 | B300 | B400
| Annual Fuel Oil use, gal | 106272 | 128949 | 70250
| Annual Fuel Oil use, lb | 757719.36 | 919406.37 | 500882.5
| % Sulfur, by Weight | 0.0015% | 0.0015% | 0.0015%
| Annual Fuel Oil Emissions, (lb/yr) | 22.7316 | 27.5822 | 15.0265
| Annual Fuel Oil Emissions, (ton/yr) | 0.011366 | 0.013791 | 0.0075132
| Emission Factor*, lb/MMBtu Nat'l gas | 0.0006 | 0.0006 | 0.0006
| Emission Factor, lb/MCF | 0.618 | 0.618 | 0.618
| Emission Factor, lb/1000 gal | 0.2139 | 0.2139 | 0.2139
| Annual Natural Gas Emissions (lb/yr) | 170.3204 | 102.4874 | 98.2992
| Annual Natural Gas Emissions (ton/yr) | 0.08516 | 0.051244 | 0.04915
| Potential Fuel Oil Emissions (lb/yr)* | 1379.8908 | 1242.22 | 1242.22
| Potential Fuel Oil Emissions (ton/yr)* | 0.68995 | 0.62111 | 0.62111
| Potential Natural Gas Emissions (lb/yr)** | 2211.0339 | 1994.483 | 1994.483
| Potential Natural Gas Emissions (ton/yr)** | 1.1055 | 0.99724 | 0.99724
Actual emissions of NOx, CO, NH3 are based on CEMS data.
All other pollutant emissions are based on annual fuel use and stack test data.
SO2 emissions are based on a maximum sulfur content fuel of 0.0015%. (SO2 = fuel use, gal*7.13 lb/gal*0.000015*2)
* Potential Oil Emissions = Stack Test Emission Factors times Boiler Rating times Max. Hours/Year on oil. Boiler #2 max. 5088 hours on oil. Boiler #3 & Boiler #4 total = 13140 Hours on oil (assume 6570 hours each)
** Potentail Natural Gas Emissions = Use Combined Permit Limit for all boilers times % of each boiler rating

## Black Start Emerg. Generator
UMASS Central Heating Plant - Black Start Emergency Generator
2018 Emission Calculations
Engine Rating: | 9.13 | MMBtu/hr
Fuel Use: | 205 | gallons |  |  | Operating data and hours from G Ritter, email 8/29/19
Hours of Operation: | 26.5 | hours
Fuel Input: | 7.7358 | gal/hr | max rating = | 65.2 | gal/hr
| <10% | assumed operating load
Fuel Oil Heating Value: | 136761 | Btu/gal
Total Heat Input: | 28.036 | MMBtu/yr
Actual Emissions
342.115
| Design Emission Factor* |  | Emissions |  | Actual
| (lb/hr) | (lb/MMBtu) | (tons/yr) |  | EF (lb/MMBTU) | EF (lb/1000 gal)
NOx | 12.91 | 1.414 | 0.17106 | 39.6435 | 12.2027 | 1668.8537
CO | 6.95 | 0.76123 | 0.092088 | 0.019822 | 6.5692 | 898.4146
VOC | 0.82 | 0.089814 | 0.010865 |  | 0.77507 | 106
PM | 0.4 | 0.043812 | 0.0053 |  | 0.37809 | 51.7073
SOx | 0.014 | 0.0015334 | 0.0001855 |  | 0.013233 | 1.8098
NH3** | 0.021 | 0.0023001 | 0.00027825 |  | 0.019849 | 2.7146
*Emission factors from UMass CHP Air Permit (1-B-08-015), Table F
**AP-42 emission factor in units of lb/MMBtu
Potential Emissions
|  | Permit limit = | 300 | hrs
|  | Emission | hours | Calculated potential emissions
|  | Factor* (lb/hr) | per year | (tons/yr)
| NOx | 12.91 | 300 | 1.9365
| CO | 6.95 | 300 | 1.0425
| VOC | 0.82 | 300 | 0.123
| PM | 0.4 | 300 | 0.06
| SOx* | 0.014 | 300 | 0.002142
| NH3** | 0.021 | 300 | 0.02876
*Emission factors from UMass CHP Air Permit (1-B-08-015), Table F
**AP-42 emission factor in units of lb/MMBtu

## Paint booth & degreaser
UMASS - Amherst Campus
2018 Actual and Potential Emissions
Maintenance Paint Booth | [5 empty] | Cold Cleaning Degreaser
Actual usage |  | 37 | liters |  |  | Actual emissions
annual paint usage |  | 9.7754 | gallons |  |  | See Naptha disposal below |  | 393 | gallons
Paint average lb VOC/gal solvent |  | 4.31 | lb VOC /gal |  |  | Total usage = waste + 5% emissions |  | 413.6842 | gallons
Paint density |  | 8.4 | lb/gal |  |  | density of solvent |  | 6.7 | lb/gal
percent by weight VOC |  | 0.5131 |  |  |  | Assume 5% of solvent added is emitted: |  | 0.069292 | tons/yr
[6 empty] | Ozone season daily: |  | 0.53302 | lb/day
pounds VOC in paint and solvent: |  | 42.1321 | lb
VOC emitted (g) from VOC report |  | 16523.3 | g
Assume 100% of VOCs are emitted: |  | 36.3949 | lb |  |  | Potential emissions
Facility Operations
total VOC emissions |  | 0.018197 | ton VOC |  |  | Hr/day | 16
| EF | 1026.1905 | lb/ton |  |  | Day/wk | 5
[6 empty] | Week/yr | 52
Particulate Emissions | [5 empty] | Hrs/Yr | 4160
lb of paint |  | 82.1136 | lb |  |  | Potential VOC Emissions, tons/yr | 0.14591
total raw material |  | 0.041057 | ton
solids in paint |  | 39.9815 | lb |  |  | EF (lb/gal) | 0.35263
assume 10% is wasted |  | 35.9834 | lb
[6 empty] | Naptha Disposal (G. Ritter/Steve LeMay e-mail 8/30/19) |  |  | Here is the data on the naptha
assume 50% is overspray |  | 17.9917 | lb |  |  | Location | Gallons |  | Petroleum Naphtha with waste code D039 (tetrachloroethylene)
[6 empty] | Studio Arts | 70
assume 95% control efficiency of filters |  | 0.89958 | lb |  |  | CHP | 45 |  | Studio Arts= 70 gal
PM emissions |  | 0.00044979 | ton |  |  | Pump Shop | 69 |  | CHP= 45 gal
| EF | 21.9107 | lb/ton |  |  | Small Engine | 45 |  | Pump shop = 69 gal
Potential Emissions | [5 empty] | Fleet | 40 |  | Small Engine = 45 gal
[6 empty] | UMTA | 124 |  | Fleet = 40 gal + 72 P of paint related material waste codes: F003, F005, D001, D018, D035, D039, D040
Operating schedule: | 1 hr/day, 7 day/wk, 52 wk/yr |  |  | 364 | hr/yr | Total | 393 | gallons
Petroleum Naphtha waste code D001
VOC |  | 0.43794 | tpy | [5 empty] | UMTA = 124 gal
PM |  | 0.010825 | tpy
Have a great weekend!
From "Spray Booth VOCs.pdf"
Steve
UMTA =120 gal

## LNG Facility
University of Massachusetts
LNG Facility - EU45
Tube-O-Therm Burners (2) - NG
Aboveground LNG Tanks (TK-01, TK-02, TK-03)
| Burner Model No. | 8 HC Tube-O-Therm | [9 empty] | TK-01 | TK-02 | TK-03
| Model # | IFWB300-DRB-C | [8 empty] | Emission Unit | 46 | 47 | 48
| Commission date | 2016-10-28 | [8 empty] | Capacity (gal) | 18000 | 18000 | 18000
| Two units, only one runs at a time. | [9 empty] | psi | 175 | 175 | 175
[11 empty] | temp (F) | -260 | -260 | -260
| Actual operation, 2018 | 186.2728 | days | (assume 24/7 operation for 6 months of operation - jan, feb, mar, apr, part of October, Nov and Dec)
|  | 24 | hr/day | [7 empty] | Throughput (gal) | 1040829.7436 | 1040829.7436 | 1040829.7436
|  | 4470.5462 | hours
| Rating | 7.5 | MMBtu/hr
|  | 0.0072816 | MMCF/hr
| Actual Fuel use | 33529.0968 | MMBtu
|  | 32.5525 | MMCF
| Potential Fuel use | 65700 | MMBtu
|  | 63.7864 | MMCF
Emission Factor Basis, AP-42 Section 1.4, Boilers < 100 MMBtu/hr
| Pollutant | Emission Factor (lb/MMCF) | Actual Emissions (lb/yr) | Actual Emissions (tpy) | Potential Emissions (lb/yr) | Potential Emissions (tpy) |  | 0.0097658
| NOx | 100 | 3255.2521 | 1.6276 | 6378.6408 | 3.1893
| SO2 | 0.6 | 19.5315 | 0.0097658 | 38.2718 | 0.019136
| CO | 84 | 2734.4118 | 1.3672 | 5358.0583 | 2.679
| PM | 1.9 | 61.8498 | 0.030925 | 121.1942 | 0.060597
| PM10 | 1.9 | 61.8498 | 0.030925 | 121.1942 | 0.060597
| PM2.5 | 1.9 | 61.8498 | 0.030925 | 121.1942 | 0.060597
| NMTOC | 5.5 | 179.0389 | 0.089519 | 350.8252 | 0.17541
| NH3 | 0.49 | 15.9507 | 0.0079754 | 31.2553 | 0.015628
2018 LNG usage
| Monthly conversion factors: |  |  | mmbtu's | Invoiced | $/MMBTU | assumed days of operation | calculated gal | % operation by quarter
18 | January | 0.0237 | dth/lb. | 66769 | 579475 | 8.68 | 31 | 807911.0401 | Q1 | 60.1%
18 | February | 0.0237 | dth/lb. | 43341 | 390159 | 9 | 28 | 524430.0857 | Q2 | 5.522%
18 | March | 0.0237 | dth/lb. | 44992 | 408417 | 9.08 | 31 | 544407.3375 | Q3 | 0%
18 | April | 0.0237 | dth/lb. | 14251 | 120930 | 8.49 | 30 | 172438.4105 | Q4 | 34.37%
18 | October Spot | 0.0237 | dth/lb. | 5838 | 56920.34 | 9.75 | 5.2728 | 70640.3369
18 | November | 0.0237 | dth/lb. | 33216 | 333965 | 10.05 | 30 | 401916.6546
18 | December | 0.0237 | dth/lb. | 49648 | 458689 | 9.24 | 31 | 600745.3657
3122489.2309
convert mmbtu to gal - 0.082644 MMBtu/gal (82644 btu/gal)

## Storage Tanks
2018 | UMASS Oil Tank Emissions - Actual
[5 empty] | 2018 Thruput | Standing Loss | Working Loss | Working Loss | Total Loss | Total Loss
AP-4 | Tank Name | Type | Fuel | Capacity, Gal. | Gallons | Lb/Yr | Lb/1000 Gal. | Lb/Yr | Lb/Yr | Tons/Yr
40 | CHP ULSD Tank #1 | AG | ULS Diesel | 234810 | 213278 | 46.44 | 0.017 | 3.6257 | 50.0657 | 0.025033
38 | CHP ULSD Tank #2 | AG | ULS Diesel | 234810 | 213278 | 46.44 | 0.017 | 3.6257 | 50.0657 | 0.025033
39 | Black Start Emergency Generator Tank | AG | ULS Diesel | 1500 | 205 | 17.77 | 0.012 | 0.00246 | 17.7725 | 0.0088862
23 | Bowditch Lodge Boiler Tank | AG | #2 Fuel Oil | 550 | 2090.8 | 0.17 | 0.018 | 0.037634 | 0.20763 | 0.00010382
23 | Farley Lodge Boiler Tank | AG | #2 Fuel Oil | 550 | 1507.3 | 0.17 | 0.018 | 0.027131 | 0.19713 | 9.8566e-05
22 | UMTS 15W/40 MotorOil | AG | Motor Oil | 1000 | 555.5 | 0.02 | 0.001 | 0.0005555 | 0.020556 | 1.0278e-05
22 | UMTS 15W/40 MotorOil | AG | Motor Oil | 1000 |  | 0.02 | 0.001 | 0 | 0.02 | 1e-05
24 | UMTS Hydraulic Fluid | AG | Trans. Fluid | 1000 | 51.5 | 0.02 | 0.001 | 5.15e-05 | 0.020051 | 1.0026e-05
25 | Life Sciences | AG | #2 Fuel Oil | 5000 | 1034.6107 | 0.17 | 0.012 | 0.012415 | 0.18242 | 9.1208e-05
46 | LNG Tank (TK-01) | AG | LNG | 18000 | 1040829.7436 | 0 | 0 | 0 | 0 | 0
47 | LNG Tank (TK-02) | AG | LNG | 18000 | 1040829.7436 | 0 | 0 | 0 | 0 | 0
48 | LNG Tank (TK-03) | AG | LNG | 18000 | 1040829.7436 | 0 | 0 | 0 | 0 | 0
14 | Conte Emergency Generator Tank | UG | ULS Diesel | 2500 | 203.3285 | 0 | 0.012 | 0.0024399 | 0.0024399 | 1.22e-06
12 | UMTS Diesel Tank #1 | UG | ULS Diesel | 10000 | 53547 | 0 | 0.012 | 0.64256 | 0.64256 | 0.00032128
12 | UMTS Diesel Tank #2 | UG | ULS Diesel | 10000 |  | 0 | 0.012 | 0 | 0 | 0
12 | Fleet Diesel Tank | UG | Biodiesel (BD20) | 10000 | 202148 | 0 | 0.012 | 2.4258 | 2.4258 | 0.0012129
11 | Fleet Gasoline Tank | UG | Gasoline | 20000 | 134461 | 0 | 5.552 | 746.5275 | 746.5275 | 0.37326
42 | UMPD Generator Tank | UG | Diesel | 5000 | 124.0304 | 0 | 0.012 | 0.0014884 | 0.0014884 | 7.4418e-07
UMASS Oil Tank Emissions - Potential
[5 empty] | Potential Thruput | Standing Loss | Working Loss | Working Loss | Total Loss | Total Loss
AP-4 | Tank Name | Type | Fuel | Capacity, Gal. | Gallons | Lb/Yr | Lb/1000 Gal. | Lb/Yr | Lb/Yr | Tons/Yr
40 | CHP ULSD Tank #1 | AG | ULS Diesel | 234810 | 12047846.5 | 46.44 | 0.017 | 204.8134 | 251.2534 | 0.12563
38 | CHP ULSD Tank #2 | AG | ULS Diesel | 234810 | 12047846.5 | 46.44 | 0.017 | 204.8134 | 251.2534 | 0.12563
39 | Black Start Emergency Generator Tank | AG | ULS Diesel | 1500 | 19560 | 17.77 | 0.012 | 0.23472 | 18.0047 | 0.0090024
25 | Life Sciences | AG | #2 Fuel Oil | 5000 | 61304
ULSD Potential thruput based on permit limit of 24,095,693 gallons, divided between two tanks.
Black Start Emergency Generator Tank potential thruput is based on permit limit of 300 hours and max. input rating of 65.2 gal/hour.
Life Sciences Generator potential
Ammonium hydroxide
2018 Annual Usage / Thruput UMass Transit Services Maintenance Department
2018 total | 24812 | gal | data from Gary Ritter e-mail 8/29/19 |  |  |  | Product | Thruput | Units
2018 total | 193481.4948 | lb |  |  |  |  | Parts Solvent Purchased |  | gallons
[7 empty] | Parts Solvent Discarded |  | gallons
2012 gal | 24000 | [5 empty] | 15W-40 Motor Oil (2 Tanks) |  | gallons
2012 emissions | 163.2 | lb NH3 |  |  |  |  | Antifreeze/Coolant |  | gallons
[7 empty] | Hydraulic Fluid |  | gallons
2018 emissions | 168.7216 | lb NH3 |  |  |  |  | R-134A Refrigerent |  | pounds
| 0.084361 | ton NH3 |  |  |  |  | Diesel Generator Fuel |  | gallons
[7 empty] | Nat Gas Generator Fuel |  | gallons
potential | 0.41 | ton NH3
Fleet Thruput (fluids from PVTA Fuel, Gas/Diesel from Campus Fuel Issues)
ef | 0.0068 | [5 empty] | Diesel - PVTA | 202148 | gal
[7 empty] | Gasoline | 134461 | gal
[7 empty] | Diesel - Fleet | 53547 | gal
[7 empty] | Motor Oil | 555.5 | gal
[7 empty] | Hydraulic Fluid | 51.5 | gal

## Small Boilers - NG1
UMass Small Boiler Emissions (Natural Gas)
2018 Operating Year - Actual Emissions
ACTUAL EMISSIONS
[6 empty] | SOx |  | NOx | Emissions | CO | Emissions | VOC | Emissions | PM/PM10 | Emissions | PM2.5 |  | NH3
| Building | Manufacturer | Rating (MMBtu/hr) | gas (therm) | gas (MMcf) | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy
| Furcolo Hall (EU27) | Burnham | 4.2 | 34688.5333 | 3.3777 | 2.0266 | 0.0010133 | 337.7657 | 0.16888 | 283.7232 | 0.14186 | 18.5771 | 0.0092886 | 6.4175 | 0.0032088 | 6.4175 | 0.0032088 | 10.8085 | 0.0054043
Emission Unit 28 | Furcolo Hall | Burnham | 2.1 | 17344.2667 | 1.6888 | 1.0133 | 0.00050665 | 168.8828 | 0.084441 | 141.8616 | 0.070931 | 9.2886 | 0.0046443 | 3.2088 | 0.0016044 | 3.2088 | 0.0016044 | 5.4043 | 0.0027021
| Stadium - McGirk | Burnham | 1.34 | 22263.95 | 2.1679 | 1.3007 | 0.00065036 | 216.7863 | 0.10839 | 182.1005 | 0.09105 | 11.9232 | 0.0059616 | 4.1189 | 0.0020595 | 4.1189 | 0.0020595 | 6.9372 | 0.0034686
| Stadium - McGirk | Burnham | 1.34 | 22263.95 | 2.1679 | 1.3007 | 0.00065036 | 216.7863 | 0.10839 | 182.1005 | 0.09105 | 11.9232 | 0.0059616 | 4.1189 | 0.0020595 | 4.1189 | 0.0020595 | 6.9372 | 0.0034686
| UMTS Boiler EVO#1 | Hamilton | 0.399 | 7692 | 0.74898 | 0.44939 | 0.00022469 | 74.8978 | 0.037449 | 62.9141 | 0.031457 | 4.1194 | 0.0020597 | 1.4231 | 0.00071153 | 1.4231 | 0.00071153 | 2.3967 | 0.0011984
| UMTS Boiler EVO#2 | Hamilton | 0.399 | 7692 | 0.74898 | 0.44939 | 0.00022469 | 74.8978 | 0.037449 | 62.9141 | 0.031457 | 4.1194 | 0.0020597 | 1.4231 | 0.00071153 | 1.4231 | 0.00071153 | 2.3967 | 0.0011984
| UMTS Boiler EVO#3 | Hamilton | 0.399 | 7692 | 0.74898 | 0.44939 | 0.00022469 | 74.8978 | 0.037449 | 62.9141 | 0.031457 | 4.1194 | 0.0020597 | 1.4231 | 0.00071153 | 1.4231 | 0.00071153 | 2.3967 | 0.0011984
| Wysocki House | HB Smith | 0.14 | 1506 | 0.14664 | 0.087984 | 4.3992e-05 | 13.7842 | 0.0068921 | 5.8656 | 0.0029328 | 0.80652 | 0.00040326 | 0.27862 | 0.00013931 | 0.27862 | 0.00013931 | 0.46925 | 0.00023463
| RTIC furnaces |  | 0.2 | 4665 | 0.45424 | 0.27254 | 0.00013627 | 42.6981 | 0.021349 | 18.1694 | 0.0090847 | 2.4983 | 0.0012491 | 0.86305 | 0.00043152 | 0.86305 | 0.00043152 | 1.4536 | 0.00072678
| EU 28 Total |  | 6.317 | 91119.1667 | 8.8724 | 5.3234 | 0.0026617 | 883.631 | 0.44182 | 718.8399 | 0.35942 | 48.798 | 0.024399 | 16.8575 | 0.0084287 | 16.8575 | 0.0084287 | 28.3916 | 0.014196
POTENTIAL EMISSIONS
[6 empty] | SOx |  | NOx | Emissions | CO | Emissions | VOC | Emissions | PM/PM10 | Emissions | PM2.5 |  | NH3
| Building | Manufacturer | Rating (MMBtu/hr) |  | gas (MMcf) | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy
| Furcolo Hall (EU 27) | Burnham | 4.2 |  | 35.9648 | 21.5789 | 0.010789 | 3596.4809 | 1.7982 | 3021.044 | 1.5105 | 197.8065 | 0.098903 | 68.3331 | 0.034167 | 68.3331 | 0.034167 | 115.0874 | 0.057544
| Furcolo Hall | Burnham | 2.1 |  | 17.9824 | 10.7894 | 0.0053947 | 1798.2405 | 0.89912 | 1510.522 | 0.75526 | 98.9032 | 0.049452 | 34.1666 | 0.017083 | 34.1666 | 0.017083 | 57.5437 | 0.028772
| Stadium - McGirk | Burnham | 1.34 |  | 11.4745 | 6.8847 | 0.0034423 | 1147.4487 | 0.57372 | 963.8569 | 0.48193 | 63.1097 | 0.031555 | 21.8015 | 0.010901 | 21.8015 | 0.010901 | 36.7184 | 0.018359
| Stadium - McGirk | Burnham | 1.34 |  | 11.4745 | 6.8847 | 0.0034423 | 1147.4487 | 0.57372 | 963.8569 | 0.48193 | 63.1097 | 0.031555 | 21.8015 | 0.010901 | 21.8015 | 0.010901 | 36.7184 | 0.018359
| UMTS Boiler EVO#1 | Hamilton | 0.399 |  | 3.4167 | 2.05 | 0.001025 | 341.6657 | 0.17083 | 286.9992 | 0.1435 | 18.7916 | 0.0093958 | 6.4916 | 0.0032458 | 6.4916 | 0.0032458 | 10.9333 | 0.0054667
| UMTS Boiler EVO#2 | Hamilton | 0.399 |  | 3.4167 | 2.05 | 0.001025 | 341.6657 | 0.17083 | 286.9992 | 0.1435 | 18.7916 | 0.0093958 | 6.4916 | 0.0032458 | 6.4916 | 0.0032458 | 10.9333 | 0.0054667
| UMTS Boiler EVO#3 | Hamilton | 0.399 |  | 3.4167 | 2.05 | 0.001025 | 341.6657 | 0.17083 | 286.9992 | 0.1435 | 18.7916 | 0.0093958 | 6.4916 | 0.0032458 | 6.4916 | 0.0032458 | 10.9333 | 0.0054667
| Wysocki House | HB Smith | 0.14 |  | 1.1988 | 0.7193 | 0.00035965 | 112.6897 | 0.056345 | 47.9531 | 0.023977 | 6.5935 | 0.0032968 | 2.2778 | 0.0011389 | 2.2778 | 0.0011389 | 3.8362 | 0.0019181
| RTIC furnaces |  | 0.2 |  | 1.7126 | 1.0276 | 0.00051378 | 160.9853 | 0.080493 | 68.5044 | 0.034252 | 9.4194 | 0.0047097 | 3.254 | 0.001627 | 3.254 | 0.001627 | 5.4804 | 0.0027402
| EU28 Total |  | 6.317 |  | 54.0928 | 32.4557 | 0.016228 | 5391.81 | 2.6959 | 4415.6908 | 2.2078 | 297.5103 | 0.14876 | 102.7763 | 0.051388 | 102.7763 | 0.051388 | 173.0969 | 0.086548
| Emission Factors-natural gas |  | lb/MMcf |  |  | 0.6 |  | 100 |  | 84 |  | 5.5 |  | 1.9 |  | 1.9 |  | 3.2
| Emission Factors-natural gas (space heaters <0.3) |  | lb/MMcf |  |  | 0.6 |  | 94 |  | 40 |  | 5.5 |  | 1.9 |  | 1.9 |  | 3.2
| Ozone Season Daily: |  | 2.5546 |  | lb/day

## Small Boilers - Oil
UMass Small Boiler Emissions (#2 Fuel Oil)
2018 Operating Year
Actual Emissions
|  |  |  | SOx |  | NOx | Emissions | CO | Emissions | VOC | Emissions | PM | Emissions | PM2.5 |  | PM10 |  | NH3
Building | Manufacturer | Unit Rating btu/hr | Fuel Use (gal) | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy
Emission Unit 21
Bowditch House (31 Cubhouse Dr) | Boch | 450100 | 2090.8 | 0.44534 | 0.00022267 | 41.816 | 0.020908 | 10.454 | 0.005227 | 0.71087 | 0.00035544 | 4.1816 | 0.0020908 | 1.7354 | 0.00086768 | 2.2581 | 0.001129 | 1.6726 | 0.00083632
Farley Lodge (41 Clubhouse Dr) | H.B Smith | 450100 | 1507.3 | 0.32105 | 0.00016053 | 30.146 | 0.015073 | 7.5365 | 0.0037682 | 0.51248 | 0.00025624 | 3.0146 | 0.0015073 | 1.2511 | 0.00062553 | 1.6279 | 0.00081394 | 1.2058 | 0.00060292
Tillson Farm | Weil Mcclain | 450000 | 852.7 | 0.18163 | 9.0813e-05 | 17.054 | 0.008527 | 4.2635 | 0.0021317 | 0.28992 | 0.00014496 | 1.7054 | 0.0008527 | 0.70774 | 0.00035387 | 0.92092 | 0.00046046 | 0.68216 | 0.00034108
93 Fearing Street | Buderus | 240000 | 1907.5 | 0.4063 | 0.00020315 | 38.15 | 0.019075 | 9.5375 | 0.0047687 | 0.64855 | 0.00032428 | 3.815 | 0.0019075 | 1.5832 | 0.00079161 | 2.0601 | 0.00103 | 1.526 | 0.000763
513 E Pleasant St. |  | 200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
758 N. Pleasant - Holocaust Memorial |  | 450100 | 1539.5 | 0.32791 | 0.00016396 | 30.79 | 0.015395 | 7.6975 | 0.0038487 | 0.52343 | 0.00026172 | 3.079 | 0.0015395 | 1.2778 | 0.00063889 | 1.6627 | 0.00083133 | 1.2316 | 0.0006158
650 East Pleasant Street |  | 200000 | 900 | 0.1917 | 9.585e-05 | 18 | 0.009 | 4.5 | 0.00225 | 0.306 | 0.000153 | 1.8 | 0.0009 | 0.747 | 0.0003735 | 0.972 | 0.000486 | 0.72 | 0.00036
Tillson Sawmill* | H.B Smith | 80000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS - OIL BOILERS |  | 2440300 | 8797.8 | 1.8739 | 0.00093697 | 175.956 | 0.087978 | 43.989 | 0.021994 | 2.9913 | 0.0014956 | 17.5956 | 0.0087978 | 7.3022 | 0.0036511 | 9.5016 | 0.0047508 | 7.0382 | 0.0035191
Potential Emissions
|  |  |  | SOx |  | NOx |  | CO |  | VOC |  | PM |  | PM2.5 |  | PM10 |  | NH3
Building | Manufacturer | Btu Rating | Max gals/hr | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | lb/yr | tpy | 24 | tpy | lb/yr | tpy
Bowditch House | Boch | 450100 | 3.215 | 5.9988 | 0.0029994 | 563.268 | 0.28163 | 140.817 | 0.070408 | 9.5756 | 0.0047878 | 56.3268 | 0.028163 | 23.3756 | 0.011688 | 30.4165 | 0.015208 | 22.5307 | 0.011265
Farley Lodge | H.B Smith | 450100 | 3.215 | 5.9988 | 0.0029994 | 563.268 | 0.28163 | 140.817 | 0.070408 | 9.5756 | 0.0047878 | 56.3268 | 0.028163 | 23.3756 | 0.011688 | 30.4165 | 0.015208 | 22.5307 | 0.011265
Tillson Farm | Weil Mcclain | 450000 | 3.2143 | 5.9975 | 0.0029987 | 563.1429 | 0.28157 | 140.7857 | 0.070393 | 9.5734 | 0.0047867 | 56.3143 | 0.028157 | 23.3704 | 0.011685 | 30.4097 | 0.015205 | 22.5257 | 0.011263
191 Fearing Street | Buderus | 240000 | 1.7391 | 3.245 | 0.0016225 | 304.6957 | 0.15235 | 76.1739 | 0.038087 | 5.1798 | 0.0025899 | 30.4696 | 0.015235 | 12.6449 | 0.0063224 | 16.4536 | 0.0082268 | 12.1878 | 0.0060939
513 E Pleasant St. |  | 200000 | 1.4493 | 2.7042 | 0.0013521 | 253.913 | 0.12696 | 63.4783 | 0.031739 | 4.3165 | 0.0021583 | 25.3913 | 0.012696 | 10.5374 | 0.0052687 | 13.7113 | 0.0068557 | 10.1565 | 0.0050783
758 N. Pleasant - Holocaust Memorial |  | 450100 | 3.2616 | 6.0857 | 0.0030429 | 571.4313 | 0.28572 | 142.8578 | 0.071429 | 9.7143 | 0.0048572 | 57.1431 | 0.028572 | 23.7144 | 0.011857 | 30.8573 | 0.015429 | 22.8573 | 0.011429
650 East Pleasant Street |  | 200000 | 1.4493 | 2.7042 | 0.0013521 | 253.913 | 0.12696 | 63.4783 | 0.031739 | 4.3165 | 0.0021583 | 25.3913 | 0.012696 | 10.5374 | 0.0052687 | 13.7113 | 0.0068557 | 10.1565 | 0.0050783
Tillson Sawmill* | H.B Smith | 80000 | 0.87912 | 0.011552 | 5.7758e-06 | 1.8098 | 0.00090488 | 0.77011 | 0.00038505 | 0.10589 | 5.2945e-05 | 0.14632 | 7.316e-05 | 0.03658 | 1.829e-05 | 0.03658 | 1.829e-05 | 0.061609 | 3.0804e-05
TOTALS - OIL BOILERS |  | 2440300 | 17.5436 | 32.7342 | 0.016367 | 3073.6319 | 1.5368 | 768.408 | 0.3842 | 52.2517 | 0.026126 | 307.3632 | 0.15368 | 127.5557 | 0.063778 | 165.9761 | 0.082988 | 122.9453 | 0.061473
Oil Emission Factors |  |  |  | 153681.595
SOx | 0.213 | lb/1000 gal
NOx | 20 | lb/1000 gal
CO | 5 | lb/1000 gal
VOC | 0.34 | lb/1000 gal
PM | 2 | lb/1000 gal
PM2.5 | 0.83 | lb/1000 gal
PM10 | 1.08 | lb/1000 gal
NH3 | 0.8 | lb/1000 gal
Ozone Season Daily: |  | 11.8217 | lb/day
Montague House and Waskiewicz are not listed because they are not contiguous to the campus.
Tillson Sawmill has been abandoned but could potentially be restarted.
Rating Calcs for Morrill Temp Boilers
33480 | hp to MMBtu/hr
150 | hp
| 5.022 | MMBtu/hr
Assume 80% efficiency | 6.2775 | MMBtu/hr
20 | hp
| 0.6696 | MMBtu/hr
Assume 80% efficiency | 0.837 | MMBtu/hr

## Emergency Generators-NG
UMass Emergency Generator Emissions - Natural Gas
2018 Operating Year
Emergency |  |  | output | input | Actual Emissions | [8 empty] | Potential Emissions (See note)
Generator | Manufacturer | Model | kW | MMBTU | Run Time | MMBtu/ | PM | SOx | NOx | CO | VOC | PM2.5 | NH3 | Run Time | MMBtu/ | PM | SOx | NOx | CO | VOC | PM2.5 | NH3
[5 empty] | Hour/year | year | tpy | tpy | tpy | tpy | tpy | tpy | tpy | Hour/year | year | tpy | tpy | tpy | tpy | tpy | tpy | tpy
Group 7
Dubois Library (Node 1) | Caterpillar |  | 250 | 2.3468 | 3 | 7.0403 | 0.00016897 | 2.1121e-06 | 0.0061591 | 0.031541 | 0.00049272 | 3.3441e-05 | 6.3362e-05 | 300 | 704.025 | 0.016897 | 0.00021121 | 2.1002 | 0.13553 | 0.46809 | 0.0033441 | 0.0063362
Emerson House | Cummins | GGMB-1205290 | 25 | 0.23467 | 0.4 | 0.09387 | 2.2529e-06 | 2.8161e-08 | 8.2121e-05 | 0.00042055 | 6.5697e-06 | 4.4588e-07 | 8.4483e-07 | 300 | 70.4025 | 0.0016897 | 2.1121e-05 | 0.061591 | 0.31541 | 0.0049272 | 0.00033441 | 0.00063362
Franklin Dining Hall | Onan | 1010JC3R/1J | 10 | 0.09387 | 4.2 | 0.39425 | 9.4621e-06 | 1.1828e-07 | 0.00034491 | 0.0017663 | 2.7593e-05 | 1.8727e-06 | 3.5483e-06 | 300 | 28.161 | 0.00067586 | 8.4483e-06 | 0.024636 | 0.12617 | 0.0019709 | 0.00013376 | 0.00025345
Hampden dining Hall | Onan | 1G0857725 | 12 | 0.11264 | 2.6 | 0.29287 | 7.029e-06 | 8.7862e-08 | 0.00025622 | 0.0013121 | 2.0497e-05 | 1.3912e-06 | 2.6359e-06 | 300 | 33.7932 | 0.00081104 | 1.0138e-05 | 0.029563 | 0.1514 | 0.0023651 | 0.00016052 | 0.00030414
Health Center South Wing | Waukesha |  | 100 | 0.9387 | 76.3 | 71.6228 | 0.0017189 | 2.1487e-05 | 0.062658 | 0.32088 | 0.0050127 | 0.00034021 | 0.00064461 | 300 | 281.61 | 0.0067586 | 8.4483e-05 | 0.24636 | 1.2617 | 0.019709 | 0.0013376 | 0.0025345
James House | Cummins |  | 25 | 0.23467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 70.4025 | 0.0016897 | 2.1121e-05 | 0.061591 | 0.31541 | 0.0049272 | 0.00033441 | 0.00063362
Lederle GRC | Onan | 10AJ-1R/8390K | 1 | 0.009387 | 1 | 0.009387 | 2.2529e-07 | 2.8161e-09 | 8.2121e-06 | 4.2055e-05 | 6.5697e-07 | 4.4588e-08 | 8.4483e-08 | 300 | 2.8161 | 6.7586e-05 | 8.4483e-07 | 0.0024636 | 0.012617 | 0.00019709 | 1.3376e-05 | 2.5345e-05
McGuirk Stadium | Generac |  | 200 | 1.8774 | 9.4 | 17.6476 | 0.00042354 | 5.2943e-06 | 0.015439 | 0.0033973 | 0.0012351 | 8.3826e-05 | 0.00015883 | 300 | 563.22 | 0.013517 | 0.00016897 | 0.49272 | 2.5233 | 0.039418 | 0.0026753 | 0.005069
Melville | Cummins |  | 25 | 0.23467 | 0.7 | 0.16427 | 3.9425e-06 | 4.9282e-08 | 0.00014371 | 0.00073596 | 1.1497e-05 | 7.8029e-07 | 1.4785e-06 | 300 | 70.4025 | 0.0016897 | 2.1121e-05 | 0.061591 | 0.31541 | 0.0049272 | 0.00033441 | 0.00063362
Patterson | Kohler | 0 | 30 | 0.28161 | 42.2 | 11.8839 | 0.00028521 | 3.5652e-06 | 0.010396 | 0.053242 | 0.00083172 | 5.6449e-05 | 0.00010696 | 300 | 84.483 | 0.0020276 | 2.5345e-05 | 0.073909 | 0.3785 | 0.0059127 | 0.00040129 | 0.00076035
Bus Garage | Kohler | 0 | 63 | 0.59138 | 28.2 | 16.6769 | 0.00040025 | 5.0031e-06 | 0.01459 | 0.074715 | 0.0011672 | 7.9215e-05 | 0.00015009 | 300 | 177.4143 | 0.0042579 | 5.3224e-05 | 0.15521 | 0.79484 | 0.012417 | 0.00084272 | 0.0015967
Research and Education Greenhouse (Bowditch) | Generac |  | 150 | 1.4081 | 2.9 | 4.0833 | 9.8e-05 | 1.225e-06 | 0.012181 | 0.00078607 | 0.0027149 | 1.9396e-05 | 3.675e-05 | 300 | 422.415 | 0.010138 | 0.00012672 | 0.36954 | 1.8925 | 0.029563 | 0.0020065 | 0.0038017
|  |  | TOTALS | 8.3638 | 170.9 | 129.9095 | 0.0031178 | 3.8973e-05 | 0.12226 | 0.48884 | 0.011521 | 0.00061707 | 0.0011692 |  | 2509.1451 | 0.060219 | 0.00075274 | 3.6794 | 8.2227 | 0.59442 | 0.011918 | 0.9
Potential emissions based on operating permit limit of 300 hr/yr.
|  | 1-100 kW | 250-350 kW | AP-42 Section 3.2 |  | Group 7
|  | g/hp hr | g/hp hr | lb/MMBtu |  | EF lb/mmbtu | EF (lb/mcf)
| PM | negligible | negligible | 0.048 |  | 0.048 | 48.96 |  |  |  | 47
| SOx | negligible | negligible | 0.0006 |  | 0.0006 | 0.612
| NOx | 5 | 17.05 |  |  | 1.8822 | 1919.8558
| CO | 25.6 | 1.1 |  |  | 7.5258 | 7676.359 | NOTE: | BHP=kW/0.746
| VOC | 0.4 | 3.8 |  |  | 0.17737 | 180.9184 |  | Inlet HP = Outlet HP/0.9
| PM2.5 |  |  | 0.0095 |  | 0.0095 | 9.69
| NH3 |  |  | 0.018 |  | 0.018 | 18.36

## Emergency Generators - Diesel
University of Massachusetts
Diesel Generator Emissions - Actual and Potential
Operating Year 2018
[8 empty] | Actual Emissions (tpy) | [6 empty] | Potential Emissions (tpy) (See note)
Generator | Manufacturer | HP (output) | BTU (input) | Output kW | Input Rate (MMBTU/hr) | Run time (hr/yr) | Total Input MMBtu/yr | PM | SOx | NOx | CO | VOC | PM2.5 | NH3 | PM | SOx | NOx | CO | VOC | PM2.5 | NH3
GROUP 1 - DIESEL
Conte Polymer Ctr | Caterpillar |  |  | 1000 | 9.387 | 3 | 28.161 | 0.004365 | 0.0040833 | 0.061954 | 0.013376 | 0.0060546 | 0.004365 | 0.00029569 | 0.4365 | 0.40833 | 6.1954 | 1.3376 | 0.60546 | 0.4365 | 0.029569
|  |  |  | Group 1 Total: | 9.387 | 3 | 28.161 | 0.004365 | 0.0040833 | 0.061954 | 0.013376 | 0.0060546 | 0.004365 | 0.00029569 | 0.4365 | 0.40833 | 6.1954 | 1.3376 | 0.60546 | 0.4365 | 0.029569
[5 empty] | 67.5324 | gal/hr | 202.5971
GROUP 2 - DIESEL
Physical Plant | Caterpillar | 107.28 | 750960 | 80 | 0.75096 | 2.5 | 1.8774 | 0.000291 | 0.00027222 | 0.0041303 | 0.00089176 | 0.00040364 | 0.000291 | 1.9713e-05 | 0.03492 | 0.032667 | 0.49563 | 0.10701 | 0.048437 | 0.03492 | 0.0023655
|  |  |  | Group 2 Total: | 0.75096 | 2.5 | 1.8774 | 0.000291 | 0.00027222 | 0.0041303 | 0.00089176 | 0.00040364 | 0.000291 | 1.9713e-05 | 0.03492 | 0.032667 | 0.49563 | 0.10701 | 0.048437 | 0.03492 | 0.0023655
[5 empty] | 5.4026 | gal/hr | 13.5065
GROUP 3 - DIESEL
Southwest-Node 2 | Caterpillar | 167.625 | 1173375 | 125 | 1.1734 | 5 | 5.8669 | 0.00090937 | 0.0008507 | 0.012907 | 0.0027868 | 0.0012614 | 0.00090937 | 6.1602e-05 | 0.054562 | 0.051042 | 0.77443 | 0.16721 | 0.075683 | 0.054562 | 0.0036961
Brooks Hall-Node 4 | Caterpillar | 167.625 | 1173375 | 125 | 1.1734 | 10 | 11.7338 | 0.0018187 | 0.0017014 | 0.025814 | 0.0055735 | 0.0025228 | 0.0018187 | 0.0001232 | 0.054562 | 0.051042 | 0.77443 | 0.16721 | 0.075683 | 0.054562 | 0.0036961
Sylvan-Node 6 | Caterpillar | 167.625 | 1173375 | 125 | 1.1734 | 5 | 5.8669 | 0.00090937 | 0.0008507 | 0.012907 | 0.0027868 | 0.0012614 | 0.00090937 | 6.1602e-05 | 0.054562 | 0.051042 | 0.77443 | 0.16721 | 0.075683 | 0.054562 | 0.0036961
Dubois Library | Caterpillar | 335.25 | 2346750 | 250 | 2.3468 | 7 | 16.4273 | 0.0025462 | 0.002382 | 0.03614 | 0.0078029 | 0.0035319 | 0.0025462 | 0.00017249 | 0.10912 | 0.10208 | 1.5489 | 0.33441 | 0.15137 | 0.10912 | 0.0073923
Webster House | Caterpillar | 469.35 | 3285450 | 350 | 3.2854 | 8 | 26.2836 | 0.004074 | 0.0038111 | 0.057824 | 0.012485 | 0.005651 | 0.004074 | 0.00027598 | 0.15277 | 0.14292 | 2.1684 | 0.46818 | 0.21191 | 0.15277 | 0.010349
Lederle (Node 5) | Caterpillar | 335.25 | 2346750 | 250 | 2.3468 | 5 | 11.7338 | 0.0018187 | 0.0017014 | 0.025814 | 0.0055735 | 0.0025228 | 0.0018187 | 0.0001232 | 0.10912 | 0.10208 | 1.5489 | 0.33441 | 0.15137 | 0.10912 | 0.0073923
Dickinson | Caterpillar | 148.851 | 1041957 | 111 | 1.042 | 2 | 2.0839 | 0.00032301 | 0.00030217 | 0.0045846 | 0.00098986 | 0.00044804 | 0.00032301 | 2.1881e-05 | 0.048451 | 0.045325 | 0.68769 | 0.14848 | 0.067206 | 0.048451 | 0.0032822
Integrated Science Building | Caterpillar | 1072.8 | 7509600 | 800 | 7.5096 | 5.4 | 40.5518 | 0.0062855 | 0.00588 | 0.089214 | 0.019262 | 0.0087186 | 0.0062855 | 0.00042579 | 0.3492 | 0.32667 | 4.9563 | 1.0701 | 0.48437 | 0.3492 | 0.023655
Engineering Lab II | Caterpillar | 402.3 | 2816100 | 300 | 2.8161 | 4 | 11.2644 | 0.001746 | 0.0016333 | 0.024782 | 0.0053506 | 0.0024218 | 0.001746 | 0.00011828 | 0.13095 | 0.1225 | 1.8586 | 0.40129 | 0.18164 | 0.13095 | 0.0088707
Chancellor | Caterpillar | 49.7511 | 348257.7 | 37.1 | 0.34826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016194 | 0.015149 | 0.22985 | 0.049627 | 0.022463 | 0.016194 | 0.001097
Honors College | Caterpillar | 1072.8 | 7509600 | 800 | 7.5096 | 8.3 | 62.3297 | 0.0096611 | 0.0090378 | 0.13713 | 0.029607 | 0.013401 | 0.0096611 | 0.00065446 | 0.3492 | 0.32667 | 4.9563 | 1.0701 | 0.48437 | 0.3492 | 0.023655
|  |  |  | Group 3 Total: | 30.7246 | 59.7 | 194.1419 | 0.030092 | 0.028151 | 0.42711 | 0.092217 | 0.041741 | 0.030092 | 0.0020385 | 1.4287 | 1.3365 | 20.2782 | 4.3783 | 1.9817 | 1.4287 | 0.096782
[5 empty] | 221.0402 | gal/hr | 1396.7046
GROUP 4 - DIESEL
Coolidge house | Cummins | 154.215 | 1079505 | 115 | 1.0795 | 4.6 | 4.9657 | 0.00076969 | 0.00072003 | 0.010925 | 0.0023587 | 0.0010676 | 0.00076969 | 5.214e-05 | 0.050197 | 0.046958 | 0.71247 | 0.15383 | 0.069628 | 0.050197 | 0.0034004
John Adams house | Cummins | 167.625 | 1173375 | 125 | 1.1734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054562 | 0.051042 | 0.77443 | 0.16721 | 0.075683 | 0.054562 | 0.0036961
John Quincy Adams | Cummins | 167.625 | 1173375 | 125 | 1.1734 | 3.7 | 4.3415 | 0.00067293 | 0.00062952 | 0.0095513 | 0.0020622 | 0.00093342 | 0.00067293 | 4.5586e-05 | 0.054562 | 0.051042 | 0.77443 | 0.16721 | 0.075683 | 0.054562 | 0.0036961
Kennedy house | Onan | 154.215 | 1079505 | 115 | 1.0795 | 10.1 | 10.903 | 0.00169 | 0.0015809 | 0.023987 | 0.0051789 | 0.0023441 | 0.00169 | 0.00011448 | 0.050197 | 0.046958 | 0.71247 | 0.15383 | 0.069628 | 0.050197 | 0.0034004
Skinner Hall | Cummins | 201.15 | 1408050 | 150 | 1.4081 | 1.1 | 1.5489 | 0.00024007 | 0.00022458 | 0.0034075 | 0.00073571 | 0.000333 | 0.00024007 | 1.6263e-05 | 0.065474 | 0.06125 | 0.92931 | 0.20065 | 0.090819 | 0.065474 | 0.0044354
Washington house | Cummins | 167.625 | 1173375 | 125 | 1.1734 | 1.9 | 2.2294 | 0.00034556 | 0.00032326 | 0.0049047 | 0.001059 | 0.00047932 | 0.00034556 | 2.3409e-05 | 0.054562 | 0.051042 | 0.77443 | 0.16721 | 0.075683 | 0.054562 | 0.0036961
Berkshire House | Cummins | 107.28 | 750960 | 80 | 0.75096 | 7 | 5.2567 | 0.00081479 | 0.00076222 | 0.011565 | 0.0024969 | 0.0011302 | 0.00081479 | 5.5196e-05 | 0.03492 | 0.032667 | 0.49563 | 0.10701 | 0.048437 | 0.03492 | 0.0023655
UMPD | Cummins | 402.3 | 2816100 | 300 | 2.8161 | 6.1 | 17.1782 | 0.0026626 | 0.0024908 | 0.037792 | 0.0081596 | 0.0036933 | 0.0026626 | 0.00018037 | 0.13095 | 0.1225 | 1.8586 | 0.40129 | 0.18164 | 0.13095 | 0.0088707
Goessmann | Cummins | 536.4 | 3754800 | 400 | 3.7548 | 4.1 | 15.3947 | 0.0023862 | 0.0022322 | 0.033868 | 0.0073125 | 0.0033099 | 0.0023862 | 0.00016164 | 0.1746 | 0.16333 | 2.4782 | 0.53506 | 0.24218 | 0.1746 | 0.011828
|  |  |  | Group 4 Total: | 14.409 | 38.6 | 61.8181 | 0.0095818 | 0.0089636 | 0.136 | 0.029364 | 0.013291 | 0.0095818 | 0.00064909 | 0.67002 | 0.62679 | 9.51 | 2.0533 | 0.92938 | 0.67002 | 0.045388
[5 empty] | 103.6622 | gal/hr | 444.7344
GROUP 5 - DIESEL
Comp. Science Bldg. | Kohler | 100.575 | 704025 | 75 | 0.70403 | 8 | 5.6322 | 0.00087299 | 0.00081667 | 0.012391 | 0.0026753 | 0.0012109 | 0.00087299 | 5.9138e-05 | 0.032737 | 0.030625 | 0.46466 | 0.10032 | 0.04541 | 0.032737 | 0.0022177
Morrill (Public Health) | Kohler | 335.25 | 2346750 | 250 | 1.4 | 5.8 | 8.12 | 0.0012586 | 0.0011774 | 0.017864 | 0.003857 | 0.0017458 | 0.0012586 | 8.526e-05 | 0.0651 | 0.0609 | 0.924 | 0.1995 | 0.0903 | 0.0651 | 0.00441
Isenburg SOM Addition | Kohler | 683.91 | 4787370 | 510 | 4.7874 | 7.2 | 34.4691 | 0.0053427 | 0.004998 | 0.075832 | 0.016373 | 0.0074108 | 0.0053427 | 0.00036193 | 0.22261 | 0.20825 | 3.1597 | 0.6822 | 0.30879 | 0.22261 | 0.01508
Animal Care | Kohler | 469.35 | 3285450 | 350 | 3.2854 | 1.7 | 5.5853 | 0.00086572 | 0.00080986 | 0.012288 | 0.002653 | 0.0012008 | 0.00086572 | 5.8645e-05 | 0.15277 | 0.14292 | 2.1684 | 0.46818 | 0.21191 | 0.15277 | 0.010349
PVTA - 2 (Bus Garage) | Kohler | 134.1 | 938700 | 100 | 0.9387 | 2.2 | 2.0651 | 0.0003201 | 0.00029945 | 0.0045433 | 0.00098094 | 0.00044401 | 0.0003201 | 2.1684e-05 | 0.04365 | 0.040833 | 0.61954 | 0.13376 | 0.060546 | 0.04365 | 0.0029569
Grounds Maintenance (Tilson) | Kohler | 134.1 | 938700 | 100 | 0.9387 | 12.3 | 11.546 | 0.0017896 | 0.0016742 | 0.025401 | 0.0054844 | 0.0024824 | 0.0017896 | 0.00012123 | 0.04365 | 0.040833 | 0.61954 | 0.13376 | 0.060546 | 0.04365 | 0.0029569
Totman | Kohler | 469.35 | 3285450 | 350 | 3.2854 | 4.1 | 13.4703 | 0.0020879 | 0.0019532 | 0.029635 | 0.0063984 | 0.0028961 | 0.0020879 | 0.00014144 | 0.15277 | 0.14292 | 2.1684 | 0.46818 | 0.21191 | 0.15277 | 0.010349
Draper | Kohler | 134.1 | 938700 | 100 | 0.9387 | 2.6 | 2.4406 | 0.0003783 | 0.00035389 | 0.0053694 | 0.0011593 | 0.00052473 | 0.0003783 | 2.5627e-05 | 0.04365 | 0.040833 | 0.61954 | 0.13376 | 0.060546 | 0.04365 | 0.0029569
Aux. Services Cold Storage | Kohler | 201.15 | 1408050 | 150 | 1.4081 | 3.5 | 4.9282 | 0.00076387 | 0.00071459 | 0.010842 | 0.0023409 | 0.0010596 | 0.00076387 | 5.1746e-05 | 0.065474 | 0.06125 | 0.92931 | 0.20065 | 0.090819 | 0.065474 | 0.0044354
Mullins | Kohler | 402.3 | 2816100 | 300 | 2.8161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13095 | 0.1225 | 1.8586 | 0.40129 | 0.18164 | 0.13095 | 0.0088707
Integrative Learning Center | Kohler | 268.2 | 1877400 | 200 | 1.8774 | 10.1 | 18.9617 | 0.0029391 | 0.0027495 | 0.041716 | 0.0090068 | 0.0040768 | 0.0029391 | 0.0001991 | 0.087299 | 0.081667 | 1.2391 | 0.26753 | 0.12109 | 0.087299 | 0.0059138
Performance Center (McGuirk) | Kohler | 241.38 | 1689660 | 180 | 1.6897 | 35.8 | 60.4898 | 0.0093759 | 0.008771 | 0.13308 | 0.028733 | 0.013005 | 0.0093759 | 0.00063514 | 0.078569 | 0.0735 | 1.1152 | 0.24078 | 0.10898 | 0.078569 | 0.0053224
|  |  |  | Group 5 Total: | 24.0696 | 93.3 | 167.7084 | 0.025995 | 0.024318 | 0.36896 | 0.079661 | 0.036057 | 0.025995 | 0.0017609 | 1.1192 | 1.047 | 15.8859 | 3.4299 | 1.5525 | 1.1192 | 0.075819
[5 empty] | 173.1626 | gal/hr | 1206.5352
GROUP 6 - DIESEL
Brown house | Kohler | 241.38 | 1689660 | 180 | 1.6897 | 3.4 | 5.7448 | 0.00089045 | 0.000833 | 0.012639 | 0.0027288 | 0.0012351 | 0.00089045 | 6.0321e-05 | 0.078569 | 0.0735 | 1.1152 | 0.24078 | 0.10898 | 0.078569 | 0.0053224
Cance house | Kohler | 46.935 | 328545 | 35 | 0.32854 | 17.8 | 5.8481 | 0.00090646 | 0.00084797 | 0.012866 | 0.0027778 | 0.0012573 | 0.00090646 | 6.1405e-05 | 0.015277 | 0.014292 | 0.21684 | 0.046818 | 0.021191 | 0.015277 | 0.0010349
Cashin house | Kohler | 268.2 | 1877400 | 200 | 1.8774 | 2.8 | 5.2567 | 0.00081479 | 0.00076222 | 0.011565 | 0.0024969 | 0.0011302 | 0.00081479 | 5.5196e-05 | 0.087299 | 0.081667 | 1.2391 | 0.26753 | 0.12109 | 0.087299 | 0.0059138
Crampton house | Cummins | 20.115 | 140805 | 15 | 0.14081 | 2.9 | 0.40833 | 6.3292e-05 | 5.9209e-05 | 0.00089834 | 0.00019396 | 8.7792e-05 | 6.3292e-05 | 4.2875e-06 | 0.0065474 | 0.006125 | 0.092931 | 0.020065 | 0.0090819 | 0.0065474 | 0.00044354
Fine arts | Cummins | 268.2 | 1877400 | 200 | 1.8774 | 2.3 | 4.318 | 0.00066929 | 0.00062611 | 0.0094996 | 0.0020511 | 0.00092837 | 0.00066929 | 4.5339e-05 | 0.087299 | 0.081667 | 1.2391 | 0.26753 | 0.12109 | 0.087299 | 0.0059138
Gorman | Kohler | 201.15 | 1408050 | 150 | 1.4081 | 4.1 | 5.773 | 0.00089482 | 0.00083709 | 0.012701 | 0.0027422 | 0.0012412 | 0.00089482 | 6.0617e-05 | 0.065474 | 0.06125 | 0.92931 | 0.20065 | 0.090819 | 0.065474 | 0.0044354
McNamara house | Kohler | 268.2 | 1877400 | 200 | 1.8774 | 5.5 | 10.3257 | 0.0016005 | 0.0014972 | 0.022717 | 0.0049047 | 0.00222 | 0.0016005 | 0.00010842 | 0.087299 | 0.081667 | 1.2391 | 0.26753 | 0.12109 | 0.087299 | 0.0059138
Moore house | Kohler | 46.935 | 328545 | 35 | 0.32854 | 2.9 | 0.95278 | 0.00014768 | 0.00013815 | 0.0020961 | 0.00045257 | 0.00020485 | 0.00014768 | 1.0004e-05 | 0.015277 | 0.014292 | 0.21684 | 0.046818 | 0.021191 | 0.015277 | 0.0010349
Rec Center | Kohler | 80.46 | 563220 | 60 | 0.56322 | 1.6 | 0.90115 | 0.00013968 | 0.00013067 | 0.0019825 | 0.00042805 | 0.00019375 | 0.00013968 | 9.4621e-06 | 0.02619 | 0.0245 | 0.37173 | 0.080259 | 0.036328 | 0.02619 | 0.0017741
Pierpont house | Cummins | 26.82 | 187740 | 20 | 0.18774 | 12.1 | 2.2717 | 0.00035211 | 0.00032939 | 0.0049976 | 0.001079 | 0.00048841 | 0.00035211 | 2.3852e-05 | 0.0087299 | 0.0081667 | 0.12391 | 0.026753 | 0.012109 | 0.0087299 | 0.00059138
Prince house | Onan | 20.115 | 140805 | 15 | 0.14081 | 3.4 | 0.47874 | 7.4204e-05 | 6.9417e-05 | 0.0010532 | 0.0002274 | 0.00010293 | 7.4204e-05 | 5.0267e-06 | 0.0065474 | 0.006125 | 0.092931 | 0.020065 | 0.0090819 | 0.0065474 | 0.00044354
Stockbridge Hall | Kohler | 134.1 | 938700 | 100 | 0.9387 | 4.1 | 3.8487 | 0.00059654 | 0.00055806 | 0.0084671 | 0.0018281 | 0.00082746 | 0.00059654 | 4.0411e-05 | 0.04365 | 0.040833 | 0.61954 | 0.13376 | 0.060546 | 0.04365 | 0.0029569
Thoreau - NEW | Onan | 8.046 | 56322 | 6 | 0.056322 | 8.5 | 0.47874 | 7.4204e-05 | 6.9417e-05 | 0.0010532 | 0.0002274 | 0.00010293 | 7.4204e-05 | 5.0267e-06 | 0.002619 | 0.00245 | 0.037173 | 0.0080259 | 0.0036328 | 0.002619 | 0.00017741
Tobin | Onan | 40.23 | 281610 | 30 | 0.28161 | 1 | 0.28161 | 4.365e-05 | 4.0833e-05 | 0.00061954 | 0.00013376 | 6.0546e-05 | 4.365e-05 | 2.9569e-06 | 0.013095 | 0.01225 | 0.18586 | 0.040129 | 0.018164 | 0.013095 | 0.00088707
Van Meter | Cummings | 201.15 | 1408050 | 150 | 1.4081 | 3.8 | 5.3506 | 0.00082934 | 0.00077584 | 0.011771 | 0.0025415 | 0.0011504 | 0.00082934 | 5.6181e-05 | 0.065474 | 0.06125 | 0.92931 | 0.20065 | 0.090819 | 0.065474 | 0.0044354
D North - Housing Bldg. North Dorm | Cummins | 402.3 | 2816100 | 300 | 2.8161 | 3.2 | 9.0115 | 0.0013968 | 0.0013067 | 0.019825 | 0.0042805 | 0.0019375 | 0.0013968 | 9.4621e-05 | 0.13095 | 0.1225 | 1.8586 | 0.40129 | 0.18164 | 0.13095 | 0.0088707
Brett Hall | Kohler | 268.2 | 1877400 | 200 | 1.8774 | 8.7 | 16.3334 | 0.0025317 | 0.0023683 | 0.035933 | 0.0077584 | 0.0035117 | 0.0025317 | 0.0001715 | 0.087299 | 0.081667 | 1.2391 | 0.26753 | 0.12109 | 0.087299 | 0.0059138
Paige | Kohler | 134.1 | 938700 | 100 | 0.9387 | 3.6 | 3.3793 | 0.00052379 | 0.00049 | 0.0074345 | 0.0016052 | 0.00072655 | 0.00052379 | 3.5483e-05 | 0.04365 | 0.040833 | 0.61954 | 0.13376 | 0.060546 | 0.04365 | 0.0029569
|  |  |  | Group 6 Total: | 18.7365 | 91.7 | 80.9629 | 0.012549 | 0.01174 | 0.17812 | 0.038457 | 0.017407 | 0.012549 | 0.00085011 | 0.87125 | 0.81504 | 12.3661 | 2.6699 | 1.2085 | 0.87125 | 0.05902
[5 empty] | 134.7946 | gal/hr | 582.4667
Group 8 - DIESEL
Lincoln Campus Center Parking | Kohler | 757.665 | 5303655 | 565 | 5.3037 | 7.5 | 39.7774 | 0.0061655 | 0.0057677 | 0.08751 | 0.018894 | 0.0085521 | 0.0061655 | 0.00041766 | 0.24662 | 0.23071 | 3.5004 | 0.75577 | 0.34209 | 0.24662 | 0.016707
|  |  |  | Group 8 Total: | 5.3037 | 7.5 | 39.7774 | 0.0061655 | 0.0057677 | 0.08751 | 0.018894 | 0.0085521 | 0.0061655 | 0.00041766 | 0.24662 | 0.23071 | 3.5004 | 0.75577 | 0.34209 | 0.24662 | 0.016707
[5 empty] | 38.1558 | gal/hr | 286.1684
Group 9 - DIESEL
Life Sciences - 1 | Cummins | 1743.3 | 12203100 | 1300 | 12.2031 | 8.2 | 100.0654 | 0.01551 | 0.014509 | 0.22014 | 0.047531 | 0.021514 | 0.01551 | 0.0010507 | 0.56744 | 0.53083 | 8.054 | 1.7389 | 0.7871 | 0.56744 | 0.03844
Life Sciences - 2 | Cummins | 1743.3 | 12203100 | 1300 | 12.2031 | 3.5 | 42.7109 | 0.0066202 | 0.0061931 | 0.093964 | 0.020288 | 0.0091828 | 0.0066202 | 0.00044846 | 0.56744 | 0.53083 | 8.054 | 1.7389 | 0.7871 | 0.56744 | 0.03844
|  |  |  | Group 9 Total: | 24.4062 | 11.7 | 142.7763 | 0.02213 | 0.020703 | 0.31411 | 0.067819 | 0.030697 | 0.02213 | 0.0014992 | 1.1349 | 1.0617 | 16.1081 | 3.4779 | 1.5742 | 1.1349 | 0.07688
[5 empty] | 175.5842 | gal/hr | 1027.1674
Note: Potential emissions are based on the 300 hours, in accordance with MassDEP guidance
Emission Factors
(Manufact. Test data)
pollutant | lb/MMBtu | lb/1000 gal
PM | 0.31 | 43.09
SOx | 0.29 | 40.31
NOx | 4.4 | 611.6
CO | 0.95 | 132.05
VOC | 0.43 | 59.77
PM2.5 | 0.31 | 43.09
NH3 | 0.021 | 2.919
NOTE: | BHP=kW/0.746
Inlet HP = Outlet HP/0.9

## NG, Diesel and Propane totals
UMass Dining Common and Misc Small Source NG Fuel Use - 2018
Data correct, need to check links
Location | Total CY 18 (Supply Therm Units) | Dining Common | Misc. Small Sources - Space Heating | Small Boiler Calcs
151 Southwest - Emerson Dorm | 5.2 |  | 5.2
Admissions- 37 Mather | 15849.6 |  | 15849.6
640 Mass. Ave - Thoreau Dorm | 6.2 |  | 6.2
650 Mass. Ave - Melville Dorm | 5.2 |  | 5.2
660 Mass. Ave - James Dorm | 4.2 |  | 4.2
BOWDITCH GREENHOUSE 211 NATURAL RESOURCES RD | 16.6 |  | 16.6
UMASS Police - 585 East Pleasant Street | 1180.5 |  | 1180.5
Berkshire Dining -121 Southwest | 27282.6 | 27282.6
Boyden Gym - 131 Commonwealth Ave | 1872.4 |  | 1872.4
Studio Arts - 110 Thatcher Rd | 0 |  | 0
Chiller Facility - 191 Governor's Dr | 5157.18 |  | 5157.18
COMM DISORDERS - 358 N Pleasant | 8212.3 |  | 8212.3
Copper Kettle, Franklin - 260 Stockbridge Rd | 15086.4 | 15086.4
Dubois Library - 154 Hicks Way | 36.1 |  | 36.1
ECSC #2, Eng. Comp Sci Complex - 140 Governors Dr | 1 |  | 1
Emergency Generator - 150 Infirmary Way | 0 |  | 0
Furcolo Hall - 813 N Pleasant St (small boiler calcs) | 52032.8 |  |  | 52032.8
Grad Research Ctr - 740 N Pleasant | 1600.6 |  | 1600.6
GREENHOUSE # 146 203 NATURAL RESOURCES RD | 7451.4 |  | 7451.4
GREENHOUSE # 548 203 NATURAL RESOURCES RD | 4434.1 |  | 4434.1
Hampden Dining - 131 Southwest Cir | 22516.5 | 22516.5
Hampshire Dining - 141 Southwest Cir | 36645.6 | 36645.6
Hasbrouck Hall Left - 666 N Pleasant | 1 |  | 1
Hasbrouck Hall Right - 666 N Pleasant | 1 |  | 1
Health Center - 150 Infirmary Way | 0 |  | 0
Integrated Science 661 Pleasant St. | 26.8 |  | 26.8
IPF Tillson | 22337.8 |  | 22337.8
240 Thatcher Way- Lab Science | 86.6 |  | 86.6
Lincoln Campus Center | 31876.6 |  | 31876.6
McGuirk Stadium (Small boiler calcs) | 44527.9 |  |  | 44527.9
Patterson Dorm - 204 Sunset Ave | 3.9 |  | 3.9
Student Union - 41 Campus Ctr Way | 8537.6 |  | 8537.6
151 Tillson Farm Rd | 1468.9 |  | 1468.9
386 Tillson Farm Rd | 7580.8 |  | 7580.8
Tillson Station - 110 Tillson Farm Rd | 8101 |  | 8101
Transit Garage (small boilers - NG) | 4665 |  |  | 4665
Worcester Dining - 669 N Pleasant | 14522 | 14522
911 N.Pleasant St., Wysocki House (small boiler calcs) | 1506 |  |  | 1506
RTIC Furnaces (from Berkshire Gas) | 23076 |  |  | 23076
Total | 367715.38 | 116053.1 | 125854.58 | 125807.7
Total CF
RTIC Furnaces Total Use (from Berkshire Gas) = | 4665 | therm | See worksheet, "Berkshire Gas RTIC and UMTS"
UMTS Boiler Total Use (from Berkshire Gas) = | 23076 | therm
#2 Fuel Oil UMass - Amherst
Listing from "Nat Gas-Propane-Oil Amherst-Calendar Yr 2018.xls"
111 N. MAPLE ST. HADLEY | - | offsite
23 TILSON FARM RD | 852.7 | Tilson Farm
31 Club House Road - Bowditch Lodge | 2090.8 | Bowdich House
41 Club House Rd - Farley Lodge | 1507.3 | Farley Lodge
513 E PLEASANT ST | 0 | UMA Dorm
650 East Pleasant Street | 900 | UMA Dorm
93 Fearing Street | 1907.5 | Fearing Street Boiler
Emergency Generator - 150 Infirmary Way | 2217.6
758 N. Pleasant - Holocaust Memorial | 1539.5
Propane Gas UMass - Amherst
Listing from "Nat Gas-Propane-Oil Amherst-Calendar Yr 2018.xls"
Amherst | 17705.1
101 Commonwealth Ave ROTC | 12
128 Tillson Farm Rd (Formerly 386) | 34.4
31 Cold Storage Dr. | 6159.3
650 East Pleasant Street | 62.7
809 N Pleasant St Montague HSE | 3019.5
990 N.PLEASANT ST North Village | 31.4
Chancellors' House | 882.2
Chenoweth Lab - 100 Holdsworth | 114.6
Fernald Hall 270 Stockbridge Rd | 12.2
Goessman Lab - 686 N Pleasant | 51.8
Morrill Science #3 | 34.2
Morrill Science #4 | 129.9
Morrill Science #5 | 10
Tillson Farm | 1033.2
Tillson Farm Coal Pile | 2915.1
Tillson Farm Power Plant | 1310.1
Tillson Farm Water Treatment | 1892.5
Hadley | 13054.8
111 N Maple St, HORSE BARN | 6416 | offsite
Hadley Farm Alpaca Barn | 492.7 | offsite
Hadley Farm Livestock Barn | 1691.2 | offsite
Hadley Farm Police Barn | 2303 | offsite
Hadley Farm Riding Arena | 2151.9 | offsite
Power Plant | 5.9
200 Mullins Way CHP | 5.9 | offsite
South Deerfield | 9699.8
Dairy Farm - 91 River Rd | 4174.1 | offsite
Tractor Barn | 2301.5 | offsite
Turf Research - 23 River Rd | 3224.2 | offsite
Grand Total | 40465.6
UMASS/TILSON FARM/ANIM HSE | 0 | offsite
| 80949.7 | total gallons propane (onsite use only)

## Space Heaters
UMASS - Amherst | [6 empty] | UMASS - Amherst
2018 Natural Gas Space Heaters Emissions | [6 empty] | 2018 Propane Space Heaters Emissions
| Various Space Heaters (approx 24 units) - see listing on NG, Diesel and Propane total sheet | [6 empty] | Various Space Heaters (approx 24 units) - see listing on NG, Diesel and Propane total sheet
| Assume conservative rating of 1 MMBtu/hr per unit, 24 units | [5 empty] | Assume conservative rating of 1 MMBtu/hr per unit, 23 units
| Potential Fuel Use = | 210240 | MMBtu/yr (based on 8760 hr/yr, 24 units, 1 MMBtu/hr each) |  |  |  | Potential Fuel Use = | 201480 | MMBtu/yr (based on 8760 hr/yr, 23 units, 1 MMBtu/hr each)
|  | 204.1165 | MMCF/yr (potential) |  |  |  |  | 2206.0659 | 1000 gal/yr (potential)
| 2018 Annual Fuel Use = | 125854.58 | therm/yr |  |  |  | 2018 Annual Fuel Use = | 17705.1 | gal/yr |  |  |  | 91330 | btu/gal
|  | 12585.458 | MMBtu/yr |  |  |  |  | 17.7051 | 1000 gal/yr |  |  |  | 0.026 | % S (260 ppm, based on range of 50 and 259 ppm.)
|  | 12.2189 | MMCF | [10 empty] | %
| Emission Factor Basis, AP-42 Section 1.4, Boilers < 100 MMBtu/hr | [5 empty] | Emission Factor Basis, AP-42 Section 1.5 LPG Combustion. Table 1.5-1, Commercial Boilers (SCC 1-03-010-02)
12.2189
| Pollutant | 0 | Actual Emissions (lb/yr) | Actual Emissions (tpy) | Potential Emissions (lb/yr) | Potential Emissions (tpy) | Pollutant | Emission Factor (lb/1000 gal) | Actual Emissions (lb/yr) | Actual Emissions (tpy) | Potential Emissions (lb/yr) | Potential Emissions (tpy)
| NOx | 100 | 1221.8891 | 0.61094 | 20411.6505 | 10.2058 | NOx | 13 | 230.1663 | 0.11508 | 28678.8569 | 14.3394
| SO2 | 0.6 | 7.3313 | 0.0036657 | 122.4699 | 0.061235 | SO2 | 0.0026 | 0.046033 | 2.3017e-05 | 5.7358 | 0.0028679
| CO | 84 | 1026.3869 | 0.51319 | 17145.7864 | 8.5729 | CO | 7.5 | 132.7882 | 0.066394 | 16545.4944 | 8.2727
| PM | 1.9 | 23.2159 | 0.011608 | 387.8214 | 0.19391 | PM | 0.2 | 3.541 | 0.0017705 | 441.2132 | 0.22061
| PM10 | 1.9 | 23.2159 | 0.011608 | 387.8214 | 0.19391 | PM10 | 0.2 | 3.541 | 0.0017705 | 441.2132 | 0.22061
| PM2.5 | 1.9 | 23.2159 | 0.011608 | 387.8214 | 0.19391 | PM2.5 | 0.2 | 3.541 | 0.0017705 | 441.2132 | 0.22061
| NMTOC | 5.5 | 67.2039 | 0.033602 | 1122.6408 | 0.56132 | NMTOC | 1 | 17.7051 | 0.0088525 | 2206.0659 | 1.103
| NH3 | 0.49 | 5.9873 | 0.0029936 | 100.0171 | 0.050009 | NH3 | -- | -- | -- | -- | --
|  | rating | 0.023415 | MMCF/hr
|  | hr/day | 12
|  | day/wk | 7
|  | wk/yr | 20

## EGenerator Raw Data
UMASS - AMHERST
Emergency Generator Raw Data - 2018
from Emergency Generator Run Times.xls
Generator | Asset Number | Fuel | Manufacturer | Output kW | 2018 Start | 2018 End | Elapsed time (hrs)
Animal Care | EG0653-049 | Diesel | Kohler | 350 | 68.6 | 70.3 | 1.7
Auxiliary Services Cold Storage | 605EG-001 | Diesel | Kohler | 150 | 30.1 | 33.6 | 3.5
Berkshire House | EG0007-001 | Diesel | Cummins | 80 | 37.9 | 44.9 | 7
Brett Hall | EG0295 | Diesel | Kohler | 200 | 18.1 | 26.8 | 8.7
Brooks Hall-Node 4 |  | Diesel | Caterpillar | 125 | 167 | 177 | 10
Brown house | EG0426-028 | Diesel | Kohler | 180 | 26.6 | 30 | 3.4
Bus Garage | 546EG-002 | Diesel | Kohler | 100 | 245.5 | 247.7 | 2.2
Cance house | EG0400-022 | Diesel | Kohler | 35 | 55 | 72.8 | 17.8
Cashin house | EG0427-027 | Diesel | Kohler | 200 | 28.6 | 31.4 | 2.8
Chancellor | 057EG-001 | Diesel | Caterpillar | 37.1 | 11.4 | 11.4 | 0
CHP Blackstart |  | Diesel
Comp. Science Bldg. | EG0651-041 | Diesel | Kohler | 75 | 0 | 8 | 8
Conte Polymer Ctr | EG0614-040 | Diesel | Caterpillar | 1000 | 231 | 234 | 3
Coolidge house | EG0353-014 | Diesel | Cummins | 115 | 497.5 | 502.1 | 4.6
Crampton house | EG0380-006 | Diesel | Onan | 15 | 161.2 | 164.1 | 2.9
Dickinson #2 | EG0132-001 | Diesel | Caterpillar | 111 | 87 | 89 | 2
Draper | EG0087-001 | Diesel | Kohler | 100 | 14.9 | 17.5 | 2.6
Dubois Library | EG0417-034 | Diesel | Caterpillar | 250 | 17.2 | 24.2 | 7
Engineering Lab II | EG0657-043 | Diesel | Caterpillar | 500 | 147 | 151 | 4
Fine arts | EG0420-036 | Diesel | Cummins | 200 | 83.4 | 85.7 | 2.3
Goessmann | EG0081-001 | Diesel | Cummings | 400 | 14.5 | 18.6 | 4.1
Gorman House | 294EG0-001 | Diesel | Kohler | 150 | 7 | 11.1 | 4.1
Grounds Maintenance (Tilson) | 684EG-001 | Diesel | Kohler | 100 | 81.2 | 93.5 | 12.3
Honors College | 711EG-001 | Diesel | Caterpillar | 800 | 89.5 | 97.8 | 8.3
Housing Bldg. North Dorm | EG0673-046 | Diesel | Cummings | 300 | 110.4 | 113.6 | 3.2
Integrative Learning Center | 704EG-001 | Diesel | Kohler | 200 | 16 | 26.1 | 10.1
ISB | 676-FOTT-1.1 | Diesel | Caterpillar | 800 | 94.6 | 100 | 5.4
John Adams house | EG0354-011 | Diesel | Cummins | 125 | 490.2 | removed
John Quincy Adams | EG0355-010 | Diesel | Cummins | 125 | 505.5 | 509.2 | 3.7
Kennedy house | EG0352-013 | Diesel | Onan | 115 | 533 | 543.1 | 10.1
Lederle (LGRC)-Node 5 |  | Diesel | Caterpillar | 250 | 166 | 171 | 5
Life Science Labs 1 | 694GEN-001 | Diesel | Cummins | 1500 | 90.5 | 98.7 | 8.2
Life Science Labs 2 | 694GEN-002 | Diesel | Cummins | 1500 | 62.4 | 65.9 | 3.5
Lincoln Campus Ctr Parking | EG0413-025 | Diesel | Kohler | 565 | 312.6 | 320.1 | 7.5
McNamara house | EG0428-029 | Diesel | Kohler | 200 | 25.7 | 31.2 | 5.5
Moore house | EG0402-023 | Diesel | Kohler | 35 | 46.7 | 49.6 | 2.9
Morrill (Public Health) | EG126-1 | Diesel | John Deere | 250 | 83.6 | 89.4 | 5.8
Mullins |  | Diesel | Kohler | 500 |  |  | 0
North village |  | Diesel | Off-site
Paige Lab | 120EG-1 | Diesel | Kohler | 100 | 14.2 | 17.8 | 3.6
Performance Center (McGuirk) | 716EG-001 | Diesel | Kohler | 180 | 121 | 156.8 | 35.8
Physical Plant | EG0170-056 | Diesel | Caterpillar | 80 | 34 | 36.5 | 2.5
Pierpont house | EG0401-024 | Diesel | Cummins | 20 | 123.5 | 135.6 | 12.1
Prince house | EG0381-009 | Diesel | Onan | 15 | 14.5 | 17.9 | 3.4
Recreation Building | 678EG-001 | Diesel | Kohler | 60 | 66.4 | 68 | 1.6
Skinner Hall | 128-EG-1 | Diesel | Cummins | 247 | 66 | 67.1 | 1.1
SOM Addition | EG0655-000 | Diesel | Kohler | 510 | 215.9 | 223.1 | 7.2
Southwest-Node 2 |  | Diesel | Caterpillar | 125 | 220 | 225 | 5
Stockbridge Hall | EG0130-032 | Diesel | Kohler | 100 | 35.5 | 39.6 | 4.1
Sylvan-Node 6 |  | Diesel | Caterpillar | 125 | 146 | 151 | 5
Thoreau house new unit 4/2018 | EG0348-017 | Diesel | Onan | 6 | 20.8 | 29.3 | 8.5
Tobin | EG0415-033 | Diesel | Onan | 30 | 494.8 | 495.8 | 1
Totman Physical Ed. | EG0123-030 | Diesel | Onan | 350 | 12.1 | 16.2 | 4.1
UMPD | 693EG-001 | Diesel | Cummins | 500 | 48.5 | 54.6 | 6.1
Van Meter | EG0032-045 | Diesel | Cummings | 150 | 140.6 | 144.4 | 3.8
Washington house | EG0356.012 | Diesel | Cummins | 125 | 563.4 | 565.3 | 1.9
Webster House (orchard hill) | EG0333-001 | Diesel | Caterpillar | 350 | 347 | 355 | 8
Bus Garage | 546EG-001 | NG | Kohler | 63 | 284.3 | 312.5 | 28.2
CNS Greenhouse (Bowditch) | 701EG-1 | NG | Generac | 150 | 54.5 | 57.4 | 2.9
Dubois Library (Node 1) | EG0417-034 | NG | Caterpillar | 250 | 190 | 193 | 3
Franklin Dining Hall | EG0334-002 | NG | Onan | 10 | 214.7 | 218.9 | 4.2
Hampden dining Hall | EG0382-015 | NG | Onan | 12.5 | 210.4 | 213 | 2.6
Lederle LGRC | EG0412-035 | NG | Onan | 1 | 230 | 231 | 1
Patterson house | EG0378-008 | NG | Kohler | 30 | 8 | 50.2 | 42.2
McGuirk Stadium | EG0345-001 | NG | Generac | 200 | 83.7 | 93.1 | 9.4
University Health Ctr | EG0291-001 | NG | Waukesha | 100 | 52 | 128.3 | 76.3
North Village | EG0477-001 | Propane | Off-site
James house | EG0350-019 | NG | Onan | 25 |  |  | 0
Melville house | EG0349-018 | NG | Onan | 25 | 23 | 23.7 | 0.7
Emerson house | EG0351-020 | NG | Cummins | 25 | 21.3 | 21.7 | 0.4

## Berskhire Gas - RTIC and UMTS
Berkshire Gas Data - 2018 (email from Gary Ritter, 3/14/19)
257 Governors Way, Bus Garage - | 23076 | therms | Transit Building 681 | 4665 | therms

## PVTA UMA Bus Fleet
2018 Annual Usage / Thruput
UMass Transit Services - Maintenance Department
Product | Thruput | Units
Parts Solvent Purchased |  | gallons
Parts Solvent Discarded |  | gallons
15W-40 Motor Oil (2 tanks) |  | gallons
Antifreeze/Coolant |  | gallons
Hydraulic Fluid |  | gallons
R-134A Refrigerant |  | pounds