## Compatibility Report
Compatibility Report for Total energy.xls
Run on 2/16/2012 14:31
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 7

## Total Energy adj sq ft
Total Energy
Fiscal Year | Cogen electricity, kWh | Purchased, kWh | Total electricity, kWh | Solar Renewable, kWh | Purchased Elect, MMBtu | Plant Gas meters, MMBtu* | Plant Gas bills MMBtu## | % Difference b/n plant gas and billed plant gas | Diesel oil, gal | Diesel oil, MMBtu | Building Gas (w/o plant), MMBtu |  | Nonrenewable energy, MMBtu | Total campus energy use, MMBtu | GSF original | Total campus energy use, MMBtu | GSF# | Total kBtu per square foot | Total EUI MWh/year/GSF | MWh electricity per square feet | Gas to Cogen electricity MMBtu/KWh | Cooling degree days^ | Heating degree days^ | % change in energy use from 2004 | % change in GSF from 2004 | % change in EUI from 2004 | Total Btu per sq ft per HDD | Total kBtu per sq ft per CDD | Savings per sq ft per HDD vs 2004 | % change in energy use from 2008 | % change in EUI from 2008
2004 | 262145457 | 66316242 | 328461699 |  | 226271.0177 | 3823671 | 3733098.663 | 2.369% | 73417 | 10131.546 | 73436 |  | 4042937.2267 | 4133509.5637 | 14063190 | 4042937.2267 | 13160015 | 307.2137 | 0.090039 | 0.024959 | 0.014241 | 946.7 | 5754.2 | 0 | 0 | 0 | 53.3895 | 0.32451 | 0% | 0 | 0
2005 | 239502234 | 80040349 | 319542583 |  | 273097.6708 | 3495919 | 3411481 | 2.415% | 64869 | 8951.922 | 70689 |  | 3764219.5928 | 3848657.5928 | 14431675 | 3764219.5928 | 13133404 | 286.6142 | 0.084002 | 0.024331 | 0.014244 | 959 | 5568.7 | 6.894% | -0.2022% | 6.705% | 51.4688 | 0.29887 | 3.598% | 0% | 0%
2006 | 174148396 | 137306802 | 311455198 |  | 468490.8084 | 2961686 | 3037415 | -2.557% | 16583 | 2288.454 | 54825 |  | 3563019.2624 | 3487290.2624 | 14501696 | 3563019.2624 | 13367829 | 266.5369 | 0.078117 | 0.023299 | 0.017442 | 1251.8 | 5496.1 | 11.87% | 1.579% | 13.24% | 48.4956 | 0.21292 | 9.166% | 0% | 0%
2007 | 222191264 | 118607943 | 340799207 |  | 404690.3015 | 3267894 | 3236113 | 0.9725% | 37359 | 5155.542 | 47724 |  | 3693682.8435 | 3725463.8435 | 14888519.87 | 3693682.8435 | 13728959 | 269.0432 | 0.078852 | 0.024823 | 0.014565 | 1155.9 | 5624.1 | 8.639% | 4.323% | 12.42% | 47.8376 | 0.23276 | 10.4% | 0% | 0%
2008 | 186085556 | 141261073 | 327346629 |  | 481982.7811 | 3257287 | 3190944 | 2.037% | 27846 | 3842.748 | 65296 |  | 3742065.5291 | 3808408.5291 | 14692023 | 3742065.5291 | 14437363 | 259.1931 | 0.075965 | 0.022674 | 0.017148 | 1085.6 | 6025 | 7.442% | 9.706% | 15.63% | 43.0196 | 0.23876 | 19.42% | 0% | 0%
2009 | 161143518 | 176681127 | 337824645 |  | 602836.0053 | 3156244 | 2960088 | 6.215% | 14789 | 2040.882 | 59946.1 |  | 3624910.9873 | 3821066.9873 | 14655095 | 3624910.9873 | 14400435 | 251.7223 | 0.073776 | 0.023459 | 0.018369 | 910.2 | 6276.4 | 10.34% | 9.426% | 18.06% | 40.1062 | 0.27656 | 24.88% | 3.131% | 2.882%
2010 | 136774662 | 179245671 | 316020333 | 30400 | 611586.2295 | 2783831.161 | 2755406 | 1.021% | 1153 | 159.114 | 49005.1216 |  | 3416156.4651 | 3444581.6261 | 14641390 | 3416260.1899 | 14386730 | 237.4591 | 0.069595 | 0.021966 | 0.020146 | 825.7 | 5761.3 | 15.5% | 9.322% | 22.71% | 41.2162 | 0.28759 | 22.8% | 8.707% | 8.385%
2011 | 139014807 | 176034726 | 315049533 | 60683 | 600630.4851 |  | 2909118.95 |  | 10022 | 1383.036 | 40212.6033 |  | 3551345.0744 |  |  | 3551552.1248 | 14386730 | 246.8631 | 0.072351 | 0.021899 | 0.020927 | 1200 | 6021.5 | 12.15% | 9.322% | 19.64% | 40.9969 | 0.20572 | 23.21% | 5.091% | 4.757%
2012 | 142295453 | 174428914 | 316724367 | 112357 | 595151.4546 |  | 2683538.94 |  | 9178 | 1266.564 | 36826.72 |  | 3316783.6786 |  |  | 3317167.0407 | 14390330 | 230.5136 | 0.06756 | 0.02201 | 0.018859 | 1346.3 | 4768.3 | 17.95% | 9.349% | 24.97% | 48.3429 | 0.17122 | 9.452% | 11.35% | 11.06%
2013 | 106325317 | 204835356 | 311160673 | 128454.2 | 698898.2347 |  | 2670946.8 |  | 1287 | 177.606 | 44792.793 |  | 3414815.4337 |  |  | 3415253.7194 | 14392792 | 237.2892 | 0.069545 | 0.021619 | 0.025121 | 1256.7 | 5863.9 | 15.53% | 9.368% | 22.76% | 40.4661 | 0.18882 | 24.21% | 8.733% | 8.451%
2014 | 130430592 | 184154948 | 314585540 | 118447.1 | 628336.6826 |  | 2912203.055 |  | 7302 | 1007.676 | 50485.146 |  | 3592032.5596 |  |  | 3592436.7011 | 14516051 | 247.4803 | 0.072532 | 0.021672 | 0.022328 | 1149.5 | 6810 | 11.14% | 10.3% | 19.44% | 36.3407 | 0.21529 | 31.93% | 3.999% | 4.519%
2015 | 112708986 | 194549595 | 307258581 | 113836.9 | 663803.2181 |  | 2631063 |  | 6999 | 965.862 | 44203.5044 |  | 3340035.5845 |  |  | 3340423.996 | 14832105 | 225.2158 | 0.066007 | 0.020716 | 0.023344 | 958 | 6107.4 | 17.38% | 12.71% | 26.69% | 36.8759 | 0.23509 | 30.93% | 10.73% | 13.11%
2016 | 95852865 | 184664752 | 280517617 | 112429.07 | 630076.1338 |  | 2324377.298 |  | 6999 | 965.862 | 41712.5218 |  | 2997131.8156 |  |  | 2997515.4236 | 14841729 | 201.9654 | 0.059193 | 0.018901 | 0.024249 | 1258 | 4880 | 25.86% | 12.78% | 34.26% | 41.3863 | 0.16054 | 22.48% | 19.9% | 22.08%
2017 | 67617928 | 246508945 | 314126873 | 120288.74 | 841088.5203 |  | 2099662 |  | 6424 | 886.512 | 25284 |  | 2966921.0323 |  |  | 2967331.4575 | 14802873 | 200.4565 | 0.05875 | 0.021221 | 0.031052 | 1450 | 5126 | 26.6% | 12.48% | 34.75% | 39.1058 | 0.13825 | 26.75% | 20.7% | 22.66%
2018 | 78415798 | 225457617 | 303873415 | 121444 | 769261.3892 |  | 2310471 |  | 6411 | 884.718 | 53971 |  | 3134588.1072 |  |  | 3135002.4741 | 14802873 | 211.7834 | 0.06207 | 0.020528 | 0.029464 | 1174 | 5908 | 22.46% | 12.48% | 31.06% | 35.8469 |  | 32.86% | 16.22% | 18.29%
2019 | 127046498 | 177678835 | 304725333 | 97758 | 606240.185 |  | 2649147 |  | 22648 | 3125.424 | 66009.64 |  | 3324522.249 |  |  | 3324855.7993 | 15304485 | 217.2472 | 0.063671 | 0.019911 | 0.020852 | 1145 | 6243 | 17.76% | 16.3% | 29.28% | 34.7985 |  | 34.82% | 11.15% | 16.18%
2020 | 122198064 | 149762928 | 271960992 | 101749 | 510991.1103 |  | 2590434 |  | 21627 | 2984.526 | 17601 |  | 3122010.6363 |  |  | 3122357.8039 | 15142675 | 206.1959 | 0.060433 | 0.01796 | 0.021199 | 1228 | 5695 | 22.77% | 15.07% | 32.88% | 36.2065 |  | 32.18% | 16.56% | 20.45%
* From records provided by Utilities from metering at the equipment end of MMSCF x 1030 MMBtu/MMSCF
**Includes Lincoln and Grant Halls | [16 empty] | 254660 | Maxwell St. Parking lot
# From 2004 to 2005 there was a change in space accounting that reduced the overall GSF; from 2007 to 2008 there was a change in space accounting that increased the GSF; from 2009-2010 the SPHE was demolished | [16 empty] | 410.4252
## FY09 Dec through April amounts were reduced due to supercompressibility adjustments (complaint filed against Vendor 2/13/9)
^Source for Degree Days from FY04-FY15: http://www.ncdc.noaa.gov/cdo-web/datasets/GHCNDMS/stations/GHCND:USC00111577/detail FY2017 http://www.degreedays.net/ | [11 empty] | 0
for Degree days from FY2018 https://portfoliomanager.energystar.gov/pm/degreeDaysCalculator
1 kWh = | 0.003412 | MMBtu | 1 gal = | 0.138 | MMBtu
energy/sq. ft./degree day

## Carbon Calculator
|  | Co-gen Electricity | Co-gen Steam | Other On-Campus Stationary | Direct Transportation | Purchased Electricity | Total Energy Use | %change in energy use from 2004
| Total Energy MMBTU | MMBtu | MMBtu | MMBtu | MMBtu | MMBtu | Total Energy Use MMBtu | %change in energy use from 2004 | Cooling degree days^ | Heating degree days^ | GSF# | KMBTU/GSF | %change in energy use from 2004
2004 | 4719605.771 | 2021306.9916 | 1721961.6739 | 73436 | 23830.4265 | 226105.9327 | 4066641.0247 |  | 946.7 | 5754.2 | 13160015 | 358.6322
2005 | 4479562.3257 | 1760616.8836 | 1659849.8989 | 70689 | 23822.5244 | 272898.4216 | 3787876.7285 | 6.855% | 959 | 5568.7 | 13133404 | 341.0816 | 4.894%
2006 | 4337678.3092 | 1301255.4787 | 1738450.2822 | 54825 | 26892.6213 | 468149.0024 | 3589572.3847 | 11.73% | 1251.8 | 5496.1 | 13622489 | 318.4204 | 11.21%
2007 | 4478703.8681 | 1580065.7954 | 1661193.0797 | 47724 | 23750.6912 | 404395.0437 | 3717128.6101 | 8.595% | 1155.9 | 5624.1 | 13983619 | 320.2822 | 10.69%
2008 | 4550810.8761 | 1382312.8446 | 1812463.5388 | 65296 | 21743.1272 | 481631.1315 | 3763446.6421 | 7.456% | 1085.6 | 6025 | 14692023 | 309.7471 | 13.63%
2009 | 4392693.1615 | 1632525.6407 | 1329597.9812 | 59946.1 | 21425.4559 | 602396.1825 | 3645891.3603 | 10.35% | 910.2 | 6276.4 | 14655095 | 299.7383 | 16.42%
2010 | 4166589.7347 | 1447778.5811 | 1307785.709 | 49005.1216 | 21466.92 | 611140.0225 | 3437176.3542 | 15.48% | 825.7 | 5761.3 | 14641390 | 284.5761 | 20.65%
2011 | 4217816.7976 | 1540965.7483 | 1369531.4653 | 40212.6033 | 21184.2323 | 600192.2714 | 3572086.3206 | 12.16% | 1200 | 6021.5 | 14641390 | 288.0749 | 19.67%
2012 | 3990622.1056 | 1335522.6035 | 1349278.093 | 36826.7159 | 16944.65 | 594717.2383 | 3333289.3007 | 18.03% | 1346.3 | 4768.3 | 14644990 | 272.4906 | 24.02%
2013 | 4097149.5539 | 1120148.6367 | 1550975.0951 | 44792.793 | 19660.7797 | 698388.3258 | 3433965.6304 | 15.56% | 1256.7 | 5863.9 | 14647452 | 279.7176 | 22%
2014 | 4212273.9203 | 1376764.6246 | 1536442.1077 | 50485.146 | 19161.0914 | 627878.2547 | 3610731.2244 | 11.21% | 1149.5 | 6810 | 14770711 | 285.1775 | 20.48%
2015 | 3951412.1043 | 1186059.3396 | 1445966.6896 | 44203.5044 | 18188.6863 | 663318.9143 | 3357737.1342 | 17.43% | 958 | 6107.4 | 14832105 | 266.4094 | 25.72%
2016 | 3556893.3632 | 1016092.8288 | 1308698.7506 | 41712.5218 | 16419.1584 | 629616.4369 | 3012539.6965 | 25.92% | 1258 | 4880 | 14841729 | 239.6549 | 33.18%
[9 empty] | 1450 | 5126 | 14841729

## Total Water
Year | Water, MCF | Water, gal |  | MCF to 1000 Gallons
2013 | 93073 | 696186.04 |  | 7.48
2014 | 113795.6 | 851191.088
2015 | 67325.11 | 503591.8228
2016 | 100240.2406 | 749797
Thousands of gallons
| FY12 | FY13 | FY14 | FY15 | FY16 | % decrease
East | 165916.124 | 280537.9236 | 477086.2184 | 141860.818 |  | 0.14498
West | 439048.5484 | 415645.5732 | 376797.6696 | 362411.3856 |  | 0.17455
Total | 604964.6724 | 696183.4968 | 853883.888 | 504272.2036 | 749797 | 0.16644 | 100692.4688 | 768283.5369

## Total Energy (NE IL HDD CDD)
Total Energy
Fiscal Year | Cogen electricity, kWh | Purchased, kWh | Total electricity, kWh | Solar Renewable, kWh | Purchased Elect, MMBtu | Plant Gas meters, MMBtu* | Plant Gas bills MMBtu## | % Difference b/n plant gas and billed plant gas | Diesel oil, gal | Diesel oil, MMBtu | Building Gas (w/o plant), MMBtu | Geothermal, MMBtu | Nonrenewable energy, MMBtu | Total campus energy use, MMBtu | GSF original | Total campus energy use, MMBtu | GSF# | Total Btu per square foot | kwh per square feet | Gas to Cogen electricity | Cooling degree days | Heating degree days | % change in energy use from 2004 | % change in GSF from 2004
2004 | 262145457 | 66316242 | 328461699 |  | 226271.0177 | 3823671 | 3733098.663 | 2.369% | 73417 | 10131.546 | 73436 |  | 4049942.0177 | 4133509.5637 | 14063190 | 4042937.2267 | 13160015 | 314096.1134 | 24.9591 | 0.014586 | 782 | 6114 | 0 | 0
2005 | 239502234 | 80040349 | 319542583 |  | 273097.6708 | 3495919 | 3411481 | 2.415% | 64869 | 8951.922 | 70689 |  | 3769016.6708 | 3848657.5928 | 14431675 | 3764219.5928 | 13133404 | 293043.4176 | 24.3305 | 0.014597 | 762 | 5987 | 6.894% | -0.2022%
2006 | 174148396 | 137306802 | 311455198 |  | 468490.8084 | 2961686 | 3037415 | -2.557% | 16583 | 2288.454 | 54825 |  | 3430176.8084 | 3487290.2624 | 14501696 | 3563019.2624 | 13622489 | 255995.0874 | 22.8633 | 0.017007 | 941 | 5695 | 11.87% | 3.514%
2007 | 222191264 | 118607943 | 340799207 |  | 404690.3015 | 3267894 | 3236113 | 0.9725% | 37359 | 5155.542 | 47724 |  | 3672584.3015 | 3725463.8435 | 14888519.87 | 3693682.8435 | 13983619 | 266416.2863 | 24.3713 | 0.014708 | 907 | 6182 | 8.639% | 6.258%
2008 | 186085556 | 141261073 | 327346629 |  | 481982.7811 | 3257287 | 3190944 | 2.037% | 27846 | 3842.748 | 65296 | 0 | 3739269.7811 | 3808408.5291 | 14692023 | 3742065.5291 | 14692023 | 259216.0745 | 22.2806 | 0.017504 | 883 | 6562 | 7.442% | 11.64%
2009 | 161143518 | 176681127 | 337824645 |  | 602836.0053 | 3156244 | 2960088 | 6.215% | 14789 | 2040.882 | 59946.1 | 0 | 3759080.0053 | 3821066.9873 | 14655095 | 3624910.9873 | 14655095 | 260733.007 | 23.0517 | 0.019587 | 690 | 6908 | 10.34% | 11.36%
2010 | 136774662 | 179245671 | 316020333 | 30400 | 611586.2295 | 2783831.161 | 2755406 | 1.021% | 1153 | 159.114 | 49005.1216 | 2032 | 3395417.3905 | 3446613.6261 | 14641390 | 3416156.4651 | 14641390 | 235402.0777 | 21.584 | 0.020353 | 623 | 6300 | 15.5% | 11.26%
2011 | 139014807 | 176034726 | 315049533 | 60683 | 600630.4851 |  | 2909118.95 |  | 10022 | 1383.036 | 40212.6033 | 2378 | 3509749.4351 |  |  | 3551345.0744 | 14707886 | 241458.5668 | 21.4204 | #VALUE! | 939 | 6680 | 12.16% | 11.76%
2012 | 142295453 | 174428914 | 316724367 | 112357 | 595151.4546 |  | 2683538.94 |  | 9178 | 1266.564 | 36826.72 | 2814 |  |  |  | 3316783.6786 | 14707886 | 225510.5648 | 21.5343 |  | 1025 | 5170 | 17.96% | 11.76%
* From records provided by Utilities from metering at the equipment end of MMSCF x 1030 MMBtu/MMSCF | [13 empty] | 468810.8715 |  | Doesn’t include Geothermal
**Includes Lincoln and Grant Halls | [13 empty] | 0.13723
# From 2004 to 2005 there was a change in space accounting that reduced the overall GSF; from 2007 to 2008 there was a change in space accounting that increased the GSF; from 2009-2010 the SPHE was demolished
## FY09 Dec through April amounts were reduced due to supercompressibility adjustments (complaint filed against Vendor 2/13/9)
1 kWh = | 0.003412 | MMBtu | 1 gal = | 0.138 | MMBtu

## Total Energy (City Level)
Total Energy
Fiscal Year | Cogen electricity, kWh | Purchased, kWh | Total electricity, kWh | Solar Renewable, kWh | Purchased Elect, MMBtu | Plant Gas meters, MMBtu* | Plant Gas bills MMBtu## | % Difference b/n plant gas and billed plant gas | Diesel oil, gal | Diesel oil, MMBtu | Building Gas (w/o plant), MMBtu | Geothermal, MMBtu | Nonrenewable energy, MMBtu | Total campus energy use, MMBtu | GSF original | Total campus energy use, MMBtu | GSF# | Total kBtu per square foot | kwh per square feet | Gas to Cogen electricity | Cooling degree days^ | Heating degree days^ | % change in energy use from 2004 | % change in GSF from 2004 | Total Btu per sq ft per HDD | Total kBtu per sq ft per CDD | Savings per sq ft per HDD vs 2004
2004 | 262145457 | 66316242 | 328461699 |  | 226271.0177 | 3823671 | 3733098.663 | 2.369% | 73417 | 10131.546 | 73436 |  | 4049942.0177 | 4133509.5637 | 14063190 | 4042937.2267 | 13160015 | 307.2137 | 24.9591 | 0.014586 | 946.7 | 5754.2 | 0 | 0 | 53.3895 | 0.32451 | 0%
2005 | 239502234 | 80040349 | 319542583 |  | 273097.6708 | 3495919 | 3411481 | 2.415% | 64869 | 8951.922 | 70689 |  | 3769016.6708 | 3848657.5928 | 14431675 | 3764219.5928 | 13133404 | 286.6142 | 24.3305 | 0.014597 | 959 | 5568.7 | 6.894% | -0.2022% | 51.4688 | 0.29887 | 3.598%
2006 | 174148396 | 137306802 | 311455198 |  | 468490.8084 | 2961686 | 3037415 | -2.557% | 16583 | 2288.454 | 54825 |  | 3430176.8084 | 3487290.2624 | 14501696 | 3563019.2624 | 13622489 | 261.5542 | 22.8633 | 0.017442 | 1251.8 | 5496.1 | 11.87% | 3.514% | 47.5891 | 0.20894 | 10.86%
2007 | 222191264 | 118607943 | 340799207 |  | 404690.3015 | 3267894 | 3236113 | 0.9725% | 37359 | 5155.542 | 47724 |  | 3672584.3015 | 3725463.8435 | 14888519.87 | 3693682.8435 | 13983619 | 264.1436 | 24.3713 | 0.014565 | 1155.9 | 5624.1 | 8.639% | 6.258% | 46.9664 | 0.22852 | 12.03%
2008 | 186085556 | 141261073 | 327346629 |  | 481982.7811 | 3257287 | 3190944 | 2.037% | 27846 | 3842.748 | 65296 | 0 | 3739269.7811 | 3808408.5291 | 14692023 | 3742065.5291 | 14692023 | 254.7005 | 22.2806 | 0.017148 | 1085.6 | 6025 | 7.442% | 11.64% | 42.2739 | 0.23462 | 20.82%
2009 | 161143518 | 176681127 | 337824645 |  | 602836.0053 | 3156244 | 2960088 | 6.215% | 14789 | 2040.882 | 59946.1 | 0 | 3759080.0053 | 3821066.9873 | 14655095 | 3624910.9873 | 14655095 | 247.3482 | 23.0517 | 0.018369 | 910.2 | 6276.4 | 10.34% | 11.36% | 39.4092 | 0.27175 | 26.19%
2010 | 136774662 | 179245671 | 316020333 | 30400 | 611586.2295 | 2783831.161 | 2755406 | 1.021% | 1153 | 159.114 | 49005.1216 | 2032 | 3395417.3905 | 3446613.6261 | 14641390 | 3418188.4651 | 14641390 | 233.4607 | 21.584 | 0.020146 | 825.7 | 5761.3 | 15.45% | 11.26% | 40.5222 | 0.28274 | 24.1%
2011 | 139014807 | 176034726 | 315049533 | 60683 | 600630.4851 |  | 2909118.95 |  | 10022 | 1383.036 | 40212.6033 | 2242.9 | 3509749.4351 |  |  | 3553587.9744 | 14641390 | 242.7084 | 21.5177 | 0.020927 | 1200 | 6021.5 | 12.1% | 11.26% | 40.307 | 0.20226 | 24.5%
2012 | 142295453 | 174428914 | 316724367 | 112357 | 595151.4546 |  | 2683538.94 |  | 9178 | 1266.564 | 36826.72 | 2681.4001 | 3278690.3946 |  |  | 3319465.0786 | 14644990 | 226.6622 | 21.6268 | 0.018859 | 1346.3 | 4768.3 | 17.89% | 11.28% | 47.5352 | 0.16836 | 10.97%
2013 | 106325317 | 204835356 | 311160673 | 128454.2 | 698898.2347 |  | 2670946.8 |  | 1287 | 177.606 | 44792.793 | 2749.5004 | 3369845.0347 |  |  | 3417564.9341 | 14647452 | 233.3215 | 21.2433 | 0.025121 | 1256.7 | 5863.9 | 15.47% | 11.3% | 39.7895 | 0.18566 | 25.47%
2014 | 130430592 | 184154948 | 314585540 | 118447.1 | 628336.6826 |  | 2912203.055 |  | 7302 | 1007.676 | 50485.146 | 2783.2996 | 3540539.7376 |  |  | 3594815.8592 | 14770711 | 243.3746 | 21.2979 | 0.022328 | 1149.5 | 6810 | 11.08% | 12.24% | 35.7378 | 0.21172 | 33.06%
2015 | 112708986 | 194549595 | 307258581 | 113836.9 | 663803.2181 |  | 2631063 |  | 6999 | 965.862 | 50485.146 | 2783.2996 | 3294866.2181 |  |  | 3349100.5257 |  |  |  | 0.023344
* From records provided by Utilities from metering at the equipment end of MMSCF x 1030 MMBtu/MMSCF
**Includes Lincoln and Grant Halls
# From 2004 to 2005 there was a change in space accounting that reduced the overall GSF; from 2007 to 2008 there was a change in space accounting that increased the GSF; from 2009-2010 the SPHE was demolished
## FY09 Dec through April amounts were reduced due to supercompressibility adjustments (complaint filed against Vendor 2/13/9)
^Source for Degree Days from FY04-FY14: http://www.ncdc.noaa.gov/cdo-web/datasets/GHCNDMS/stations/GHCND:USC00111577/detail
1 kWh = | 0.003412 | MMBtu | 1 gal = | 0.138 | MMBtu
energy/sq. ft./degree day