## HP Duct Thermal Bridge v2
Lueftung | Speicher1 | Var1
-
|  |  | HW Heat Pump duct losses | [16 empty] | DRAFT: WARM 2021
2021-07-16
Hours running calculation
[5 empty] | HP Power Output | 1.2 | kW | From tech data |  | DHW consumption | 25 | l/person.day | Standard PHPP value
[5 empty] | DHW consumption | 0.075 | m3/d |  |  | Occupancy | 3 | People/heat pump | Number of people
[5 empty] | c water | 1.16 | kWh/m3K |  |  | performance ratio from PHPP | 1.6 |  | From cell V220 on DHW+Distribution
[5 empty] | water out | 60 | °C
[5 empty] | water in | 10 | °C
[5 empty] | dT | 50 | K
[5 empty] | running hours = | 5.8 | h/d
[5 empty] | diversity factor = | 0.24167
Heat pump ON duct loss characteristics
|  |  |  | Design air flow rate |  |  | m³/h | 300 | From HP technical data
|  |  |  | Temperature reduction of exhaust air |  |  | K | 5 | From HP technical data | [8 empty] | P Frostschutz [W] | #REF!
|  |  |  | Secondary calculation |  |  |  |  | Secondary calculation | [8 empty] | Betriebsstunden [kh/a] | #REF!
|  |  |  | Y-value outdoor air duct |  |  |  |  | Y-value exhaust air duct |  |  |  |  | Hilfsgröße R' | 5.9367 |  | Hilfsgröße R' | 5.9367
[5 empty] | Nominal width: | 150 | mm |  |  | Nominal width: | 150 | mm |  | Nebenrechnung (Iteration): |  |  | Nebenrechnung (Iteration):
[5 empty] | Insulation thickness: | 40 | mm |  |  | Insulation thickness: | 40 | mm |  | a- Näherung | 8 | W/(m²K) | a- Näherung | 8 | W/(m²K)
[14 empty] | k*-Näherung | 0.46047 | W/(mK) | k*-Näherung | 0.46047 | W/(mK)
[5 empty] | Reflective coating? |  | Yes |  |  | Reflective coating? |  | yes |  | OberflächentemperaturDiff_Näh | 0.95591 | K | OberflächentemperaturDiff_Näh | 1.3542 | K
[6 empty] | x | No |  |  |  | x | no |  | a- Näherung | 5.6759 | W/(m²K) | a- Näherung | 5.8721 | W/(m²K)
[14 empty] | k*-Näherung | 0.44592 | W/(mK) | k*-Näherung | 0.44755 | W/(mK)
[5 empty] | Thermal conductivity | 0.036 | W/(mK) |  |  | Thermal conductivity | 0.036 | W/(mK) |  | OberflächentemperaturDiff_Näh | 1.3048 | K | OberflächentemperaturDiff_Näh | 1.7932 | K
[5 empty] | Nominal air flow rate | 300 | m³/h |  |  | Nominal air flow rate | 300 | m³/h |  | a- Näherung | 5.8501 | W/(m²K) | a- Näherung | 6.0478 | W/(m²K)
[14 empty] | k*-Näherung | 0.44737 | W/(mK) | k*-Näherung | 0.44893 | W/(mK)
[5 empty] | DJ | 12 | K |  |  | DJ | 17 | K |  | OberflächentemperaturDiff_Näh | 1.27 | K | OberflächentemperaturDiff_Näh | 1.7464 | K
[5 empty] | Exterior duct diameter | 0.15 | m |  |  | Exterior duct diameter | 0.15 | m |  | a- Näherung | 5.8342 | W/(m²K) | a- Näherung | 6.0305 | W/(m²K)
[5 empty] | Exterior diameter | 0.23 | m |  |  | Exterior diameter | 0.23 | m |  | k*-Näherung | 0.44724 | W/(mK) | k*-Näherung | 0.44879 | W/(mK)
[5 empty] | a-Interior | 19.4716 | W/(m²K) |  |  | a-Interior | 19.4716 | W/(m²K) |  | OberflächentemperaturDiff_Näh | 1.2731 | K | OberflächentemperaturDiff_Näh | 1.7509 | K
[5 empty] | a-Surface | 5.8355 | W/(m²K) |  |  | a-Surface | 6.032 | W/(m²K) |  | a- Näherung | 5.8356 | W/(m²K) | a- Näherung | 6.0322 | W/(m²K)
[5 empty] | HP ON Y-value | 0.44725 | W/(mK) |  |  | HP ON Y-value | 0.44881 | W/(mK) |  | k*-Näherung | 0.44726 | W/(mK) | k*-Näherung | 0.44881 | W/(mK)
[5 empty] | Surface temperature difference | 1.2729 | K |  |  | Surface temperature difference | 1.7505 | K |  | OberflächentemperaturDiff_Näh | 1.2728 | K | OberflächentemperaturDiff_Näh | 1.7505 | K
Standby duct characteristics
[14 empty] | Nebenrechnung für Wärmeübergang innen |  |  | Nebenrechnung für Wärmeübergang innen
[14 empty] | w | 4.7157 | m/s | w | 4.7157 | m/s
[14 empty] | Re | 51109.4872 | - | Re | 51109.4872 | -
[5 empty] | Nominal width: | 150 | mm |  |  | Nominal width: | 150 | mm |  | Nusselt | 117.2283 | - | Nusselt | 117.2283 | -
[5 empty] | Insul. thickness: | 40 | mm |  |  | Insul. thickness: | 40 | mm
[5 empty] | Thermal conductivity | 0.036 | W/(mK) |  |  | Thermal conductivity | 0.036 | W/(mK)
[5 empty] | Interior pipe diameter: | 0.15 | m |  |  | Interior pipe diameter: | 0.15 | m
[5 empty] | Exterior pipe diameter: | 0.23 | m |  |  | Exterior pipe diameter: | 0.23 | m |  |  |  |  | Nebenrechnung Wärmebereitstellungsgrad
[5 empty] | a-Surface | 6.8 | W/(m²K) |  |  | a-Surface | 6.8 | W/(m²K) | [5 empty] | Reduktionsfaktor Frostschutz
[5 empty] | Y-value | 0.40974 |  |  |  | Y-value | 0.40974 | [5 empty] | Außenaufstellung | Tau
[5 empty] | Reduction factor | 0.5 |  |  |  | Reduction factor | 0.5 | [6 empty] | Tab
[5 empty] | HP OFF Y-value | 0.20487 | W/(mK) |  |  | HP OFF Y-value | 0.20487 | W/(mK) | [5 empty] | Tzu
Tzu'
[17 empty] | Innenaufstellung | Tau
Tfo
Tfo'
|  |  | Summary values for PHPP | [14 empty] | Pel
[5 empty] | SUPPLY HP AVERAGE Y-value | 0.26345 | W/(mK) |  |  | EXTRACT HP AVERAGE Y-value | 0.26382 | W/(mK)
Note on L9: Sally Godber: from HP manuf tech data
Note on L20: Based on PHPP 9 duct losses calculation for ventilation systems
Note on L39: Sally Godber: Based on standard winter internal temp of 20C and external temp of 8C. OK for midlands downwards, for more norther locations adjust from PHPP
Note on H47: Sally Godber: Uses the "Auxiliary calculation for interior drain pipes that are ventilated through the roof" from phpp9. not updated to phpp10 (in abayance) and hasn't been checked for applicability.
Note on AE57: Wenn Frostschutzheizregister dann 0.97 Wenn EWT dann 0.8
Note on L59: Sally Godber: random factor, used in PHPP as RWP/SVPs go to drains that are usually warmer than ambient. As BETA need to decide what is reasonable here.
Note on Q59: Sally Godber: random factor, used in PHPP as RWP/SVPs go to drains that are usually warmer than ambient. As BETA need to decide what is reasonable here.
Note on K65: Enter as an ambient thermal bridge, with the corresponding lengths of supply & extract ducts