## Read first
This workbook is for calculating the minimum recommended distances between intake and exhaust openings and boiler flues using the equation provided in Annex A of BS EN 13779 Ventilation for non-residential buildings-Performance requirements for ventilation and room-conditioning systems:
A detailed description of the calculation along with tables of coefficients can be found in Dutch regulation for the Siting of Air Inlets - AIVC Vol 19, No 3 June 1998
Select from drop down menu
enter data in yellow cells
calculated values are in green cells
Each sheet in this workbook is password protected with the following password: |  | 1234
The final sheet labelled 'Table 3' in the workbook includes the configurations for the inlet and outlets required for determination of the coefficients.
There are some hidden sheets critical to the correct functioning of the calculations, please do not delete.
v0.3 | Formula for gas fired boiler corrected.
v0.2 | Designed by WARM: Low Energy Building Design
This calculation sheet is offered free but with the following caveats:
x | Please do not redistribute without our logo and contact details
x | no claims are made for its accuracy or correctness
x | do not rely on anything on this sheet
x | there is NO WARRANTY of any sort, implied or otherwise
x | there is NO SUPPORT offered - but if you find any errors - please let us know

## Calculation
Calc ref | Select type of polluting outlet | Select Configuration | Exhaust air extract rate qv (m3/hr) or Max boiler output (kW) | Dilution coefficients (from table 2) |  | length of connecting line between air inlet and the air exhaust | difference in height between air intake and air exhaust | dilution factor | Separation distances OK?
|  | See Table 3 |  | C1 | C2 | l (m) | dh (m) | f
SVP on roof vent in wall | Ventilation outlet | 1 | 90 | 325 | 650 | 2 | 1 | 0.0038462 | YES
Intake below exhaust | Ventilation outlet | 3 | 90 | 650 | 325 | 1 | 1 | 0.0051282 | YES | Ventilation outlet
Intake next to exhaust | Ventilation outlet | 3 | 90 | 650 | 325 | 1 | 0 | 0.0076923 | YES | Fume outlet (gas fired)
Intake above exhast | Ventilation outlet | 4 | 90 | 500 | -163 | 1 | 1 | 0.014837 | NO | Fume outlet (other fuel)
gas boiler exhaust | Fume outlet (gas fired) | 3 | 24 | 163 | 440 | 1 | 0.3 | 0.016607 | NO
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | 1
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | 2
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | 3
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | 4
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | 5
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | 6
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | 7
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | 8
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | 9
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | 12
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | 13
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A |  |  | #N/A | #N/A
Note on D2: WARM: Note that original equation requires qv in l/s. We have converted to m3/hr as this is the unit more commonly used in passivhaus. Conversion factor used is 1l/s=3.6m3/hr

## table 2
Table 2: Coefficients C1 and C2 depending on the position and type of outlet
C1
Type of outlet | Position determined according to table 5
| 1 | 6 | 8 | 9 | 2 | 3 | 15 | 4 | 16 | 5 | 7 | 10 | 11 | 13 | 12 | 14 | 17
Ventilation outlet | 325 | 325 | 325 | 325 | 163 | 650 | 650 | 500 | 500 | 163 | 163 | 163 | 220 | 220 | 325 | 325 | 163
Fume outlet (gas fired) | 163 | 163 | 163 | 163 | 60 | 163 | 163 | 500 | 500 | 80 | 80 | 80 | 110 | 110 | 163 | 163 | 110
Fume outlet (other fuel) | 325 | 325 | 325 | 325 | 220 |  |  |  |  | 220 | 220 | 220
C2
Type of outlet | Position determined according to table 5
| 1 | 6 | 8 | 9 | 2 | 3 | 15 | 4 | 16 | 5 | 7 | 10 | 11 | 13 | 12 | 14 | 17
Ventilation outlet | 650 | 650 | 650 | 650 | 163 | 325 | 325 | -163 | -163 | 163 | 163 | 163 | 650 | 650 | 110 | 163 | 163
Fume outlet (gas fired) | 325 | 325 | 325 | 325 | 60 | 440 | 440 | -325 | -325 | 80 | 80 | 80 | 325 | 325 | 60 | 80 | 325
Fume outlet (other fuel) | 1100 | 1100 | 1100 | 1100 | 220 |  |  |  |  | 650 | 650 | 650

## Table 3
Source: Dutch regulation for the Siting of Air Inlets - AIVC Vol 19, No 3 June 1998

## equation 1 (hidden)
where
B | = | combusion appliance capacity (kW)
C1 | = | dilution coefficient (table 2 and table 3)
C2 | = | dilution coefficient (table 2 and table 3)
l | = | distance between air inlet and exhaust outlet (m)
dh | = | distance in height between air inlet and exhaust outlet (m)
f | = | dilution factor (acceptable dilution factors must be less than value in table 1)